## Sheet1
Asset | Location | Asset Description | Location Description | Parent | Failure Class | Location Parent | Criticality | Failure Class | GL Account | Area | Status | SE - Safety Element | PLE - Production Loss Element | EE - Environmental Element | RE - Repair Element | RF - Redundancy Factor | FRE - Failure Rate element | Criticality = Log10 (Total Score) = Log10 (SE) + Log10 (PLE) + Log10 (EE) + Log10 (RE) + Log10 (RF) + Log10 (FRE) | New_Criticality | RISK_RANKING_Point_System | RISK RANKING - Risk Matrix | HSECES Asset (Y/N) | Criticality | Maint PM Reqd (Y/N) | No. of Failure during last 3Y | Recomm PM Freq (Months) | m-mech, e- elec, c- ctrl, s- cvl/ str, g- f&g, f- fire sys, d- delete, i- insp, o- HSEFD, a- admin, p- pipeline, t- cctv | Additional PM (Months) | Performance Standard Applicable (Y/N) | PM Check sheet to Include MAT (Y/N) | Delete (0) | Soon to be mothballed (1) | No routine PM, but s/d strategy reqd, maintain spares (Y) | PM | Status | Section/ Discipline | Work Type | Activity code | Frequency | Frequency Units | Next Due Date | Job Plan Sequence
969512493 | SDHUSSEINY | HP Prodesk 600 G1 | Hussein Younes |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512747 | LASERJET-2420N |  | CONTROLE ROOM |  |  |  | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512813 | SD-DSUB410-SW01 | Cisco Switch - WS-C3650-24PD | IRP-II Substation |  |  | P&T_410_SS | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512748 | LASERJER-4200 | HP LASERJER-4200 B&W - Warehouse | Warehouse Building - Control Room |  |  | P&T_WAREHOUSE | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512826 | SD-CORE-SW01 | Cisco Switch - WS-C6509-E | Control Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512831 | MUSSAFAH_SUB_VOI | Cisco Voice Switch - WS-C3560G-24PS-S | IRP-I Substation |  |  | P&T_400_SS | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512815 | SD-DSIS-SW01 | Cisco Swith - WS-C3650-48PD | Satellite Instrument Shelter |  |  | P&T_SIS | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512816 | SD-DSECURITY-SW01 | Cisco switch - WS-C3650-48PD | Security Gate Building |  |  | P&T_SECURITY | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512495 | SD-MSFH-JABER | HP Prodesk 600 G1 | Jaber Ahmed Al Hammadi |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512750 | LASERJET- 400 | HP LASERJET-400 B&W - Warehouse | Warehouse Buildind - Mechanical Room |  |  | P&T_WAREHOUSE | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512751 | LASERJET 400 | HP LASERJET-400 - Old Admin | Old Admin Building - ELECTRICAL SUPERVISOR |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512762 | HP COLOR P- CP5225 | HP COLOR LASERJET-CP5225 - New Admin - Room 212 | New Admin Buliding |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512767 | NEW ADMIN(OFFICE009) | Scanner Fujitsu - Office 009 | New Admin Buliding |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374389 | M410LS057 | OUTDOOR LOUD SPEAKER NEAR TANK-001 NW SIDE ON POLE-ZONE-B2 | Loud Speaker with J/B-Outdoor-NEAR TANK-001 NW SIDE ON POLE | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374411 | M410LSZA3 | LOUD SPEAKER AT ZONE A-SIS (M410LS029,M410LS030,M410LS031,M410LS032 ,M410LS033 ,M410LS106,M410LS107,M410LS108,M410LS109,M410LS110,M410LS064) | LOUD SPEAKER AT ZONE A-SIS = 11 LS. |  | PA_SYS | M410LSZA | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374429 | M410FU07 | RIM SEAL PROTECTION AT TANK-007(M410FU207A,M410FU207B,M410FU207C, M410FU207D,M410FU207E) | RIM SEAL PROTECTION AT TANK-007 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374430 | M410FU08 | RIM SEAL PROTECTION AT TANK-008(M410FU208A,M410FU208B,M410FU208C, M410FU208D,M410FU208E) | RIM SEAL PROTECTION AT TANK-008 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374431 | M410FU09 | RIM SEAL PROTECTION AT TANK-009(M410FU209A,M410FU209B,M410FU209C, M410FU209D,M410FU209E) | RIM SEAL PROTECTION AT TANK-009 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374432 | M410FU10 | RIM SEAL PROTECTION AT TANK-010(M410FU210A,M410FU210B,M410FU210C, M410FU210D,M410FU210E) | RIM SEAL PROTECTION AT TANK-010 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346275 | PL312EOV31201 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-1 | 969275346 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346276 | PL312EOV31202 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-2 | 969275347 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346277 | PL312EOV31203 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-3 | 969275348 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346278 | PL312EOV31204 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-4 | 969275349 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346279 | PL312EOV31205 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-5 | 969275350 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346280 | PL312EOV31206 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-6 | 969275351 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346281 | PL312EOV31301 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-1 | 969275352 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346282 | PL312EOV31302 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-2 | 969275353 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346283 | PL312EOV31303 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-3 | 969275354 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346284 | PL312EOV31304 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-4 | 969275355 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346285 | PL312EOV31305 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-5 | 969275356 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346286 | PL312EOV31306 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-6 | 969275357 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346287 | PL312EOV001 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"ULG PIPELINE | 969275342 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346288 | PL312EOV002 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, ULG FROM TARRIFTAPOFF AT SV STATION-4 | 969275343 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346289 | PL312EOV003 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"GAS OIL PIPELINE | 969275344 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346290 | PL312EOV004 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, GAS OIL FROM TARRIFTAPOFF AT SV STATION-4 | 969275345 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969346291 | PL315EOV31513 | Hydraulic Control Unit | ELECTRO HYDRAULIC VALVE, SV STATION-13 | 969275358 | PACKAGE | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516603 | M410XYLDB031D | HEAT DETECTOR AT 410-P-031D | HEAT DETECTOR AT 410-P-031D |  | FGBHFD | M410FWCP031D | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516604 | M410XYLDB031E | HEAT DETECTOR AT 410-P-031E | HEAT DETECTOR AT 410-P-031E |  | FGBHFD | M410FWCP031E | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516605 | M410XYLDB031F | HEAT DETECTOR AT 410-P-031F | HEAT DETECTOR AT 410-P-031F |  | FGBHFD | M410FWCP031F | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516606 | M410XYLDB031G | HEAT DETECTOR AT 410-P-031G | HEAT DETECTOR AT 410-P-031G |  | FGBHFD | M410FWCP031G | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516607 | M410XYLDC031A | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031A | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031A |  | FGBFFD | M410FWCP031A | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516608 | M410XYLDC031B | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031B | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031B |  | FGBFFD | M410FWCP031B | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516609 | M410XYLDC031C | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031C | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031C |  | FGBFFD | M410FWCP031C | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516610 | M410XYLDC031D | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031D | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031D |  | FGBFFD | M410FWCP031D | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516611 | M410XYLDC031E | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031E | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031E |  | FGBFFD | M410FWCP031E | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516612 | M410XYLDC031F | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031F | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031F |  | FGBFFD | M410FWCP031F | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516613 | M410XYLDC031G | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031G | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031G |  | FGBFFD | M410FWCP031G | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516614 | M410XYLDD031A | HEAT DETECTOR AT 410-P-031A | HEAT DETECTOR AT 410-P-031A |  | FGBHFD | M410FWCP031A | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516615 | M410XYLDD031B | HEAT DETECTOR AT 410-P-031B | HEAT DETECTOR AT 410-P-031B |  | FGBHFD | M410FWCP031B | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516616 | M410XYLDD031C | HEAT DETECTOR AT 410-P-031C | HEAT DETECTOR AT 410-P-031C |  | FGBHFD | M410FWCP031C | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516617 | M410XYLDD031D | HEAT DETECTOR AT 410-P-031D | HEAT DETECTOR AT 410-P-031D |  | FGBHFD | M410FWCP031D | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516618 | M410XYLDD031E | HEAT DETECTOR AT 410-P-031E | HEAT DETECTOR AT 410-P-031E |  | FGBHFD | M410FWCP031E | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516619 | M410XYLDD031F | HEAT DETECTOR AT 410-P-031F | HEAT DETECTOR AT 410-P-031F |  | FGBHFD | M410FWCP031F | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516620 | M410XYLDD031G | HEAT DETECTOR AT 410-P-031G | HEAT DETECTOR AT 410-P-031G |  | FGBHFD | M410FWCP031G | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205080 | M410MOV0311 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175584 | MOV | M410T003 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0311-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/10/18 | ME-PM-002-M6
969205081 | M410MOV0312 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175585 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0312-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/10/18 | ME-PM-002-M6
969205082 | M410MOV0401 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175586 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0401-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/10/18 | ME-PM-002-M6
969205083 | M410MOV0402 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175587 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0402-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969205084 | M410MOV0403 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175588 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0403-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969205085 | M410MOV0404 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175589 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0404-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/10/18 | ME-PM-002-M6
969205086 | M410MOV0405 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175590 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0405-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/10/18 | ME-PM-002-M6
969205087 | M410MOV0406 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175591 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0406-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/10/18 | ME-PM-002-M6
969205088 | M410MOV0407 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175592 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0407-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969205089 | M410MOV0408 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175593 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0408-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969205090 | M410MOV0409 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175594 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0409-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/11/18 | ME-PM-002-M6
969205091 | M410MOV0410 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175595 | MOV | M410T004 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0410-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/11/18 | ME-PM-002-M6
969205092 | M410MOV0411 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175596 | MOV | M410T004 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0411-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969205093 | M410MOV0412 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-004 | 969175597 | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0412-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969205094 | M410MOV0501 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175598 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0501-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/11/18 | ME-PM-002-M6
969205095 | M410MOV0502 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175599 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0502-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/11/18 | ME-PM-002-M6
969205096 | M410MOV0503 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175600 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0503-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/11/18 | ME-PM-002-M6
969205097 | M410MOV0504 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175601 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0504-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969205098 | M410MOV0505 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175602 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0505-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969205099 | M410MOV0506 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175603 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0506-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/11/18 | ME-PM-002-M6
969205100 | M410MOV0507 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175604 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0507-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/11/18 | ME-PM-002-M6
969205101 | M410MOV0508 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175605 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0508-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/11/18 | ME-PM-002-M6
969205102 | M410MOV0509 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175606 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0509-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/11/18 | ME-PM-002-M6
969205103 | M410MOV0510 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175607 | MOV | M410T005 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0510-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/11/18 | ME-PM-002-M6
969205104 | M410MOV0511 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175608 | MOV | M410T005 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0511-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/11/18 | ME-PM-002-M6
969205105 | M410MOV0512 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-005 | 969175609 | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0512-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/11/18 | ME-PM-002-M6
969205106 | M410MOV0601 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175610 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0601-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/11/18 | ME-PM-002-M6
969205107 | M410MOV0602 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175611 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0602-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/11/18 | ME-PM-002-M6
969205108 | M410MOV0603 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175612 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0603-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/11/18 | ME-PM-002-M6
969205109 | M410MOV0604 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175613 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0604-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/11/18 | ME-PM-002-M6
969205110 | M410MOV0605 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175614 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0605-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/11/18 | ME-PM-002-M6
969205111 | M410MOV0606 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175615 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0606-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/12/18 | ME-PM-002-M6
969205112 | M410MOV0607 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175616 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0607-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/12/18 | ME-PM-002-M6
969205113 | M410MOV0608 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175617 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0608-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969205114 | M410MOV0609 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175618 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0609-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969205115 | M410MOV0610 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175619 | MOV | M410T006 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0610-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969205116 | M410MOV0611 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175620 | MOV | M410T006 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0611-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/12/18 | ME-PM-002-M6
969205117 | M410MOV0612 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-006 | 969175621 | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0612-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/12/18 | ME-PM-002-M6
969205118 | M410MOV0701 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175622 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0701-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969205119 | M410MOV0702 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175623 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0702-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969205120 | M410MOV0703 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175624 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0703-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
969205121 | M410MOV0704 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175625 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0704-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969205122 | M410MOV0705 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175626 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0705-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
969205123 | M410MOV0706 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175627 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0706-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969205124 | M410MOV0707 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175628 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0707-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969205125 | M410MOV0708 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175629 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0708-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/12/18 | ME-PM-002-M6
969205126 | M410MOV0709 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175630 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0709-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/12/18 | ME-PM-002-M6
969205127 | M410MOV0710 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175631 | MOV | M410T007 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0710-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/12/18 | ME-PM-002-M6
969205128 | M410MOV0711 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175632 | MOV | M410T007 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0711-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969205129 | M410MOV0712 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-007 | 969175633 | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0712-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969205130 | M410MOV0801 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175634 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0801-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/12/18 | ME-PM-002-M6
969205131 | M410MOV0802 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175635 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0802-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/12/18 | ME-PM-002-M6
969205132 | M410MOV0803 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175636 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0803-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 31/12/18 | ME-PM-002-M6
969205133 | M410MOV0804 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175637 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0804-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/01/19 | ME-PM-002-M6
969205134 | M410MOV0805 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175638 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0805-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205135 | M410MOV0806 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175639 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0806-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205136 | M410MOV0807 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175640 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0807-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969417164 | MV96632 | TOYOTA HILUX PICK-UP 11-96632 TERMINAL OPERATION SHIFT SUPV.(WHITE) | TOYOTA HILUX PICK-UP 11-96632 TERMINAL OPERATION SHIFT SUPV.(WHITE) |  | VEHICLE | MVEHICLES | 3 | VEHICLE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | a | 0 | N | N | 0 | 0 | 0 | MV96632-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 05/08/18 | MM-PM-029-M1
969518369 | M400FAGP006 | FIRE & GAS ALARM CONTROL PANEL AT NEW ADMIN BUILDING | FIRE & GAS ALARM CONTROL PANEL AT NEW ADMIN BUILDING |  | F&G_PNL | MADMIN1 | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516358 | PL100FD625 | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT |  | FGBFFD | PL100FACP620 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516359 | PL100FD626 | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT |  | FGBFFD | PL100FACP620 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516360 | PL100FD627 | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT |  | FGBFFD | PL100FACP620 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516361 | PL100XAC621 | MANUAL ALARM CALL POINT AT SHWEIHAT | MANUAL ALARM CALL POINT AT Shewihat |  | PA_SYS | PL100FACP620 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516362 | PL100XAC622 | MANUAL ALARM CALL POINT AT SHWEIHAT | MANUAL ALARM CALL POINT AT Shewihat |  | PA_SYS | PL100FACP620 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516363 | PL100XAC623 | MANUAL ALARM CALL POINT AT SHWEIHAT | MANUAL ALARM CALL POINT AT Shewihat |  | PA_SYS | PL100FACP620 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516364 | PL312FD401 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365112 | M410XHD606A | LINEAR HEAT DETECTOR FOR TANK-001 | LINEAR HEAT DETECTOR FOR TANK-001 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281288 | M410PT921AB | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT921AB-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281289 | M410PT921BA | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT921BA-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281290 | M410PT921BB | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT921BB-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281291 | M410PT941AA | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT941AA-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281292 | M410PT941AB | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT941AB-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281293 | M410PT941BA | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT941BA-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281294 | M410PT941BB | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT941BB-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281295 | M410TG921AF | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351520 | M410MX107 | STATIC MIXER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 | STATIC MIXER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 10 | 5 | 50 | 10 | 5 | 6.0969 | Low | Medium | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969282134 | M400MOV324 | ACTUATOR,ELECTRIC MOTOR | FILLING MOV ON LUBRICITY IMPROVER TANK 302. |  | MOV | M400T302 | 3 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV324-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/01/19 | ME-PM-002-M6
969278592 | PL312CCTV020 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278593 | PL312CCTV021 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278594 | PL312CCTV022 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484421 | M410HOS10 | #10 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #10 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL POD 10/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484415 | M410HOS4 | #4 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #4 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL PODS 4/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484416 | M410HOS5 | #5 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #5 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL PODS 5/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484417 | M410HOS6 | #6 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #6 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL POD 6/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484419 | M410HOS8 | #8 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #8 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL POD 8/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484420 | M410HOS9 | #9 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #9 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL POD 9/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485978 | M410DOM1P2 | PUMP#2 IN DOMINATOR #1 5K GPM -BIG FLOW SYSTEM. | PUMP #2 OF DOMINATOR #1 WITH 5K GPM CAPACITY -BIG FLOW SYSTEM. |  | PACKAGE | M410DOM1 | 2 | BFS | 617101-310600 | MTERMINAL | NOT READY | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485979 | M410DOM2P1 | PUMP#1 IN DOMINATOR #2 5K GPM -BIG FLOW SYSTEM. | PUMP #1 OF DOMINATOR #2 WITH 5K GPM CAPACITY -BIG FLOW SYSTEM. |  | PACKAGE | M410DOM2 | 2 | BFS | 617101-310600 | MTERMINAL | NOT READY | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485993 | M410FLP3 | FLOATING PUMP#3 FOR NEPTUNE #2, 5K GPM FROM THE SEA. BIG FLOW SYSTEM. | HYDRAULIC DRIVE FLOATING PUMP #3, USED WITH THE NEPTUNE UNITS, BIG FLOW FIRE FIGHTING SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485997 | M410FLP4 | FLOATING PUMP#4 FOR NEPTUNE #2, 5K GPM FROM THE SEA. BIG FLOW SYSTEM. | HYDRAULIC DRIVE FLOATING PUMP #4, USED WITH THE NEPTUNE UNITS, BIG FLOW FIRE FIGHTING SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485977 | M410DOM1P1 | PUMP#1 IN DOMINATOR #1 5K GPM -BIG FLOW SYSTEM. | PUMP #1 OF DOMINATOR #1 WITH 5K GPM CAPACITY -BIG FLOW SYSTEM. |  | PACKAGE | M410DOM1 | 2 | BFS | 617101-310600 | MTERMINAL | NOT READY | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485980 | M410DOM2P2 | PUMP#2 IN DOMINATOR #2 5K GPM -BIG FLOW SYSTEM. | PUMP #2 OF DOMINATOR #2 WITH 5K GPM CAPACITY -BIG FLOW SYSTEM. |  | PACKAGE | M410DOM2 | 2 | BFS | 617101-310600 | MTERMINAL | NOT READY | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485981 | M410FLP1 | FLOATING PUMP#1 FOR NEPTUNE #1 5K GPM FROM THE SEA. BIG FLOW SYSTEM. | HYDRAULIC DRIVE FLOATING PUMP #1, USED WITH THE NEPTUNE UNITS, BIG FLOW FIRE FIGHTING SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281324 | M410P050BB | LUB OIL PUMP FOR 410-P-002B PUMP | LUBE OIL PUMP FOR 410-P-002B PUMP |  | PUCEOH | M410P002B | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Non Critical | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P050BB-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969281325 | M410P051BA | LUB OIL PUMP FOR 410-P-004B PUMP | LUBE OIL PUMP FOR 410-P-004B PUMP |  | PUCEOH | M410P004B | 3 | PUCEOH | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P051BA-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969281326 | M410P051BB | LUB OIL PUMP FOR 410-P-004B PUMP | LUBE OIL PUMP FOR 410-P-004B PUMP |  | PUCEOH | M410P004B | 3 | PUCEOH | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P051BB-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969281327 | M410EA050AA | AIR BLAST COOLER FOR 410-P-002A/B | AIR BLAST COOLER FOR 410-P-002A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA050AA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969281328 | M410EA050AB | AIR BLAST COOLER FOR 410-P-002A/B | AIR BLAST COOLER FOR 410-P-002A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA050AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969281329 | M410EA050BA | AIR BLAST COOLER FOR 410-P-002A/B | AIR BLAST COOLER FOR 410-P-002A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA050BA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969281336 | M410L050AB | DUPLEX FILTER FOR 410-P-002A/B | DUPLEX FILTER FOR 410-P-002A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281337 | M410L050BA | DUPLEX FILTER FOR 410-P-002A/B | DUPLEX FILTER FOR 410-P-002A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281340 | M410L051AB | DUPLEX FILTER FOR 410-P-004A/B | DUPLEX FILTER FOR 410-P-004A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281341 | M410L051BA | DUPLEX FILTER FOR 410-P-004A/B | DUPLEX FILTER FOR 410-P-004A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281342 | M410L051BB | DUPLEX FILTER FOR 410-P-004A/B | DUPLEX FILTER FOR 410-P-004A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281343 | M410P002A | VIBRATION MONITORING SYSTEM, SUB-ASSY OF 410-P-002A | AL AIN ULG MAIN LINE PUMP | 969269213 | EMERSDD | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281344 | M410P002B | VIBRATION MONITORING SYSTEM, SUB-ASSY OF 410-P-002B | AL AIN ULG MAIN LINE PUMP | 969269214 | EMERSDD | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281345 | M410P004A | VIBRATION MONITORING SYSTEM, SUB-ASSY OF 410-P-004A | AL AIN GAS OIL MAIN LINE PUMP | 969269215 | EMERSDD | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195518 | M410FU423 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195536 | M410FU301 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195537 | M410FU302 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195538 | M410FU303 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195539 | M410FU304 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195540 | M410FU305 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195541 | M410FU306 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195542 | M410FU307 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195543 | M410FU308 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195544 | M410FU309 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195545 | M410FU310 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195519 | M410FU424 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195546 | M410FU311 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195547 | M410FU312 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195548 | M410FU313 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195549 | M410FU314 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195553 | M400DCSMC005 | PLCR DCS MARSHALLING CABINET | PLCR DCS MARSHALLING CABINET |  | DCS_PNL | M400SYS | 3 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195554 | M400DCSSC004 | PLCR DCS SYSTEM CABINET | PLCR DCS SYSTEM CABINET |  | DCS_PNL | M400SYS | 3 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195555 | M400DCSSRC001 | PLCR NETWORK/SERVER CABINET | PLCR NETWORK/SERVER CABINET |  |  | M400SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195556 | M400ESDMC003 | PLCR ESD MARSHALLING CABINET | PLCR ESD MARSHALLING CABINET |  |  | M400SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195557 | M400ESDSC003 | PLCR ESD SYSTEM CABINET | PLCR ESD SYSTEM CABINET |  |  | M400SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195558 | M400FOPPSC001 | PLCR NETWORK/SERVER CABINET | PLCR NETWORK/SERVER CABINET |  |  | M400SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195520 | M410FU425 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195589 | M410CHV2354009 | 12" DUAL PLATE CHECK VALVE, FLANGE, 300# | 12" DUAL PLATE CHECK VALVE, FLANGE, 300# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195590 | M410CHV2354010 | 16" DUAL PLATE CHECK VALVE, FLANGE, 300# | 16" DUAL PLATE CHECK VALVE, FLANGE, 300# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195591 | M410CHV2354011 | 28" DUAL PLATE CHECK VALVE, FLANGE, 300# | 28" DUAL PLATE CHECK VALVE, FLANGE, 300# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195592 | M410CHV2354012 | 3" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 300# | 3" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 300# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195593 | M410DCSMC001 | SIS-001 DCS MARSHALLING CABINET | SIS-001 DCS MARSHALLING CABINET |  | DCS_PNL | M410SYS | 3 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195594 | M410DCSMC002 | SIS-001 DCS MARSHALLING CABINET | SIS-001 DCS MARSHALLING CABINET |  | DCS_PNL | M410SYS | 3 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195595 | M410DCSSC001 | SIS-001 DCS SYSTEM CABINET | SIS-001 DCS SYSTEM CABINET |  | DCS_PNL | M410SYS | 3 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195596 | M410DCSSC002 | SIS-001 DCS SYSTEM CABINET | SIS-001 DCS SYSTEM CABINET |  | DCS_PNL | M410SYS | 3 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195597 | M410ESDMC001 | SIS-001 ESD MARSHALLING CABINET | SIS-001 ESD MARSHALLING CABINET |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195598 | M410ESDMC002 | SIS-001 ESD MARSHALLING CABINET | SIS-001 ESD MARSHALLING CABINET |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935453 | SALAINTP8 | TEST POINT # 8 (C.P. STATION-1 AT KM 3.8) | TEST POINT # 8 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935469 | SALAINTP21 | TEST POINT # 21 (C.P.STATION-2 AT KM 18.5) | TEST POINT # 21 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132697 | M400MK002B | MOTOR,ELECTRIC, AIR BLOWER MOTOR, 3.00 KW, VARIABLE HZ, 415 V, VARIABLE RPM, 3 | MOTOR FOR AIR BLOWER - B |  | MOTOR | M400K002B | 2 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MK002B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 20/12/18 | ME-PM-014-M6
969132711 | M400AT256 | OUTFLOW QUALITY - PH ANALYSER | OUTFLOW QUALITY CONTROL- PH ANALYZER. |  | ANALYSER | M400WWTPANALZ | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518370 | M400FECP003 | FIRE SUPRESSION PANEL AT NEW ADMIN BUILDING | FIRE SUPRESSION PANEL AT NEW ADMIN BUILDING-SERVER ROOM |  | F&G_PNL | MMADMIN2 | 3 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932612 | M400L004B | 8 FILTER COALESCER 4 SEPARATOR - MUSSAFAH-ADIA JET A1 PIPE LINE. | COALESCER FILTER & SEPARATOR - MUSSAFAH-ADIA JET A1 PIPE LINE |  | VESSEL | M400FILTER | 3 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 50 | 10 | 50 | 1 | 10 | 7.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932615 | AA13VA2BA391 | VALVE, BALL, 2" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 2" RB 150RF |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932616 | AA13VA2BA398 | VALVE, BALL, 2" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 2" FB 150RF |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932617 | AA13VA2BA691 | VALVE, BALL, 2" X 1-1/2" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted | BALL VALVE 2" X 1-1/2" RB 900RF |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932618 | AA13VA3BA398 | VALVE, BALL, 3" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 3" FB 150RF |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932619 | AA13VA4BA391 | VALVE, BALL, 4" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 4" RB 150RF |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932620 | AA13VA8BA391 | VALVE, BALL, 8" X 6" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; | BALL VALVE 8"X6" RB 150RF TRUNNION MOUNT GEAR OPR |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175921 | M410LT013C | ULG 91 TANK 410-T-001 | SAAB ROSEMOUNT ULG 91 TANK 410-T-001 |  | LVL_TX | M410T001 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365317 | M400MV1XX1 | FOAM PUMP MOTOR AT FIRE STATION FOAM ROOM. | FOAM PUMP MOTOR AT FIRE STATION FOAM ROOM. |  | PUCE | MFIRE | 3 | 0 | 617101-310510 | MTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MV1XX1-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 27/01/19 | ME-PM-LT1-6M
969365318 | M400WO01 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO01-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365320 | M400WO03 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO03-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969532772 | M400RVRV11B | RIM VENT RELIEF VALVE FOR TANK T-111 | RIM VENT RELIEF VALVE FOR TANK T-111 |  | PSV | M400T111 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532773 | M400RVRV11C | RIM VENT RELIEF VALVE FOR TANK T-111 | RIM VENT RELIEF VALVE FOR TANK T-111 |  | PSV | M400T111 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532774 | M400RVRV11D | RIM VENT RELIEF VALVE FOR TANK T-111 | RIM VENT RELIEF VALVE FOR TANK T-111 |  | PSV | M400T111 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365319 | M400WO02 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO02-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365321 | M400WO04 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO04-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365322 | M400WO05 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO05-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365323 | M400WO06 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO06-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365324 | M400WO07 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO07-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365325 | M400WO08 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO08-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365326 | M400WO09 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO09-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365327 | M400WO10 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO10-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
935162 | M30LG261 | GAUGE LEVEL | Level for Filter Coalescer 30-L-006 |  |  | M30LEVEL | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935163 | M30LG262 | GAUGE LEVEL | Level for Filter Coalescer 30-L-007 |  |  | M30LEVEL | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935164 | M400LG531 | GAUGE, LEVEL, TRANSPARENT , 559MM , 804MM , 2" X 300LB RF FLANGED , 300 LB , A10 | Level for Filter Coalescer Seperator 400-L-003A | 932609 | INDICATR | M400L003A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935165 | M400LG532 | GAUGE, LEVEL, TRANSPARENT , 559MM , 804MM , 2" X 300LB RF FLANGED , 300 LB , A10 | Level for Filter Coalescer Seperator 400-L-003B | 932610 | INDICATR | M400L003B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935166 | M400LG751 | GAUGE, LEVEL, TRANSPARENT , 641MM , 1038MM , 2" X 300LB RF FLANGED , 300 LB , A1 | Level for Filter Coalescer 400-L-004A | 932611 | INDICATR | M400L004A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935167 | M400LG752 | GAUGE, LEVEL, TRANSPARENT , 641MM , 1038MM , 2" X 300LB RF FLANGED , 300 LB , A1 | Level for Filter Coalescer 400-L-004B | 932612 | INDICATR | M400L004B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935168 | M400LG927A | GAUGE, LEVEL, REFLEX , 981MM , 1199MM , 2" X 300LB RF FLANGED , 300 LB , A105/SS | Level for Corr. Inhibitor Dosing tank 400-T-080 |  | INDICATR | M400LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935169 | M400LG927B | GAUGE, LEVEL, REFLEX , 981MM , 1199MM , 2" X 300LB RF FLANGED , 300 LB , A105/SS | Level for Corr. Inhibitor Dosing tank 400-T-080 |  | INDICATR | M400LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ERH57225 | SCPS1 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION | TRANSFORMER RECTIFIER (C.P. STATION-1 AT 3.8 KM) |  | CATHPRO | SALAINCPS1 | 3 | CATHPRO | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SCPS1-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/12/18 | ME-PM-008-M6
ERH57226 | SCPS2 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION | TRANSFORMER RECTIFIER (C.P. STATION-2 AT 18.5 KM) |  | CATHPRO | SALAINCPS2 | 3 | CATHPRO | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SCPS2-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 16/09/18 | ME-PM-008-M6
ERH57227 | SCPS3 | CATHODIC PROTECTION , NO MODIFIER | TRANSFORMER RECTIFIER (C.P. STATION-3 AT 84.5 KM) |  | CATHPRO | SALAINCPS3 | 3 | CATHPRO | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SCPS3-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 09/08/18 | ME-PM-008-M6
ERH57228 | SCPS4 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION | C.P. STATION-4 AL AIN PIPE LINE AT 149 KM TRANSFORMER RECTIFIER. |  | CATHPRO | SALAINCPS4 | 3 | CATHPRO | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SCPS4-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 26/09/18 | ME-PM-008-M6
ESA57571 | M60MDB001 | SWITCHGEAR, 415V,3 PHASE,50HZ , 415 volts, FLOOR , IP54 , 3 , 3+1 , MAIN SWITCH | MAIN DISTRIBUTION BOARD |  | MCC_SWBD | M60SUBSTN | 2 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937651 | M400P019 | SYSTEM | OFF SPEC JET A1 MAIN LINE PUMP TO RUWAIS. | 935830 |  | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P019MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-001-M6
937652 | M400P018B | SYSTEM | JET A1 MAIN LINE PUMP-B TO ADIA. | 935829 |  | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | M400P018BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/11/18 | MM-PM-005-M6
937653 | M400P018A | SYSTEM | JET A1 MAIN LINE PUMP-A TO ADIA. | 935828 |  | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P018AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-005-M6
937654 | M400P016B | SYSTEM | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP | 935827 |  | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-002-M6
937655 | M400P016A | SYSTEM | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP | 935826 |  | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 04/10/18 | MM-PM-002-M6
937909 | M400ME033 | BOILER, PACKAGE | ELECTRIC STEAM BOILER AT MUSAFFAH TERMINAL IRP-1 |  | SBOILERS | M400BOILER | 3 | SBOILERS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Non Critical | Low | Non Critical | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937910 | M400MX001 | STATIC MIXER FOR 16" RUWAIS MUSSAFAH LINE | STATIC MIXER FOR 16" RUWAIS MUSSAFAH LINE |  |  | M400FAN | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937911 | M400MX002 | MIXER, STATIC | STATIC MIXER FOR 10" ADR MUSSAFAH LINE |  |  | M400FAN | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937912 | M400ME032A | PACKAGE | FSII & CI SKID FOR JP8 TANKER LOADING |  | PACKAGE | M400PKG | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937913 | M400ME032B | PACKAGE | FSII & CI SKID FOR JP8 TANKER LOADING |  | PACKAGE | M400PKG | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939158 | M400TI419 | INDICATOR, TEMPERATURE | Main E-MOTOR 'V' Winding For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI419-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/10/18 | MC-PM-010-Y1
939159 | M400TI420 | INDICATOR, TEMPERATURE | Main E-MOTOR 'W' Winding For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI420-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/10/18 | MC-PM-010-Y1
939160 | M400TI421 | INDICATOR, TEMPERATURE | Main E-MOTOR 'W' Winding For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI421-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/10/18 | MC-PM-010-Y1
939161 | M400TI422A | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing NDE For Pump 400-P-016 | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI422A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 31/10/18 | MC-PM-010-Y1
939162 | M400TI422B | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing NCE For Pump 400-P-016 | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI422B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/11/18 | MC-PM-010-Y1
939163 | M400TI423A | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing CE For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI423A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/11/18 | MC-PM-010-Y1
939164 | M400TI423B | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing CE For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI423B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/11/18 | MC-PM-010-Y1
939165 | M400TI424A | INDICATOR, TEMPERATURE | Pump Radial Bearing D.E. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI424A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/11/18 | MC-PM-010-Y1
939166 | M400TI424B | INDICATOR, TEMPERATURE | Pump Radial Bearing D.E. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI424B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/11/18 | MC-PM-010-Y1
939167 | M400TI425A | INDICATOR, TEMPERATURE | Casing For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI425A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/11/18 | MC-PM-010-Y1
939168 | M400TI426A | INDICATOR, TEMPERATURE | Pump Radial Bearing N.D.E. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI426A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/11/18 | MC-PM-010-Y1
939169 | M400TI426B | INDICATOR, TEMPERATURE | TEMP. ELEMENT. AT NON DRIVE END OF 400P16B. | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI426B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/11/18 | MC-PM-010-Y1
939170 | M400TI427A | INDICATOR, TEMPERATURE | Thrust Bearing D.E. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI427A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/11/18 | MC-PM-010-Y1
939171 | M400TI427B | INDICATOR, TEMPERATURE | Thrust Bearing D.E. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI427B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/11/18 | MC-PM-010-Y1
939172 | M400TI428A | INDICATOR, TEMPERATURE | Thrust Bearing N.D.E. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI428A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/11/18 | MC-PM-010-Y1
939173 | M400TI428B | INDICATOR, TEMPERATURE | Thrust Bearing N.D.E. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI428B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/11/18 | MC-PM-010-Y1
939174 | M400TI429C | INDICATOR, TEMPERATURE | Lube Oil Header Temp. For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI429C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/11/18 | MC-PM-010-Y1
939175 | M400TI461 | INDICATOR, TEMPERATURE | Main E-MOTOR 'U' Winding For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI461-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939176 | M400TI462 | INDICATOR, TEMPERATURE | Main E-MOTOR 'U' Winding For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI462-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939177 | M400TI463 | INDICATOR, TEMPERATURE | Main E-MOTOR 'V' Winding For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI463-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939178 | M400TI463C | INDICATOR, TEMPERATURE | Lube Oil Heater Tripped for 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI463C-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939179 | M400TI464 | INDICATOR, TEMPERATURE | Main E-MOTOR 'V' Winding For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI464-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939180 | M400TI465 | INDICATOR, TEMPERATURE | Main E-MOTOR 'W' Winding For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI465-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939181 | M400TI466 | INDICATOR, TEMPERATURE | Main E-MOTOR 'W' Winding For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI466-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939182 | M400TI467A | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing NCE For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI467A-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939183 | M400TI467B | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing NCE For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI467B-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939184 | M400TI468A | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing CE For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI468A-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939185 | M400TI468B | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing CE For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI468B-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939186 | M400TI469A | INDICATOR, TEMPERATURE | Pump Radial Bearingd D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI469A-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939187 | M400TI469B | INDICATOR, TEMPERATURE | Pump Radial Bearingd D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI469B-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939188 | M400TE469B | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Pump Radial Bearingd D.E. For Pump 400-P-019 | 939187 | TEMP_ELE | M400TI469B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939189 | M400TI470A | INDICATOR, TEMPERATURE | Casing For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI470A-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939190 | M400TI471A | INDICATOR, TEMPERATURE | Pump Radial Bearing N.D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI471A-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939191 | M400TI471B | INDICATOR, TEMPERATURE | Pump Radial Bearing N.D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI471B-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939192 | M400TI472A | INDICATOR, TEMPERATURE | Thrust Bearing D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI472A-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939193 | M400TI472B | INDICATOR, TEMPERATURE | Thrust Bearing D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI472B-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939194 | M400TI473A | INDICATOR, TEMPERATURE | Thrust Bearing N.D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI473A-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939195 | M400TI473B | INDICATOR, TEMPERATURE | Thrust Bearing N.D.E. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI473B-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939196 | M400TI474C | INDICATOR, TEMPERATURE | Lube Oil Header Temp. For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI474C-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939197 | M400TI501 | INDICATOR, TEMPERATURE | SKIN Temp. ELEMENT FOR ADR 10" N/R P/L |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI501-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/04/19 | MC-PM-010-Y1
939198 | M400TI502 | INDICATOR, TEMPERATURE | Temp. Between ADR 10" & Ruwais 10" Naphtha P/L |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI502-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/04/19 | MC-PM-010-Y1
939199 | M400TI503 | INDICATOR, TEMPERATURE | PIG Indication for To/From Ruwais 10" Naphtha P/L |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI503-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/04/19 | MC-PM-010-Y1
939200 | M400TI541A | INDICATOR, TEMPERATURE | TEMP.ELEMENT NEPTHA/REFORM P/L, JET A1,CUSTODY MET | 938681 |  | M400FC541A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI541A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/06/19 | MC-PM-010-Y1
939201 | M400TI541B | INDICATOR, TEMPERATURE | TEMP.ELEMENT NEPTHA/REFORM P/L, JET A1,CUSTODY MET | 938682 |  | M400FC541B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI541B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/06/19 | MC-PM-010-Y1
939202 | M400TI550 | INDICATOR, TEMPERATURE | Temp. Between ADR 10" & Ruwais 10" Naphtha P/L |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI550-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/04/19 | MC-PM-010-Y1
939203 | M400TI552 | INDICATOR, TEMPERATURE | Temp. outlet of 400-PV-561 |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI552-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/04/19 | MC-PM-010-Y1
939204 | M400TI566 | INDICATOR, TEMPERATURE | Temp.ADR Ruwais SRR P/L to Scr. Rec. 400-PLR-006 |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI566-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/04/19 | MC-PM-010-Y1
939205 | M400TI567 | INDICATOR, TEMPERATURE | Temp. ADR Ruwais SRR P/L to Ruwais Recpt. Terminal |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI567-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/04/19 | MC-PM-010-Y1
939206 | M400TI568 | INDICATOR, TEMPERATURE | SKIN Temp. ADR Ruwais SRR P/L from 400-PLR-007 |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI568-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/05/19 | MC-PM-010-Y1
939207 | M400TI620A | INDICATOR, TEMPERATURE | TEMP. ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 938683 |  | M400FC620A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI620A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/06/19 | MC-PM-010-Y1
939208 | M400TI620B | INDICATOR, TEMPERATURE | TEMP. ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 938684 |  | M400FC620B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI620B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/06/19 | MC-PM-010-Y1
939209 | M400TI620C | INDICATOR, TEMPERATURE | TEMP. ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 938685 |  | M400FC620C | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI620C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/06/19 | MC-PM-010-Y1
939210 | M400TI651 | INDICATOR, TEMPERATURE | Temp. Rws-Mussafah MP P/L to Scr. Recvr. 400-PLR-0 |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI651-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/04/19 | MC-PM-010-Y1
939211 | M400TI652 | INDICATOR, TEMPERATURE | Ruwais Mussafah MP P/L scr. reciver isolation lin |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI652-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/04/19 | MC-PM-010-Y1
939214 | M400TI751 | INDICATOR, TEMPERATURE | Temp. at Jet A1 P/L from storage tanks |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI751-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/05/19 | MC-PM-010-Y1
939215 | M400TI752 | INDICATOR, TEMPERATURE | Temp.at Suct. side of 400-G-017B in Jet A1 P/L |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI752-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/05/19 | MC-PM-010-Y1
939216 | M400TI771A | INDICATOR, TEMPERATURE | Temp. at 400-FT-771A in Mussafah - ADIA JET A1 P/L | 938686 |  | M400FC771A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI771A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/06/19 | MC-PM-010-Y1
939217 | M400TI771B | INDICATOR, TEMPERATURE | Temp. at 400-FT-771A in Mussafah - ADIA JET A1 P/L | 938687 |  | M400FC771B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI771B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/06/19 | MC-PM-010-Y1
939218 | M400TI772 | INDICATOR, TEMPERATURE | TEMP.ELEMENT 400-FT-772,CUSTODY METERING SYSTEM | 938688 |  | M400FC772 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI772-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/08/18 | MC-PM-010-Y1
939219 | M400TI801 | INDICATOR, TEMPERATURE | Temp. at Muss. Adia Jet A1 P/L from 400-P-018A/B |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI801-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/05/19 | MC-PM-010-Y1
939220 | M400TI802 | INDICATOR, TEMPERATURE | TEMP.ELE. MUSSAFAH TERMINAL FOR JET A1 P/L TO ADIA |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI802-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/05/19 | MC-PM-010-Y1
939221 | M400TI851 | INDICATOR, TEMPERATURE | Temp. Mussafah-Al Ain MP Tie-In P/L to 400-P-015A/ |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI851-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/05/19 | MC-PM-010-Y1
939222 | M400TI861A | INDICATOR, TEMPERATURE | Mussafah - TIE In MP P/L | 938689 |  | M400FC861A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI861A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/08/18 | MC-PM-010-Y1
939223 | M400TI861B | INDICATOR, TEMPERATURE | Mussafah - TIE In MP P/L (TEMPERATURE ELEMENT) | 938690 |  | M400FC861B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI861B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/08/18 | MC-PM-010-Y1
939224 | M400TI881 | INDICATOR, TEMPERATURE | Temp. at Mussafah-Al Ain MP Tie-In P/L |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI881-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/05/19 | MC-PM-010-Y1
939225 | M400TI882 | INDICATOR, TEMPERATURE | Temp. at Muss.-Al Ain MP Tie-In P/L to tie in poin |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI882-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/05/19 | MC-PM-010-Y1
939226 | M400VE401X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing NCE for 400-P-016A |  | VIBRE_TX | M400VI401X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939227 | M400VE401Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing NCE for 400-P-016A |  | VIBRE_TX | M400VI401Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939228 | M400VE402X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing CE for 400-P-016A |  | VIBRE_TX | M400VI402X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939229 | M400VE402Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing CE for 400-P-016A |  | VIBRE_TX | M400VI402Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939230 | M400VE403X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing D.E. 400-P-016A |  | VIBRE_TX | M400VI403X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933977 | MQ600VA3CH391 | VALVE, CHECK, SWING , 3" , 150 LB , 425 DEG C MAX , RF FLANGE , ASTM A216 GR WCB | CHECK VALVE, 3" 150 LB, RF FLG |  | VALCH | MQ600VALVE | 3 | VALCH | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933978 | MQ600VA3GL391 | GLOBE VALVE | GLOBE VALVE, 3" 150 LB, RF FLG |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933979 | MQ600VA34GA191 | GATE VALVE | GATE VALVE, 3/4" 1500 LB, SW |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933980 | MQ600VA34GL091 | GLOBE VALVE | GLOBE VALVE, 3/4" 800 LB, SW |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLD56667 | M10PIPING | PIPELINE HYDROCARBON | COMMON PIPING FOR PRODUCT STORAGE TANKS AREA |  |  | M10COMMON | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLM56137 | SALAINPIPE | AL-AIN TRANSFER PIPE LINE | AL-AIN TRANSFER PIPE LINE |  | PIPING | MTERMINAL | 2 | PIPING | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 100 | 50 | 100 | 11.699 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLM56139 | SADIAPIPE | ABU DHABI INT'L AIRPORT PRODUCT TRANSFER PIPE LINE | ABU DHABI INT'L AIRPORT PRODUCT TRANSFER PIPE LINE |  | PIPING | AT800 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 100 | 50 | 100 | 11.699 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLM56140 | SMPIPE | MAIN PIPE RUNS , NO MODIFIER | SANT/ MUSAFAH MULTY PRODUCT TRANSFER PIPE LINE. |  | PIPING | MTERMINAL | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 100 | 50 | 100 | 11.699 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLM56141 | SMLPGPIPE | LPG TRANSFER PIPE LINE TO MUSSAFAH. | LPG TRANSFER PIPE LINE TO MUSSAFAH. |  | PIPES | MTERMINAL | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934017 | AT800VA1GA091 | GATE VALVE | GATE VALVE, 1" 800 LB, SW |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934018 | AT800VA12GA092 | GATE VALVE 1/2" | GATE VALVE, 1/2" 800 LB, SW+NPT |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934019 | AT800VA2GA491 | GATE VALVE | GATE VALVE, 2" 300 LB, RF FLG |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934020 | AT800VA2GL491 | GLOBE VALVE | GLOBE VALVE,2" 300 LB, RF FLG |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934021 | AT800VA34GA091 | GATE VALVE 3/4" | GATE VALVE, 3/4" 800 LB, SW |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934022 | AT800VA34GA092 | GATE VALVE 3/4" | GATE VALVE, 3/4" 800 LB, SW+NPT |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934023 | AT800VA8GL491 | GLOBE VALVE | GLOBE VALVE, 8" 300 LB, RF FLG |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934025 | M400MVS001 | PANEL CONTROL | MOV CONTROL SYSTEM |  | M_STATIO | M400SYS | 1 | M_STATIO | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVS001-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 23/09/18 | ME-MSTR-MOV-M3
934026 | M400MVS002 | PANEL CONTROL | MOV CONTROL SYSTEM |  | M_STATIO | M400SYS | 1 | M_STATIO | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVS002-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 26/08/18 | ME-MSTR-MOV-M3
935929 | M400LE016A3 | Heater for Lube Oil Pump 400MP016A | Heater for Lube Oil Pump 400MP016A |  | ELEC_HTR | M400P016A | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LE016A3-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 03/12/18 | ME-PM-006-Y
935930 | M400LE016AA | COOLER | ULG95/98/GO/JET A1/KEROS M/L PMP AIR BLAST COOLER |  |  | M400P016A | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935931 | M400LE016AB | COOLER | ULG95/98/GO/JET A1/KEROS M/L PMP AIR BLAST COOLER |  |  | M400P016B | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935932 | M400LE016B3 | Heater for Lube Oil Pump 400MP016B | Heater for Lube Oil Pump 400MP016B |  | ELEC_HTR | M400P016B | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | AA213MOV148-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
935933 | M400LE016BA | COOLER | ULG95/98/GO/JET A1/KEROS M/L PMP AIR BLAST COOLER |  |  | M400P016A | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935934 | M400LE016BB | COOLER | ULG95/98/GO/JET A1/KEROS M/L PMP AIR BLAST COOLER |  |  | M400P016B | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935935 | M400LE019A3 | Heater for Lube Oil Pump 400MP019 | Heater for Lube Oil Pump 400MP019 |  | ELEC_HTR | M400P019 | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | AA213MOV149-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
935936 | M400LE019A | COOLER | OFF SPEC JET A1 M/L PUMP AIR BLAST COOLER |  |  | M400P019 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935937 | M400LE019B | COOLER | OFF SPEC JET A1 M/L PUMP AIR BLAST COOLER |  |  | M400P019 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935938 | M400LF016AA | FILTER, OIL | ULG95/98/GO/JET A1/KER M/L PUMP LUBOIL FILTER |  | VESSEL | M400P016A | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 1 | 1 | 1.3979 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935939 | M400LF016AB | FILTER, OIL | ULG95/98/GO/JET A1/KER M/L PUMP LUBOIL FILTER |  | VESSEL | M400P016B | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 1 | 1 | 1.3979 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935940 | M400LF016BA | FILTER, OIL | ULG95/98/GO/JET A1/KER M/L PUMP LUBOIL FILTER |  | VESSEL | M400P016A | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935941 | M400LF016BB | FILTER, OIL | ULG95/98/GO/JET A1/KER M/L PUMP LUBOIL FILTER |  | VESSEL | M400P016B | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935942 | M400LF019A | FILTER, OIL | OFF SPEC JET A1 M/L PUMP LUB OIL FILTER |  | VESSEL | M400P019 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532771 | M400RVRV11A | RIM VENT RELIEF VALVE FOR TANK T-111 | RIM VENT RELIEF VALVE FOR TANK T-111 |  | PSV | M400T111 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Non Critical | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POT56676 | M5101V101 | POT NO MODIFIER | K.O. POT AT LPG PIPELEINE PIG RECEIVER IN MTF |  |  | M5101R02 | 2 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132800 | M400POV715 | VALVE,SEQUENCIAL CONTROL/ESD | PUEUMATIC DRIVEN BV-OUTFLOW TO CHANNEL |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV715-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/09/18 | MC-PM-026-M6
IAS500531 | U51PSLL146 | SWITCH, PRESSURE, DIAPHRAGM , 125-480VAC 15A , 4-28 BAR , SPDT , IP66 , 1/2" NPT | PRESSURE SWITCH LPG PIPE LINE | ISD99111 | PRES_SWT | U51PLL146 | 1 | PRES_SWT | 623101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131692 | M400XLF206 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE FOR TANKS T-117/118/119/120 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131695 | M400XLF210 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE FOR SCRAPPER AREA |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131700 | M400XHD202B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-015B |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD202B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM05.M3
969131707 | M400XHD206A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR INTER TANK TRANSFER PUMP 400-MP-021B |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD206A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 15/08/18 | MFPS-PM05.M3
969131714 | M400XHD211B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-112 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD211B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 22/08/18 | MFPS-PM05.M3
969131717 | M400XHD213A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-114 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD213A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 26/08/18 | MFPS-PM05.M3
969131718 | M400XHD213B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-114 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD213B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 03/09/18 | MFPS-PM05.M3
969131719 | M400XHD214A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-115 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD214A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 03/09/18 | MFPS-PM05.M3
969131720 | M400XHD214B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-115 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD214B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 03/09/18 | MFPS-PM05.M3
969131721 | M400XHD215A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-116 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD215A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/09/18 | MFPS-PM05.M3
969131722 | M400XHD215B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-116 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD215B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/09/18 | MFPS-PM05.M3
969532783 | M400RVRV13C | RIM VENT RELIEF VALVE FOR TANK T-113 | RIM VENT RELIEF VALVE FOR TANK T-113 |  | PSV | M400T113 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516346 | M400UPSAC004A | AC UPS IN NEW ADMIN BUILDING WITH 163 CELLS OF 375AH TYPE VR NiCD. |  |  | INVRT_UP |  | 1 | INVRT_UP | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516354 | PL100FD621 | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT |  | FGBFFD | PL100FACP620 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516355 | PL100FD622 | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT |  | FGBFFD | PL100FACP620 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516356 | PL100FD623 | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT |  | FGBFFD | PL100FACP620 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516357 | PL100FD624 | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT | FLAME DETECTOR (UV/IR TYPE) AT SHWEIHAT |  | FGBFFD | PL100FACP620 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516365 | PL312FD402 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516366 | PL312FD403 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516367 | PL312FD404 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516368 | PL312FD405 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516369 | PL312FD406 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516370 | PL312FD407 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516371 | PL312FD408 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516372 | PL312FD409 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516373 | PL312FD410 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 | FLAME DETECTOR (UV/IR TYPE) AT SV STATION- 4 |  | FGBFFD | PL312SV4 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516377 | PL312GDH109 | FLAMMABLE GAS DETECTOR AT SV STATION-1 | FLAMMABLE GAS DETECTOR AT SV STATION-1 |  | FG_DET | PL312SV1 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516378 | PL312GDH110 | FLAMMABLE GAS DETECTOR AT SV STATION-1 | FLAMMABLE GAS DETECTOR AT SV STATION-1 |  | FG_DET | PL312SV1 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516379 | PL312GDH111 | FLAMMABLE GAS DETECTOR AT SV STATION-1 | FLAMMABLE GAS DETECTOR AT SV STATION-1 |  | FG_DET | PL312SV1 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516380 | PL312GDH112 | FLAMMABLE GAS DETECTOR AT SV STATION-1 | FLAMMABLE GAS DETECTOR AT SV STATION-1 |  | FG_DET | PL312SV1 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516385 | PL312GDH209 | FLAMMABLE GAS DETECTOR AT SV STATION-2 | FLAMMABLE GAS DETECTOR AT SV STATION-2 |  | FG_DET | PL312SV2 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516386 | PL312GDH210 | FLAMMABLE GAS DETECTOR AT SV STATION-2 | FLAMMABLE GAS DETECTOR AT SV STATION-2 |  | FG_DET | PL312SV2 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516387 | PL312GDH211 | FLAMMABLE GAS DETECTOR AT SV STATION-2 | FLAMMABLE GAS DETECTOR AT SV STATION-2 |  | FG_DET | PL312SV2 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516388 | PL312GDH212 | FLAMMABLE GAS DETECTOR AT SV STATION-2 | FLAMMABLE GAS DETECTOR AT SV STATION-2 |  | FG_DET | PL312SV2 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516393 | PL312GDH309 | FLAMMABLE GAS DETECTOR AT SV STATION-3 | FLAMMABLE GAS DETECTOR AT SV STATION-3 |  | FG_DET | PL312SV3 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516394 | PL312GDH310 | FLAMMABLE GAS DETECTOR AT SV STATION-3 | FLAMMABLE GAS DETECTOR AT SV STATION-3 |  | FG_DET | PL312SV3 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516395 | PL312GDH311 | FLAMMABLE GAS DETECTOR AT SV STATION-3 | FLAMMABLE GAS DETECTOR AT SV STATION-3 |  | FG_DET | PL312SV3 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516396 | PL312GDH312 | FLAMMABLE GAS DETECTOR AT SV STATION-3 | FLAMMABLE GAS DETECTOR AT SV STATION-3 |  | FG_DET | PL312SV3 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516397 | PL312GDH401 | FLAMMABLE GAS DETECTOR AT SV STATION-4 | FLAMMABLE GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516398 | PL312GDH402 | FLAMMABLE GAS DETECTOR AT SV STATION-4 | FLAMMABLE GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516400 | PL312GDH404 | FLAMMABLE GAS DETECTOR AT SV STATION-4 | FLAMMABLE GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516401 | PL312GDH409 | FLAMMABLE GAS DETECTOR AT SV STATION-4 | FLAMMABLE GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516402 | PL312GDH410 | FLAMMABLE GAS DETECTOR AT SV STATION-4 | FLAMMABLE GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516403 | PL312GDH411 | FLAMMABLE GAS DETECTOR AT SV STATION-4 | FLAMMABLE GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516404 | PL312GDH412 | FLAMMABLE GAS DETECTOR AT SV STATION-4 | FLAMMABLE GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516409 | PL312GDH509 | FLAMMABLE GAS DETECTOR AT SV STATION-5 | FLAMMABLE GAS DETECTOR AT SV STATION-5 |  | FG_DET | PL312SV5 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516410 | PL312GDH510 | FLAMMABLE GAS DETECTOR AT SV STATION-5 | FLAMMABLE GAS DETECTOR AT SV STATION-5 |  | FG_DET | PL312SV5 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516411 | PL312GDH511 | FLAMMABLE GAS DETECTOR AT SV STATION-5 | FLAMMABLE GAS DETECTOR AT SV STATION-5 |  | FG_DET | PL312SV5 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516412 | PL312GDH512 | FLAMMABLE GAS DETECTOR AT SV STATION-5 | FLAMMABLE GAS DETECTOR AT SV STATION-5 |  | FG_DET | PL312SV5 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516417 | PL312GDH609 | FLAMMABLE GAS DETECTOR AT SV STATION-6 | FLAMMABLE GAS DETECTOR AT SV STATION-6 |  | FG_DET | PL312SV6 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516418 | PL312GDH610 | FLAMMABLE GAS DETECTOR AT SV STATION-6 | FLAMMABLE GAS DETECTOR AT SV STATION-6 |  | FG_DET | PL312SV6 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518371 | M400FECP004 | FIRE SUPRESSION PANEL AT NEW ADMIN BUILDING | FIRE SUPRESSION PANEL AT NEW ADMIN BUILDING-ELECTRICAL ROOM |  | BLDGS | MMADMIN2 | 3 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518372 | M400XGC302 | FLAMMABLE GAS DETECTOR AT LOWER ROOF ADMIN BUILDING | FLAMMABLE GAS DETECTOR AT THE ROOF OF NEW ADMIN BUILDING HVAC DUCT INTAKE EAST SIDE, SECOND FROM LEFT |  | FG_DET | M400FAGP006 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518373 | M410FCP001 | FIRE CONTROL PANEL AT EMERGENCY DIESEL GENERATOR IRP-II | FIRE CONTROL PANEL AT EMERGENCY DIESEL GENERATOR ROOM IRP-II |  | F&G_PNL | M410EPB001 | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518374 | M410FGSC001 | FIRE & GAS SYSTEM, TRIPLE MODUAL REDUNDANT PANEL AT SIS | FIRE & GAS SYSTEM, TRIPLE MODUAL REDUNDANT PANEL IRP-II - SIS BUILDING |  | F&G_PNL | M410SIS | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518375 | M410FU006ICP | FIRE SUPPRESSION PANEL AT S/S-II BUILDING | FIRE SUPPRESSION PANEL AT SUB STATION BUILDING |  | F&G_PNL | M410SS | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518376 | M410FU007ICP | FIRE SUPRESSION PANEL AT SIS | FIRE SUPRESSION PANEL AT SIS BUILDING |  | F&G_PNL | M410SIS | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518377 | M410FU008ICP | FIRE SUPPRESSION PANEL AT EXT CONTROL ROOM | FIRE SUPPRESSION PANEL AT EXT CONTROL ROOM |  | F&G_PNL | MMECR | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969518378 | M410FU200 | FIRE ALARM RIM SEAL PANEL AT SIS | FARSP PANEL (FIRE ALARM RIM SEAL PANEL)-SIS |  | F&G_PNL | M410SIS | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516419 | PL312GDH611 | FLAMMABLE GAS DETECTOR AT SV STATION-6 | FLAMMABLE GAS DETECTOR AT SV STATION-6 |  | FG_DET | PL312SV6 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969418062 | PL300HPU2 | VALVE,SEQUENCIAL CONTROL/ESD, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE | HYDROLIC POWER UNIT IN SVS2 USED TO OPERATE 3 BALL VALVES,MP16"X900LB, NR10"X600LB, SRR12"X600LB. |  | SD_VLV | PL300SVS2 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969418064 | PL300HPU4 | VALVE,SEQUENCIAL CONTROL/ESD, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE | HYDROLIC POWER UNIT IN SVS4 USED TO OPERATE 3 BALL VALVES,MP16"X900LB, NR10"X600LB, SRR12"X600LB. |  | SD_VLV | PL300SVS4 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969418065 | PL300HPU5 | VALVE,SEQUENCIAL CONTROL/ESD, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE | HYDROLIC POWER UNIT IN SVS5 USED TO OPERATE 3 BALL VALVES,MP16"X900LB, NR10"X600LB, SRR12"X600LB. |  | SD_VLV | PL300SVS5 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969418066 | PL300HPU6 | VALVE,SEQUENCIAL CONTROL/ESD, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE | HYDROLIC POWER UNIT IN SVS6 USED TO OPERATE 3 BALL VALVES,MP16"X900LB, NR10"X600LB, SRR12"X600LB. |  | SD_VLV | PL300SVS6 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969418067 | PL300HPU7 | VALVE,SEQUENCIAL CONTROL/ESD, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE | HYDROLIC POWER UNIT IN SVS7 USED TO OPERATE 2 BALL VALVES, NR10"X600LB, SRR12"X600LB. |  | SD_VLV | PL300SVS7 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374433 | M410FU11 | RIM SEAL PROTECTION AT TANK-011(M410FU211A,M410FU211B,M410FU211C, M410FU211D,M410FU211E) | RIM SEAL PROTECTION AT TANK-011 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374434 | M410FU12 | RIM SEAL PROTECTION AT TANK-012(M410FU212A,M410FU212B,M410FU212C, M410FU212D,M410FU212E) | RIM SEAL PROTECTION AT TANK-012 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374435 | M410FU13 | RIM SEAL PROTECTION AT TANK-013(M410FU213A,M410FU213B,M410FU213C, M410FU213D,M410FU213E) | RIM SEAL PROTECTION AT TANK-013 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374436 | M410FU14 | RIM SEAL PROTECTION AT TANK-014(M410FU214A,M410FU214B,M410FU214C, M410FU214D,M410FU214E) | RIM SEAL PROTECTION AT TANK-014 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374437 | M410FU15 | RIM SEAL PROTECTION AT TANK-015(M410FU215A,M410FU215B,M410FU215C, M410FU215D,M410FU215E) | RIM SEAL PROTECTION AT TANK-015 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374438 | M410FU16 | RIM SEAL PROTECTION AT TANK-016(M410FU216A,M410FU216B,M410FU216C, M410FU216D,M410FU216E) | RIM SEAL PROTECTION AT TANK-016 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374439 | M410XGC001 | FLAMMABLE GAS DETECTORS AT EMERGENCY DIESEL GENERATOR ROOM IRP-II | FLAMMABLE GAS DETECTORS AT EMERGENCY DIESEL GENERATOR ROOM IRP-II |  | FG_DET | M410FCP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374440 | M410XGC002 | FLAMMABLE GAS DETECTORS AT EMERGENCY DIESEL GENERATOR ROOM IRP-II | FLAMMABLE GAS DETECTORS AT EMERGENCY DIESEL GENERATOR ROOM IRP-II |  | FG_DET | M410FCP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374441 | M410XGC003 | FLAMMABLE GAS DETECTORS AT EMERGENCY DIESEL GENERATOR ROOM IRP-II | FLAMMABLE GAS DETECTORS AT EMERGENCY DIESEL GENERATOR ROOM IRP-II |  | FG_DET | M410FCP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933173 | U2902L | PIG,LAUNCHER, 10 IN, API 5L X52/PSL 2 | PIG LAUNCHER FOR NAPHTA / REFORMATE PIPELINE. |  |  | S-PIG-LAUNCHERS | [14 empty] | Low | N | Low | N |  | 60 | i
933174 | U2903L | RECEIVER, PIG, 12IN , 600 LB , SRR , 94 kg/cm² , 95 Deg.C , API 5L X52/PSL 2 , A | PIG LAUNCHER FOR SRR PIPELINE. |  |  | S-PIG-LAUNCHERS | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933175 | M400PLR002 | PIG, LAUNCHER | NAPHTHA/REFORMATE PIPE LINE LAUNCHER |  |  | M400MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933176 | M400PLR003 | RECEIVER, PIG, 10IN , 600 LB , NAPHTHA/REFORMATE , 95.5 kg/cm² , 87 Deg.C , API | NAPHTHA/REFORMATE PIPE LINE RECEIVER |  |  | M400MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933177 | M400PLR006 | PIG, LAUNCHER, 12" | SRR PIPE LINE LAUNCHER |  |  | M400MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933178 | M400PLR007 | RECEIVER, PIG, 12IN , 600 LB , SRR , 94 kg/cm² , 95 Deg.C , API 5L X52/PSL 2 , A | SRR PIPE LINE RECEIVER |  |  | M400MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933179 | M400PLR011 | PIG, LAUNCHER | MULTI PRODUCTS PIPE LINE LAUNCHER |  |  | M400MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933180 | M400PLR012 | RECEIVER, PIG, 10IN , 900 LB , MULTI PRODUCTS , 143 kg/cm² , 87 Deg.C , API 5L X | MULTI PRODUCTS PIPE LINE RECEIVER |  |  | M400MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933181 | M400PLR016 | LAUNCHER, PIG, 10", 300 LB, JET A1, 47 kg/cm², 87 Deg.C, API 5L GRADE B/PS. | JET A1 PIPE LINE LAUNCHER TO ADIA AT800PLR102. |  |  | M400MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933182 | MQ600PLR013 | PIG LAUNCHER | MULTI PRODUCTS PIPE LINE LAUNCHER |  |  | MQ600MISC | 3 | 0 | 617101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933183 | MQ600PLR014 | PIG RECEIVER | MULTI PRODUCTS PIPE LINE RECEIVER |  |  | MQ600MISC | 3 | 0 | 617101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933184 | MQ600PLR015 | PIG LAUNCHER | MULTI PRODUCTS PIPE LINE LAUNCHER |  |  | MQ600MISC | 3 | 0 | 617101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933188 | AT800PLR102 | PIG RECEIVER | JET A1 PIPE LINE RECEIVER FROM M400PLR016. |  |  | AT800MISC | 2 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933189 | U29YYIS781 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  |  | U2902L | 2 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | U29YYIS781-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 10/06/19 | MC-PM-029-Y2
933190 | U29YYIS782 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  |  | U2902L | 2 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | U29YYIS782-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 10/06/19 | MC-PM-029-Y2
933191 | U29YYIS783 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  |  | U2903L | 2 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | U29YYIS783-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 11/07/19 | MC-PM-029-Y2
933192 | U29YYIS784 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  |  | U2903L | 2 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | U29YYIS784-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 11/07/19 | MC-PM-029-Y2
933193 | PL300YYIS3011A | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS1 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933194 | PL300YYIS3011B | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS1 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933195 | PL300YYIS3012A | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS2 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933196 | PL300YYIS3012B | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS2 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933197 | PL300YYIS3013A | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS3 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933198 | PL300YYIS3013B | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS3 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933199 | PL300YYIS3014A | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS4 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933200 | PL300YYIS3014B | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS4 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933201 | PL300YYIS3015A | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS5 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933202 | PL300YYIS3015B | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS5 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933203 | PL300YYIS3016A | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS6 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933204 | PL300YYIS3016B | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS6 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933205 | PL300YYIS3017A | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS7 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933206 | PL300YYIS3017B | SCRAPER SIGNALLER | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS7 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933207 | PL300YYIS3021A | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS1 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933208 | PL300YYIS3021B | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS1 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933209 | PL300YYIS3022A | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS2 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933210 | PL300YYIS3022B | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS2 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933211 | PL300YYIS3023A | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS3 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933212 | PL300YYIS3023B | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS3 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933213 | PL300YYIS3024A | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS4 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933214 | PL300YYIS3024B_ | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS4 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933215 | PL300YYIS3025A | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS5 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933216 | PL300YYIS3025B | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS5 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933217 | PL300YYIS3026A | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS6 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933218 | PL300YYIS3026B | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS6 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933219 | PL300YYIS3027A | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS7 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933220 | PL300YYIS3027B | SCRAPER SIGNALLER | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS7 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933221 | PL300YYIS3031A | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS1 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933222 | PL300YYIS3031B | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS1 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933223 | PL300YYIS3032A | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS2 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933224 | PL300YYIS3032B | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS2 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933225 | PL300YYIS3033A | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS3 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933226 | PL300YYIS3033B | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS3 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933227 | PL300YYIS3034A | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS4 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933228 | PL300YYIS3034B | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS4 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933229 | PL300YYIS3035A | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS5 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933230 | PL300YYIS3035B | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS5 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933231 | PL300YYIS3036A | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS6 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933232 | PL300YYIS3036B | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  | MAG_TXTR | PL300SVS6 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933233 | M400YYIS501 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  |  | M400MISC | 2 | LMT_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400YYIS501-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 12/08/19 | MC-PM-029-Y2
933234 | M400YYIS502 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS502-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 12/08/19 | MC-PM-029-Y2
933235 | M400YYIS503 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS503-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 13/09/19 | MC-PM-029-Y2
933236 | M400YYIS504 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | NAPHTHA / REFORMATE SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS504-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 13/09/19 | MC-PM-029-Y2
933237 | M400YYIS566 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS566-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 14/10/19 | MC-PM-029-Y2
933238 | M400YYIS567 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS567-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 14/10/19 | MC-PM-029-Y2
933239 | M400YYIS568 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS568-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 20/07/19 | MC-PM-029-Y2
933240 | M400YYIS569 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | STRAIGHT RUN RESIDUE SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS569-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 20/07/19 | MC-PM-029-Y2
933241 | M400YYIS651 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | MULTI PRODUCT SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS651-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 14/08/19 | MC-PM-029-Y2
933242 | M400YYIS652 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | MULTI PRODUCT SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS652-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 14/08/19 | MC-PM-029-Y2
933243 | M400YYIS801 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | JET A1 SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS801-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 13/09/19 | MC-PM-029-Y2
933244 | M400YYIS802 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | AL AIN SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS802-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 13/09/19 | MC-PM-029-Y2
933245 | M400YYIS881 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | MULTI PRODUCT AL AIN SCRAPER SIGNALLERSCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS881-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 14/10/19 | MC-PM-029-Y2
933246 | M400YYIS882 | SCRAPER SIGNALLER, NO MODIFIER, Bi-directional , visual flag & snap acting micro | MULTI PRODUCT SCRAPER SIGNALLER |  |  | M400MISC | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | M400YYIS882-MC1 | ACTIVE | CONT | PM | EDS | 2 | YEARS | 14/10/19 | MC-PM-029-Y2
933247 | MQ600YYIS001 | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  |  | MQ600MISC | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933248 | MQ600YYIS002 | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  |  | MQ600MISC | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933249 | MQ600YYIS003 | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  |  | MQ600MISC | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933250 | MQ600YYIS004 | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  |  | MQ600MISC | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933251 | MQ600YYIS005 | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  |  | MQ600MISC | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933252 | MQ600YYIS006 | SCRAPER SIGNALLER | MULTI PRODUCT SCRAPER SIGNALLER |  |  | MQ600MISC | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933259 | AT800YYIS101 | SCRAPER SIGNALLER | JET A1 SCRAPER SIGNALLER |  |  | AT800MISC | 2 | MAG_TXTR | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933260 | AT800YYIS102 | SCRAPER SIGNALLER | JET A1 SCRAPER SIGNALLER |  |  | AT800MISC | 2 | MAG_TXTR | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933261 | M20MOV861 | ACTUATOR, ELECTRIC MOTOR, JET A1 , 18.4 , MOTORISED , AUDCO , 415V , 3 , 50HZ , | JET A1, 10" X 8" CL 150 |  | MOV | M20MOTOR | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933262 | M20MOV862 | ACTUATOR, ELECTRIC MOTOR, JET A1 , 18.4 , MOTORISED , ADUCO , 415V , 3 , 50HZ , | JET A1, 6" CL 150 |  | MOV | M20MOTOR | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933263 | M20MOV863 | ACTUATOR, ELECTRIC MOTOR, JET A1 , 18.4 , MOTORISED , AUDCO , 415V , 3 , 50HZ , | JET A1, 10" X 8" CL 150 |  | MOV | M20MOTOR | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933264 | M20MOV864 | ACTUATOR, ELECTRIC MOTOR, JET A1 , 18.4 , MOTORISED , ADUCO , 415V , 3 , 50HZ , | JET A1, 6" CL 150 |  | MOV | M20MOTOR | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933265 | AA213MOV146 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ12F10B4, IP68, 203Nm | MOV IN ALAIN RECEIVING STATION, GAS OIL, 10" X 8" CL 150. |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933266 | AA213MOV147 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ12F10B4, IP68, 203Nm | MOV IN ALAIN RECEIVING STATION, GAS OIL, 10" X 8" CL 150 |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933267 | AA213MOV148 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV IN ALAIN RECEIVING STATION, GAS OIL, 12" X 10" CL 150-WITH EXTN LG 1680MM |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933268 | AA213MOV149 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV IN ALAIN RECEIVING STATION, GAS OIL, 12" X 10" CL 150-WITH EXTN LG 2170MM |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130805 | M400MP203A | MOTOR,ELECTRIC, FIRE WATER JOCKEY PUMP, 30 KW, 50 HZ, 415 V, S1, M3BP 200MLA2, 6312C3/6310C3, 2960 RPM, 3, 52 AMP, COUNTER CLOCK WISE, F | MOTOR FOR FIRE WATER JOCKEY PUMP AT FIRE WATER PUMP HOUSE |  | MOTOR | M400P203A | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MP203A-ME1 | ACTIVE | ELEC | PM | FIM | 6 | MONTHS | 18/08/18 | ME-PM-014-M6
969130807 | M400MP204A | MOTOR,ELECTRIC, PORTABLE WATER PUMP, IP55, 50 HZ, 415 V, S1, 3 | MOTOR FOR PORTABLE WATER PUMP NEAR WAREHOUSE |  | MOTOR | M400P204A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP204A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 20/08/18 | ME-PM-014-M6
969130809 | M400MP205A | MOTOR,ELECTRIC, WASTE WATER OILY PUMP, IP55, 18.5 KW, 50 HZ, 415 V, S1, Ex n A, 180MLB, DDE-6310/C3 , NDE-6309/C3, VERTICAL, 3, STAR, 34 AMP, F, II T3, 214 KG | MOTOR FOR WASTE WATER OILY PUMP-A |  | MOTOR | M400P205A | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MP205A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/09/18 | ME-PM-014-M6
969130810 | M400MP075 | MOTOR,ELECTRIC, MOTOR FOR SUMP PUMP, 5.5 KW, 50 HZ, 415 V, M3JP 132SMB 2V1, 6205 2ZC3/6204 2ZC3, 2892 RPM, 3, 10.5 AMP | MOTOR FOR SUMP PUMP |  | MOTOR | M400P075 | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 5 | 5 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP075-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 09/12/18 | ME-PM-014-M6
969130811 | M400MP076 | MOTOR,ELECTRIC, MOTOR FOR SUMP PUMP, 9.2 KW, 50 HZ, 415 V, S1, M3JP 132SME 2V1, 6208 2Z C3/6208 2Z C3, 2892 RPM, 3, 16.6 AMP, F | MOTOR FOR SUMP PUMP |  | MOTOR | M400P076 | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP076-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 22/01/19 | ME-PM-014-M6
969130806 | M400MP203B | MOTOR,ELECTRIC, FIRE WATER JOCKEY PUMP, 30 KW, 50 HZ, 415 V, S1, M3BP 200MLA2, 6312C3/6310C3, 2960 RPM, 3, 52 AMP | MOTOR FOR FIRE WATER JOCKEY PUMP AT FIRE WATER PUMP HOUSE |  | MOTOR | M400P203B | 1 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MP203B-ME1 | ACTIVE | ELEC | PM | FIM | 6 | MONTHS | 02/09/18 | ME-PM-014-M6
969130808 | M400MP204B | MOTOR,ELECTRIC, PORTABLE WATER PUMP, 50 HZ, 415 V | POTABLE WATER PUMP MOTOR NEAR WAREHOUSE |  | MOTOR | M400P204B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP204B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/09/18 | ME-PM-014-M6
969132260 | M400XGC001 | DETECTOR, FLAMMABLE GAS | Flammable GD for HVAC ROOM-PLCR |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC001-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132261 | M400XGC004 | DETECTOR, FLAMMABLE GAS | Flammable GD for SUB-STATION HVAC ROOM |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC004-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132262 | M400XGC009 | DETECTOR, FLAMMABLE GAS | Flammable GD for HVAC ROOM OF ADMINSTRATION BUILDING |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC009-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132263 | M400XGC005 | DETECTOR, FLAMMABLE GAS | Flammable GD for SUB-STATION HVAC ROOM |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC005-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132264 | M400XGC008 | DETECTOR, FLAMMABLE GAS | Flammable GD for HVAC ROOM OF ADMINSTRATION BUILDING |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC008-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132265 | M400XGC002 | DETECTOR, FLAMMABLE GAS | Flammable GD for HVAC ROOM-PLCR |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC002-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132266 | M400XGC003 | DETECTOR, FLAMMABLE GAS | Flammable GD for HVAC ROOM-PLCR |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC003-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132267 | M400XGC007 | DETECTOR, FLAMMABLE GAS | Flammable GD for HVAC ROOM OF ADMINSTRATION BUILDING |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC007-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969132268 | M400XGC006 | DETECTOR, FLAMMABLE GAS | Flammable GD for SUB-STATION HVAC ROOM |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC006-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/08/18 | MFPS-PM02.M3
969131549 | M400XSP128 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN HVAC AIR INTAKE DUCT OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131550 | M400XSP131 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN FOAM STORAGE ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131551 | M400XSP132 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN AIR COMPRESSOR ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131552 | M400XSP133 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CO2 & N2 ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131558 | M400XSP139 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN OFFICE STAFF ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131564 | M400XSP145 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN TRAINING ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131571 | M400XSP161 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN PALLET AREA IN WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131602 | M400XHE017 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT TRANSFORMER M400-TML001A IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131605 | M400XHE020 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR FOR 400-EPB-001 IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131606 | M400XHE021 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR FOR BATTERY ROOM IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131622 | M400XAC004 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT CORRIDOR-PLCR |  | PB_HS-MC | M400FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC004-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 24/09/18 | MFPS-PM07.M3
969131625 | M400XAC011 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT NEAR 400TMM001A & NER001 ROOM |  | PB_HS-MC | M400FACP002 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC011-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 21/10/18 | MFPS-PM07.M3
969131626 | M400XAC012 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT SUB STATION BUILDING ENTRANCE |  | PB_HS-MC | M400FACP002 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC012-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 21/10/18 | MFPS-PM07.M3
969131627 | M400XAC013 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT SUB STATION BUILDING |  | PB_HS-MC | M400FACP002 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC013-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 21/10/18 | MFPS-PM07.M3
969131553 | M400XSP134 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CO2 & N2 ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131632 | M400XAC022 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT ADMINISTRATION BUILDING |  | PB_HS-MC | M400FACP004 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC022-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969131635 | M400XAC031 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT OUTSIDE AIR COMPRESSOR & FOAM STORAGE-FIRE STATION |  | PB_HS-MC | M400FACP003 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC031-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969131636 | M400XAC032 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT OUTSIDE STAFF OFFICE-FIRE STATION BUILDING |  | PB_HS-MC | M400FACP003 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC032-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969131637 | M400XAC034 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT LOBBY AREA-FIRE STATION BUILDING |  | PB_HS-MC | M400FACP003 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC034-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969131638 | M400XAC035 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT LOBBY AREA-FIRE STATION BUILDING |  | PB_HS-MC | M400FACP003 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC035-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969131639 | M400XAC040 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT WEST SIDE OF WAREHOUSE |  | PB_HS-MC | M400FACP005 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC040-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 23/10/18 | MFPS-PM07.M3
969131641 | M400XAC042 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT OUTSIDE SUPERVISOR'S OFFICE IN WAREHOUSE. |  | PB_HS-MC | M400FACP005 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC042-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 23/10/18 | MFPS-PM07.M3
969131666 | M400XAL006 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT TELECOM ROOM-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131669 | M400XAL009 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT HVAC ROOM-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131670 | M400XAL020 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT SWITCHGEAR ROOM SUB STATION |  | ALARMANC | M400FACP002 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131554 | M400XSP135 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN ENTRANCE LOBBY OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131662 | M400XAL002 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT CONTROL ROOM-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131663 | M400XAL003 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT UPS ROOM-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131664 | M400XAL004 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT BATTERY ROOM-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131665 | M400XAL005 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT SCADA ROOM-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131671 | M400XAL021 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT SWITCHGEAR ROOM SUB STATION |  | ALARMANC | M400FACP002 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131672 | M400XAL022 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT HVAC ROOM SUB STATION |  | ALARMANC | M400FACP002 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131673 | M400XAL023 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT BATTERY ROOM SUB STATION |  | ALARMANC | M400FACP002 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131674 | M400XAL025 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT CORRIDOR OF ADMINISTRATION BUILDING |  | ALARMANC | M400FACP004 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131675 | M400XAL026 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT CORRIDOR OF ADMINISTRATION BUILDING |  | ALARMANC | M400FACP004 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131677 | M400XAL031 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT ENTRANCE LOBBY AREA OF FIRE STATION BUILDING |  | ALARMANC | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131678 | M400XAL032 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT OUTSIDE STAFF OFFICE OF FIRE STATION BUILDING |  | ALARMANC | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131555 | M400XSP136 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN ENTRANCE LOBBY OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131556 | M400XSP137 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN TOILET OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131557 | M400XSP138 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CHANGING ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131559 | M400XSP140 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN OFFICE STAFF ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131560 | M400XSP141 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN PANTRY ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131561 | M400XSP142 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN WORK STATION & LAB AREA OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131562 | M400XSP143 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN DRY POWDER FILLING STATION OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131563 | M400XSP144 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN TRAINING ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131565 | M400XSP146 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN LOBBY AREA OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131566 | M400XSP147 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN TOILET OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131567 | M400XSP148 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN OFFICE ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131568 | M400XSP149 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SUPERVISOR ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131569 | M400XSP150 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SAFEY ENGINEER ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131570 | M400XSP151 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SAFEY ENGINEER ROOM OF FIRE STATION |  | FG_DET | M400FACP003 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMA57224 | SALAIN12DTPM101 | Motor for Circulation Pump 110V | Motor for Circulation Pump 110V |  | MOTOR | SALAINDMS1 | 3 | MOTOR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMA57571 | M40PM172 | MOTOR, ELECTRIC, SLOPS LOADING MOTOR , SEE DUTY CYCLE , IP 55 , 4.7 KW, 50 HZ, 4 | SLOPS LOADING MOTOR ADNOC DIST. |  | MOTOR | M40P172 | 2 | MOTOR | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M40PM172-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 20/08/18 | ME-PM-014-M6
EMA57572 | M40PM173 | MOTOR, ELECTRIC, SLOPS LOADING MOTOR , SEE DUTY CYCLE , IP 55 , 4.7 KW, 50 HZ, 4 | SLOPS LOADING MOTOR ADNOC DIST. |  | MOTOR | M40P173 | 2 | MOTOR | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M40PM173-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 18/09/18 | ME-PM-014-M6
939532 | M400VH002A | MANUAL HOIST FOR DG SET | MANUAL HOIST FOR DIESEL GENERATOR. |  | CRHO | M400EPB001 | 4 | CRHO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939537 | M400VH002B | MANUAL HOIST FOR DG SET | MANUAL HOIST FOR DIESEL GENERATOR. |  | CRHO | M400EPB001 | 4 | CRHO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933410 | M400MOV085 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-104 OUTLET HEADER (GAS OIL, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV085-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
933411 | M400MOV086 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-104 OUTLET HEADER (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV086-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/02/19 | ME-PM-002-M6
933412 | M400MOV087 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-104 OUTLET ISOLATION (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV087-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/01/19 | ME-PM-002-M6
933413 | M400MOV088 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-104 TO LOADING PUMP 221B,C & D.(GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV088-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/01/19 | ME-PM-002-M6
933414 | M400MOV091 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-117 OUTLET SHELL VALVE (JET A1, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV091-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/09/18 | ME-PM-002-M6
933415 | M400MOV092 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-117 OUTLET ISOLATION.(JET A1, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV092-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
933416 | M400MOV093 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-117 TO LOADING PUMP 227A,B & C.(JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV093-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
933417 | M400MOV094 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-117 OUTLET HEADER (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV094-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/09/18 | ME-PM-002-M6
933418 | M400MOV095 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-117 OUTLET HEADER (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV095-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/01/19 | ME-PM-002-M6
933419 | M400MOV096 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 12 SEC, 6" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-117 INLET HEADER LINE.(JET A1, 6" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV096-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
933420 | M400MOV097 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-117 INLET HEADER LINE.(JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV097-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/09/18 | ME-PM-002-M6
933421 | M400MOV098 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-117 INLET ISOLATION (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV098-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/09/18 | ME-PM-002-M6
933422 | M400MOV099 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-117 INLET SHELL LINE (JET A1, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV099-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
933423 | M400MOV100 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-118 OUTLET SHELL VALVE (JET A1, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV100-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
933424 | M400MOV101 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-118 OUTLET ISOLATION (JET A1 MOV FROM TANK T118, 18" X 16" CL 150.) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV101-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
933425 | M400MOV102 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-118 LOADING TO PUMP 227A,B & C.(JET A1, 14" X 12" CL 150 ON TANK 118.) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV102-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/01/19 | ME-PM-002-M6
933426 | M400MOV103 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-118 OUTLET HEADER (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV103-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/09/18 | ME-PM-002-M6
933427 | M400MOV104 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-118 OUTLET HEADER.(JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV104-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/01/19 | ME-PM-002-M6
933428 | M400MOV105 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 12 SEC, 6" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-118 INLET HEADER (JET A1, 6" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV105-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/09/18 | ME-PM-002-M6
933429 | M400MOV106 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-118 INLET HEADER (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV106-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/09/18 | ME-PM-002-M6
933430 | M400MOV107 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-118 INLET ISOLATION (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV107-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/09/18 | ME-PM-002-M6
933431 | M400MOV108 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-118 INLET SHELL VALVE (JET A1, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV108-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
933432 | M400MOV109 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-117 OUTLET HEADER.(JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV109-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933433 | M400MOV110 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-118 OUTLET HEADER.(JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV110-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/09/18 | ME-PM-002-M6
933434 | M400MOV111 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-105 INLET ISOLATION (ULG 98, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV111-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/01/19 | ME-PM-002-M6
933435 | M400MOV112 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-105 INLET HEADER (ULG 98, 10" X 8" CL 300 WITH EXTN LG 2000MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV112-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/01/19 | ME-PM-002-M6
933436 | M400MOV113 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" X 6" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-105 INLET HEADER (ULG 98, 8" X 6" CL 300 WITH EXTN LG 2030MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV113-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/02/19 | ME-PM-002-M6
933437 | M400MOV114 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-105 OUTLET HEADER (ULG 98, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV114-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/02/19 | ME-PM-002-M6
933438 | M400MOV115 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-105 OUTLET HEADER.(ULG 98, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV115-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/02/19 | ME-PM-002-M6
933439 | M400MOV116 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-105 OUTLET ISOLATION (ULG 98, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV116-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/02/19 | ME-PM-002-M6
933440 | M400MOV117 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-105 TO LOADING PUMP 222-223 (ULG 98, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV117-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/01/19 | ME-PM-002-M6
933441 | M400MOV118 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-106 INLET ISOLATION (ULG 98, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV118-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/11/18 | ME-PM-002-M6
969132635 | M400MOV702 | ACTUATOR,ELECTRIC MOTOR | COMPRESSOR VENTING REQ, FOR MOV AT WWTP SUMP CHAIN-II |  | MOV | M400WWTP | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV702-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/12/18 | ME-PM-002-M6
934037 | M400UPSAC001A | POWER SUPPLY UNINTERRUPTED | AC POWER SUPPLY UNINTERRUPTED |  | INVRT_UP | M400BATT | 1 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400UPSAC001A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 10/11/18 | ME-PM-017-M6
934038 | M400UPSAC001B | POWER SUPPLY UNINTERRUPTED | AC POWER SUPPLY UNINTERRUPTED |  | INVRT_UP | M400BATT | 1 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400UPSAC001B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 17/11/18 | ME-PM-017-M6
934039 | M400UPSAC002A | POWER SUPPLY UNINTERRUPTED | AC POWER SUPPLY UNINTERRUPTED |  | INVRT_UP | M400BATT | 1 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400UPSAC002A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/11/18 | ME-PM-017-M6
934040 | M400UPSAC002B | POWER SUPPLY UNINTERRUPTED | AC POWER SUPPLY UNINTERRUPTED |  | INVRT_UP | M400BATT | 1 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400UPSAC002B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 02/12/18 | ME-PM-017-M6
934045 | AT800UPSAC6 | POWER SUPPLY UNINTERRUPTED | AC POWER SUPPLY UNINTERRUPTED |  | INVRT_UP | AT800BATT | 3 | INVRT_UP | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | Y | AT800UPSAC6-ME1 | INACTIVE |  | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-017-M6
934049 | M20P227A | PUMP, CENTRIFUGAL, HORIZONTAL OH2 , JET A1 ROAD LOADING PUMPS , CENTERLINE , IN | JET A1 ROAD LOADING PUMPS |  | PUCE | M20PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934050 | M20P227B | PUMP, CENTRIFUGAL, HORIZONTAL OH2 , JET A1 ROAD LOADING PUMPS , CENTERLINE , IN | JET A1 ROAD LOADING PUMPS |  | PUCE | M20PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934051 | M400P021A | PUMP, CENTRIFUGAL, VERTICAL, VS 6 , ULG95/ULG98/ INTER TANK TRANSFER PUMPS , SEP | ULG95/ULG98/ INTERNAL TANK TRANSFER PUMP-A. |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P021A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/12/18 | MM-PM-007-M6
934052 | M400P021B | PUMP, CENTRIFUGAL, VERTICAL, VS 6 , ULG95/ULG98/ INTER TANK TRANSFER PUMPS , SEP | ULG95/ULG98/ INTERNAL TANK TRANSFER PUMP-B |  | PUCE | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P021B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-007-M6
934053 | M400P021C | PUMP, CENTRIFUGAL, VERTICAL, VS 6 , ULG95/ULG98/ INTER TANK TRANSFER PUMPS , SEP | ULG95/ULG98/ INTERNAL TANK TRANSFER PUMP-C. |  | PUCE | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P021C-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/08/18 | MM-PM-007-M6
934250 | M400PG862 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS | Booster Pump 400-P-015B Suction Pr. | 933875 |  | M400P015B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934251 | M400PG883 | GAUGE, PRESSURE, INDICATION , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. at Mussafah-Al Ain MP Tie-In P/L |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934252 | M400PG885 | GAUGE, PRESSURE, INDICATION , 0-250 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | 400-P-016A Discharge Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934253 | M400PG888 | GAUGE, PRESSURE, INDICATION , 0-250 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | 400-P-016B Discharge Pressure | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934254 | M400PG898 | GAUGE, PRESSURE, INDICATION , 0-250 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. at Mussafah-Al Ain MP Tie-In P/L to 400-PLR-01 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934255 | M400PG901 | GAUGE, PRESSURE, INDICATION , 0-250 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pressure at 400-PLR-012 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934256 | M400PG902 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pressure at 400-PLR-012 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934257 | M400PG903 | GAUGE, PRESSURE, INDICATION , 0-250 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. at Mussafah-Al Ain MP Tie-In P/L to Tie in Poi |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934258 | M400PG904 | GAUGE, PRESSURE, INDICATION , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | 400-P-016A Suction Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934259 | M400PG905 | GAUGE, PRESSURE, INDICATION , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | SUCTION PRESSURE GAUGE FOR 400P016A | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934260 | M400PG926 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pressure at Suction side of 400-P-080A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934261 | M400PG927 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pressure at Discharge side of 400-P-080A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934262 | M400PG928 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Suction Line 400-P-203A |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934263 | M400PG929 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Suction Line 400-P-203B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934264 | M400PG930 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Suction Line 400-P-201A | 936404 |  | M400P201A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934265 | M400PG931 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Suction Line 400-P-201B | 936405 |  | M400P201B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934266 | M400PG932 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | inlet Pressure to 400-FT-620A/B/C |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934267 | M400PG933 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Outlet Pressure from 400-FT-620A/B/C |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934268 | M400PG934 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | inlet Pressure to 400-FT-861A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934269 | M400PG935 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Outlet Pressure from 400-FT-861A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934270 | M400PG936 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pump 400-P-080A Disc.Line | 934060 |  | M400P080A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934271 | M400PG937 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pump 400-P-080B Disc.Line | 934061 |  | M400P080B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934272 | M400PG938 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Mussafah-Adia Jet A1 P/L inlet to 400-FT-771A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934273 | M400PG939 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Mussafah-Adia Jet A1 P/L Outlet from 400-FT-771A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934274 | M400PG940 | GAUGE, PRESSURE, INDICATION , 0-3 KG/CM2 , 100MM , 1/2" MNPT , SS 316L , 316L SS | Suction Line 400-P-203A | 936409 |  | M400P203A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 1 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934275 | M400PG941 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Line 400-P-203A | 936409 |  | M400P203A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934276 | M400PG942 | GAUGE, PRESSURE, INDICATION , 0-3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Suction Line 400-P-203B | 936410 |  | M400P203B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934277 | M400PG943 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Line 400-P-203B | 936410 |  | M400P203B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934278 | M400PG944 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Suction Line 400-P-201A | 936404 |  | M400P201A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934279 | M400PG945 | GAUGE, PRESSURE, INDICATION , 0-25 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Line 400-P-201A | 936404 |  | M400P201A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934280 | M400PG946 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Suction Line 400-P-201B | 936405 |  | M400P201B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934281 | M400PG947 | GAUGE, PRESSURE, INDICATION , 0-25 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Line 400-P-201B | 936405 |  | M400P201B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934282 | M400PG948 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Suction Line 400-P-201C | 936406 |  | M400P201C | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934283 | M400PG949 | GAUGE, PRESSURE, INDICATION , 0-25 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Line 400-P-201C | 936406 |  | M400P201C | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934284 | M400PG950 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Suction Line 400-P-202 |  |  | M400P202 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934285 | M400PG951 | GAUGE, PRESSURE, INDICATION , 0-25 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Line 400-P-201C |  |  | M400P201C | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934286 | M400PG952 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Press.At Potable Water U/G Storage 400-V-117 | 938645 |  | M400V117 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934287 | M400PG953 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Press.At Potable Water U/G Storage 400-V-117 | 938645 |  | M400V117 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934288 | M400PG954 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Bladder Vessel 400-V-178 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934289 | M400PG955 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Suction Line 400-P-201D | 936407 |  | M400P201D | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934290 | M400PG957 | GAUGE, PRESSURE, INDICATION , 0-4 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Gas Oil Storage Tank 400-V-179 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934291 | MQ600PG002 | GAUGE PRESSURE | Pressure at 600-PLR-013 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934292 | MQ600PG003 | GAUGE PRESSURE | Pressure at 600-PLR-013 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934293 | MQ600PG004 | GAUGE PRESSURE | Pressure at 600-PLR-013 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934294 | MQ600PG005 | GAUGE PRESSURE | Pr. at Mussafah -Al Ain MultiProduct Tie-In P/L |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934295 | MQ600PG009 | GAUGE PRESSURE | Pressure at 600-PLR-014 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934296 | MQ600PG010 | GAUGE PRESSURE | Pressure at 600-PLR-014 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934297 | MQ600PG011 | GAUGE PRESSURE | Pressure at 600-PLR-014 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934298 | MQ600PG012 | GAUGE PRESSURE | Pressure at 600-PLR-015 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934299 | MQ600PG013 | GAUGE PRESSURE | Pressure at 600-PLR-015 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934300 | MQ600PG014 | GAUGE PRESSURE | Pressure at 600-PLR-015 |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934301 | MQ600PG015 | GAUGE PRESSURE | PRESSURE GAUGE |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934302 | MQ600PG017 | GAUGE PRESSURE | PRESSURE GAUGE |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934303 | MQ600PG018 | GAUGE PRESSURE | PRESSURE GAUGE |  |  | MQ600PRESS | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132035 | PL300BATT003A | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V | BATTERY BANK-A =38 Nos FOR SV-3. |  | BATTERY | PL300BAT003 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939331 | U29PT670 | TRANSMITTER, PRESSURE, ELECTRONIC , 0-150 KG/CM2 , 10.5 - 36vdc , 1/2" - 14 NPTF | SRR Main Pumps 2937-JA/B/C to 2903-L/302-PL-002 | 939411 | PRES_TX | U29PI670 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939576 | U29TI710 | LOOP, TEMPERATURE INDICATOR INSTRU, ENDRESS HAUSER , TMT162-RB4A41N31XB + TEMP | TEMP. SRR MAIN PUMPS 2937JA/B/C TO 2903L | 933174 | OPENLOOP | U2903L | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29TI710-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/05/19 | MC-PM-010-Y1
939579 | U29TI711 | LOOP, TEMPERATURE INDICATOR INSTRU, ENDRESS HAUSER , TMT162-RB4A41N31XB + TEMP | TEMP. 2903L SCRAPER LAUNCHER-SV STATION-7 | 933174 | OPENLOOP | U2903L | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29TI711-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/05/19 | MC-PM-010-Y1
939587 | M400VH004B | MANUAL HOIST FOR INTERTANK TRANSFER PUMP HOUSE | MANUAL HOIST FOR INTERTANK TRANSFER PUMP HOUSE |  | CRHO | MPH2 | 4 | CRHO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939588 | M400VH005 | MANUAL HOIST TRANSFER/FW PUMP HOUSE | MANUAL HOIST FOR INTERTANK TRANSFER PUMP HOUSE |  | CRHO | MPH2 | 4 | CRHO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939589 | M400V301 | ISO CONTAINER FOR PPD ADDITIVE | ISO CONTAINER FOR PPD ADDITIVE |  | VESSEL | M400TANKS | 3 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 5 | 1 | 1 | 1 | 2.0969 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939590 | M400V302 | ISO CONTAINER FOR LI ADDITIVE | ISO CONTAINER FOR LI ADDITIVE |  | VESSEL | M400TANKS | 2 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939591 | M400AG301 | MOTOR,ELECTRIC, PPD ADDITIVE TANK MIXER, IP65, 2.2 KW, 50 HZ, 415 V, S1, M2BA 100L4B, 6206C3/6206C3, 1415 RPM, 3, 6.5 AMP, F | MOTOR, PPD ADDITIVE TANK MIXER |  | MOTOR | M400T301 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | Y | M400AG301-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 08/12/18 | ME-PM-014-M6
939593 | M400AG302 | MOTOR,ELECTRIC, LUBRICITY ADDITIVE MIXER, IP 65, 2.2 KW, 50 HZ, 415 V, S1, M2BA 100L4B, 6206 C3/6206 C3, 1415 RPM, 3, 6.5 AMP, F | MOTOR, LUBRICITY ADDITIVE VESSEL MIXER. |  | MOTOR | M400T302 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | Y | M400AG302-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 08/01/19 | ME-PM-014-M6
939594 | M400E301 | ELECTRIC HEATER FOR PPD ADDITIVE MIXING TANK | ELECTRIC HEATER FOR PPD ADDITIVE MIXING TANK |  | ELEC_HTR | M400T301 | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939595 | M400E302 | ELECTRIC HEATER FOR PPD ISO CONTAINER | ELECTRIC HEATER FOR PPD ISO CONTAINER |  | ELEC_HTR | M400T302 | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939596 | M400E303 | ELECTRIC HEATER FOR LI ADDITIVE MIXING TANK | ELECTRIC HEATER FOR LI ADDITIVE MIXING TANK |  | ELEC_HTR |  | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939597 | M400E304 | ELECTRIC HEATER FOR LI ISO CONTAINER | ELECTRIC HEATER FOR LI ISO CONTAINER |  | ELEC_HTR |  | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939598 | M400V179 | GENERATOR GAS OIL STORAGE TANK | GAS OIL STORAGE TANK |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 10 | 10 | 10 | 5 | 5 | 5 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939599 | M400V180A | FIRE GAS OIL STORAGE TANK | GAS OIL STORAGE VESSEL |  | VESSEL | M400TANKS | 2 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939600 | M400V180B | FIRE GAS OIL STORAGE TANK | GAS OIL STORAGE VESSEL |  | VESSEL | M400TANKS | 2 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939601 | M400V180C | FIRE GAS OIL STORAGE TANK | GAS OIL STORAGE VESSEL |  | VESSEL | M400TANKS | 2 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939602 | M400V180D | FIRE GAS OIL STORAGE TANK | GAS OIL STORAGE VESSEL |  | VESSEL | M400TANKS | 2 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933482 | M400MOV192 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-120 TO LOADING PUMP 227A,B, & C (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV192-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/01/19 | ME-PM-002-M6
933483 | M400MOV193 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-120OUTLET HEADER (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV193-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933484 | M400MOV194 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-120 OUTLET HEADER (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV194-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/01/19 | ME-PM-002-M6
933485 | M400MOV195 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 12 SEC, 6" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-120INLET HEADER (JET A1, 6" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV195-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933486 | M400MOV196 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-120 INLET HEADER (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV196-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/09/18 | ME-PM-002-M6
933487 | M400MOV197 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-120 INLET ISOLATION VALVE (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV197-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/09/18 | ME-PM-002-M6
933488 | M400MOV198 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-120 INLET SHELL (JET A1, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV198-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933489 | M400MOV199 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-119 OUTLET HEADER (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV199-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933490 | M400MOV200 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-120 OUTLET HEADER (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV200-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933491 | M400MOV201 | ACTUATOR,ELECTRIC MOTOR, SLOP, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-109 INLET ISOLATION (SLOP, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV201-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/02/19 | ME-PM-002-M6
933492 | M400MOV202 | ACTUATOR,ELECTRIC MOTOR, SLOP, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-109 INLET HEADER (SLOP, 10" X 8" CL 300 WITH EXTN LG 1680MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV202-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/02/19 | ME-PM-002-M6
933493 | M400MOV203 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-109 OUTLET VALVE TO TRANSFER (SLOP, 8" X 6" CL 150 WITH EXTN LG 1370) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV203-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
933494 | M400MOV204 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-109 TO LOADING PUMP (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV204-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/09/18 | ME-PM-002-M6
933495 | M400MOV205 | ACTUATOR,ELECTRIC MOTOR, SLOP, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-110 INLET ISOLATION (SLOP, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MOV205-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/09/18 | ME-PM-002-M6
933496 | M400MOV206 | ACTUATOR,ELECTRIC MOTOR, SLOP, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-110 INLET HEADER (SLOP, 10" X 8" CL 300 WITH EXTN LG 1680MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV206-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/09/18 | ME-PM-002-M6
933497 | M400MOV207 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80 EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-110 OUTLET VALVE TO TRANSFER (SLOP, 8" X 6" CL 150 WITH EXTN LG 2280) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV207-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/09/18 | ME-PM-002-M6
933498 | M400MOV208 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80 EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-110 TO LOADING PUMP 226A (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV208-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/09/18 | ME-PM-002-M6
933499 | M400MOV209 | ACTUATOR,ELECTRIC MOTOR, KEROSENE, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-108 OUTLET MANIFOLD (KEROSENE, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV209-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/01/19 | ME-PM-002-M6
933500 | M400MOV210 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-109 OUTLET HEADER (SLOP, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV210-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
933501 | M400MOV211 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-024A SUCTION LINE (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV211-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/12/18 | ME-PM-002-M6
933502 | M400MOV212 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-024A SUCTION LINE (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV212-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/12/18 | ME-PM-002-M6
933503 | M400MOV213 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 72RPM, 9 SEC, 4" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80 EP, IQ10F10B4, IP68, 203Nm | MOV FOR 400-P-024A DISCHARGE (SLOPGAS OIL, 4" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV213-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/12/18 | ME-PM-002-M6
933504 | M400MOV214 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 72RPM, 9 SEC, 4" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80 EP, IQ10F10B4, IP68, 203Nm | MOV FOR 400-P-024A DISCHARGE LINE (SLOP, 4" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV214-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/12/18 | ME-PM-002-M6
933505 | M400MOV215 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ12F10B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-024B SUCTION LINE (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV215-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/12/18 | ME-PM-002-M6
933506 | M400MOV216 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ12F10B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-024B SUCTION LINE (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV216-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/12/18 | ME-PM-002-M6
933507 | M400MOV217 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 72RPM, 9 SEC, 4" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80 EP, IQ10F10B4, IP68, 203Nm | MOV FOR 400-P-024B DISCHARGE LINE (SLOP, 4" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV217-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
933508 | M400MOV218 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 72RPM, 9 SEC, 4" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80 EP, IQ10F10B4, IP68, 203Nm | MOV FOR 400-P-024B DISCHARGE (SLOP, 4" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV218-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/12/18 | ME-PM-002-M6
933509 | M400MOV221 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-117 OUTLET HEADR (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV221-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/09/18 | ME-PM-002-M6
933510 | M400MOV222 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-118 OUTLET HEADER (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV222-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/09/18 | ME-PM-002-M6
933511 | M400MOV223 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-119 OUTLET HEADER (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV223-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933512 | M400MOV224 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-120 OUTLET HEADER (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV224-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/10/18 | ME-PM-002-M6
933513 | M400MOV225 | ACTUATOR,ELECTRIC MOTOR, KEROSENE, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-108 TO LOADING PUMP 225 (KEROSENE, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV225-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/01/19 | ME-PM-002-M6
933514 | M400MOV301 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 INLET SHELL (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV301-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/01/19 | ME-PM-002-M6
933515 | M400MOV302 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 OUTLET SHELL (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV302-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/02/19 | ME-PM-002-M6
933516 | M400MOV303 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-102 INLET SHELL (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV303-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/01/19 | ME-PM-002-M6
933517 | M400MOV304 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-102 OUTLET SHELL (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV304-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/02/19 | ME-PM-002-M6
933518 | M400MOV305 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-103 INLET SHELL (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV305-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/02/19 | ME-PM-002-M6
933519 | M400MOV306 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-103 OUTLET SHELL (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV306-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/02/19 | ME-PM-002-M6
933520 | M400MOV307 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-104 INLET SHELL (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV307-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/02/19 | ME-PM-002-M6
933521 | M400MOV308 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-104 OUTLET SHELL (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV308-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/02/19 | ME-PM-002-M6
933522 | M400MOV309 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-105 INLET SHELL (JET A1, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV309-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/02/19 | ME-PM-002-M6
933523 | M400MOV310 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-105 OUTLET SHELL SIDE (JET A1, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV310-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/02/19 | ME-PM-002-M6
933524 | M400MOV311 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-106 INLET SHELL (ULG 98, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV311-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/02/19 | ME-PM-002-M6
933525 | M400MOV312 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-106 OUTLET SHELL (ULG 98, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV312-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/02/19 | ME-PM-002-M6
936092 | M400ME010B | HVAC, DUCTED TYPE SPLIT A/C, 30 TON, R22, 415V, 1.0KW, RAUC C30, TRANE, CSHA140K0E00, 3NOS | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING |  | PACKAGE | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936093 | MQ600ME001A | HVAC, R22, 415V, 1.0kW, RAUC C25, TRANE, CSHA140K0E00, R-22, 3NOS | Air Cooled Condensing Unit |  | PACKAGE | MQ600 | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936094 | MQ600ME001B | HVAC, R22 , 1.0KW , RAUC C25 , TRANE , CSHA140K0E00 , CSHA093K0E00 | Air Cooled Condensing Unit |  | PACKAGE | MQ600 | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936103 | MQ600ME001AHU2 | HVAC, R22 , CLCP 012 V & 1 , kW , CLCP - 012 , 1NOS , 1 | Air Handling Uniit |  | PACKAGE | MQ600ME001B | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936104 | MQ600ME001AHU1 | HVAC, R22 , CLCP 012 V & 1 , kW , CLCP - 012 , 1NOS , 1 | Air Handling Uniit |  | PACKAGE | MQ600ME001A | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936105 | M400ME010AHU1 | HVAC, DUCTED TYPE SPLIT A/C, 30 TON, R22, 415V, 415V, CLCP 014 V & 1, 8 kWkW, kW, CLCP - 014, 1NOS, 1, FRAME - Y2 - 132 | AIR HANDLING UNIT AT ADMINISTRATION BUILDING |  | PACKAGE | M400ME010A | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936106 | M400ME010AHU2 | HVAC, DUCTED TYPE SPLIT A/C, 30 TON, R22, 415V, 415V, CLCP 014 V & 1, 8 kWkW, kW, CLCP - 014, 1NOS, 1, AIR BLOWER MDLNO | AIR HANDLING UNIT AT ADMINISTRATION BUILDING |  | PACKAGE | M400ME010B | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936107 | M400ME009AHU1 | HVAC, DUCTED TYPE SPLIT A/C, 120 TONS, R22, 415V, 415V, CLCP 060 H & 1, 11 kWkW, kW, CLCP - 060, 2NOS, 1, FRAME - Y2 - 160 M | AIR HANDLING UNIT IN S/S-400 AT IRP MTERMINAL |  | PACKAGE | M400ME009A | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936108 | M400ME009AHU2 | HVAC, 120 TONS, R22, 415V, 415V, CLCP 060 H & 1, 11kW, kW, CLCP - 060, 2NOS, 1, FRAME - Y2 - 160 | AIR HANDLING UNIT IN S/S-400 AT IRP MTERMINAL |  | PACKAGE | M400ME009B | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936109 | M400ME008AHU1 | HVAC, R22 , CLCP 060 H & 1 , kW , CLCP - 060 , 2NOS , 1 , FRAME - Y2 - 160 M | AIR HANDLING UNIT AT CONTROL ROOM OF IRP MTERMIAL |  | PACKAGE | M400ME008A | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936110 | M400ME008AHU2 | HVAC, DUCTED TYPE SPLIT A/C, 120 TONS, R22, 415V, 415V, CLCP 060 H & 1, 11 kWkW, kW, CLCP - 060, 2NOS, 1, FRAME - Y2 - 160 M | AIR HANDLING UNIT AT CONTROL ROOM OF IRP MTERMINAL |  | PACKAGE | M400ME008B | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933442 | M400MOV119 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-106 INLETHEADER (ULG 98, 10" X 8" CL 300 WITH EXTN LG 2000MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV119-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/01/19 | ME-PM-002-M6
933443 | M400MOV120 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" X 6" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-106 INLET HEADER (ULG 98, 8" X 6" CL 300 WITH EXTN LG 2030MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV120-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/02/19 | ME-PM-002-M6
933444 | M400MOV121 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-115 INLET HEADER (ULG 98, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV121-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/12/18 | ME-PM-002-M6
933445 | M400MOV122 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-106 OUTLET HEADER (ULG 98, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV122-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/02/19 | ME-PM-002-M6
933446 | M400MOV123 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-106 TRANSFER OUTLET (ULG 98, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV123-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/02/19 | ME-PM-002-M6
933447 | M400MOV124 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-106 TO LOADING PUMP 222/223 (ULG 98, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV124-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/01/19 | ME-PM-002-M6
933448 | M400MOV125 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-107 INLET ISOLATION (ULG 98, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV125-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933449 | M400MOV126 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-107 INLET HEADER (ULG 98, 10" X 8" CL 300 WITH EXTN LG 2000MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV126-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/01/19 | ME-PM-002-M6
933450 | M400MOV127 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" X 6" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-107 INLET HEADER (ULG 98, 8" X 6" CL 300 WITH EXTN LG 2030MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV127-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/02/19 | ME-PM-002-M6
933451 | M400MOV128 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-107 OUTLET HEADER (ULG 98, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV128-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/02/19 | ME-PM-002-M6
933452 | M400MOV129 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-107 OUTLET HEADER (ULG 98, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV129-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/02/19 | ME-PM-002-M6
933453 | M400MOV130 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-107 OUTLET ISOLATION (ULG 98, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV130-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/02/19 | ME-PM-002-M6
933454 | M400MOV131 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-107 TO LOADING PUMP 222/223 (ULG 98, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV131-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933455 | M400MOV141 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-021A SUCTION LINE (ULG 95 / ULG 98 , 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV141-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/11/18 | ME-PM-002-M6
933456 | M400MOV142 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-021A SUCTION LINE.(ULG 95 / ULG 98 , 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV142-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/11/18 | ME-PM-002-M6
933457 | M400MOV143 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-021A DISCHARGE LINE (ULG 95 / ULG 98, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV143-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/11/18 | ME-PM-002-M6
933458 | M400MOV144 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80 EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-021A DISCHARGE LINE.(ULG 95 / ULG 98, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV144-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/11/18 | ME-PM-002-M6
933459 | M400MOV145 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-021B SUCTION LINE (ULG 95 / ULG 98 , 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV145-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/11/18 | ME-PM-002-M6
933460 | M400MOV146 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-021B SUCTION LINE(ULG 95 / ULG 98 , 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV146-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/12/18 | ME-PM-002-M6
933461 | M400MOV147 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-021B DISCHARGE LINE.(ULG 95 / ULG 98, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV147-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/11/18 | ME-PM-002-M6
933462 | M400MOV148 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-021B DISCHARGE (ULG 95 / ULG 98, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV148-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/11/18 | ME-PM-002-M6
933463 | M400MOV149 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80 EP, IQ20F14B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-021C SUCTION LINE (ULG 95 / ULG 98 , 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV149-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/12/18 | ME-PM-002-M6
933464 | M400MOV150 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-021C SUCTION LINE (ULG 95 / ULG 98 , 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV150-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/12/18 | ME-PM-002-M6
933465 | M400MOV151 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-021C DISCHARGE (ULG 95 / ULG 98, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV151-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/12/18 | ME-PM-002-M6
933466 | M400MOV152 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-021C DISCHAARGE LINE.(ULG 95 / ULG 98, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV152-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/12/18 | ME-PM-002-M6
933467 | M400MOV153 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV (WFJ) FOR 400 -P- 022A SUCTION LINE (GAS OIL, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV153-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/11/18 | ME-PM-002-M6
933468 | M400MOV154 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-022A SUCTION (GAS OIL, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV154-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
933469 | M400MOV155 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV (WFJ) FOR 400-P-022B SUCTION LINE (GAS OIL, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV155-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/12/18 | ME-PM-002-M6
935789 | M400DT651 | TRANSMITTER, VIBRATING TUBE , 300-1100 KG/M3 , 4-20MA , 240VAC,+/- 10%, 50 Hz +/ | RUWAIS MUSSAFAH M P/L RECEIVNG-DENSITY SKID 900LB |  | ANALYSER | M400SYS | 2 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DT651-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/08/18 | MC-PM-014-M3
935826 | M400P016A | PUMP,CENTRIFUGAL, HORIZONTAL, CONTINUOUS, ULG95/98/GOIL/JET A1/KEROSEN MAIN LINE, 0.684 - 0.871, CENTERLINE, 6 X 8 X 13L HDO, 10, INDUCTION MOTOR, 2130-3400, 12.03, 58.9, 730 M, 13 - 45, HYDRODYNAMIC, HYDRODYNAMIC, 8, A 276 GR. 410, A 487 GR. CA6NM, A 276 GR. 420, A 276 GR. 420 ANNEALED, A 216, 313 MM, RATED, API 610 | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 04/10/18 | MM-PM-002-M6
935827 | M400P016B | PUMP,CENTRIFUGAL, HORIZONTAL, CONTINUOUS, ULG98/95/G OIL/JET A1/KEROSEN MAIN LINE, 0.684 - 0.871, CENTERLINE, 6 X 8 X 13L HDO, 10, INDUCTION MOTOR, 2130-3400, 12.03, 58.9, 730 M, 13 - 45, HYDRODYNAMIC, HYDRODYNAMIC, 8, A 276 GR. 410, A 487 GR. CA6NM, A 276 GR. 420, A 276 GR. 420 ANNEALED, A 216, 313 MM, RATED, API 610 | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP |  | PUCE | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-002-M6
935828 | M400P018A | PUMP, CENTRIFUGAL, HORIZONTAL , CONTINUOUS , JET A1 MAIN LINE , 0.751 - 0.841 , | JET A1 MAIN LINE PUMP-A TO ADIA. |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P018AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-005-M6
935829 | M400P018B | PUMP, CENTRIFUGAL, HORIZONTAL , CONTINUOUS , JET A1 MAIN LINE , 0.751 - 0.841 , | JET A1 MAIN LINE PUMP-B TO ADIA. |  | PUCE | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | M400P018BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/11/18 | MM-PM-005-M6
935830 | M400P019 | PUMP, CENTRIFUGAL, HORIZONTAL , INTERMITTENT , OFF SPEC JET A1 MAIN LINE , 0.751 | OFF SPEC JET A1 MAIN LINE PUMP TO RUWAIS. |  | PUCE | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P019MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-001-M6
935836 | M400TCV461 | VALVE CONTROL | OFF SPEC JET A1 MAIN LINE PUMP-3 WAY TEMP.CONT.VLV |  |  | M400P019 | 3 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935837 | M400TCV401 | VALVE CONTROL | ULG95/98/GO/JETA1/KERO M/L PUMP-3 WAYTEMP.CONT.VLV |  | CNTR_VLV | M400P016A | 3 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935838 | M400TCV416 | VALVE CONTROL | ULG95/98/GO/JET A1/KERO M/L PUMP-3WAY TEMPCONT.VLV |  |  | M400P016B | 3 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935839 | M400PSV401 | VALVE, SAFETY RELIEF, JET A1/KEROSENE , 3/4" , MNPT INLET , 316 SS , 316 SS , SS | SAFETY RELIEF VALVE FOR AUXILIARY LUB UNIT OF 400P16A. |  | PSV | M400P016A | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935840 | M400PSV402 | VALVE, SAFETY RELIEF, JET A1/KEROSENE , 3/4" , MNPT INLET , 316 SS , 316 SS , SS | SAFETY RELIEF VALVE FOR AUXILIARY LUB UNIT OF 400P16A. |  | PSV | M400P016A | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935841 | M400PSV405 | VALVE CONTROL | ULG95/98/GO/JET A1/KERO M/L PUMP PRES.CONTROL VLV |  |  | M400P016A | 1 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935842 | M400PSV416 | VALVE, SAFETY RELIEF, JET A1/KEROSENE , 3/4" , MNPT INLET , 316 SS , 316 SS , SS | ULG95/98/GO/JET A1/KEROS M/L PUMP-RELIEF VALVE |  | PSV | M400P016B | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935843 | M400PSV417 | VALVE, SAFETY RELIEF, JET A1/KEROSENE , 3/4" , MNPT INLET , 316 SS , 316 SS , SS | SAFETY RELIEF VALVE FOR AUXILIARY LUB UNIT OF 400P16B. |  | PSV | M400P016B | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935844 | M400PSV420 | VALVE CONTROL | ULG95/98/GO/JET A1/KERO M/L PUMP PRES.CONTROL VLV |  |  | M400P016B | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935845 | M400PSV461 | VALVE, SAFETY RELIEF, JET A1/KEROSENE , 3/4" , MNPT INLET , 316 SS , 316 SS , SS | SAFETY RELIEF VALVE FOR AUXILIARY LUB UNIT OF OFF SPEC JET A1 M/L PUMP 400P19. |  | PSV | M400P019 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935846 | M400PSV462 | VALVE, SAFETY RELIEF, JET A1 , 3/4" , MNPT INLET , 316 SS , 316 SS , SS , SPRING | SAFETY RELIEF VALVE FOR AUXILIARY LUB UNIT OF OFF SPEC JET A1 M/L PUMP 400P19. |  | PSV | M400P019 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935847 | M400PSV465 | VALVE CONTROL | OFF SPEC JET A1 M/L PUMP PRES.CONTROL VLV |  |  | M400P019 | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935848 | M400RO401 | VALVE, BALL, 1" , 150 LB , 100 DEG C , RF FLANGE , DOUBLE 3 WAY , VITON O-RING , | ULG95/98/GOL/JET A1/KEROS M/L PUMP C/O VALVE |  | VALVE | M400P016A | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935849 | M400RO416 | VALVE, BALL, 1" , 150 LB , 100 DEG C , RF FLANGE , DOUBLE 3 WAY , VITON O-RING , | ULG95/98/GOL/JET A1/KEROS M/L PUMP C/O VALVE |  | VALVE | M400P016B | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935850 | M400RO461 | VALVE, BALL, 1" , 150 LB , 100 DEG C , RF FLANGE , DOUBLE 3 WAY , VITON O-RING , | OFF SPEC JET A1 MAIN LINE PUMP |  | VALVE | M400P019 | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935851 | M400MP019 | MOTOR,ELECTRIC, OFF SPEC JET A1, IP55, 990, 50, 1306, EX (d), ET 630 L2, EFNLB Sep-80,EFNLO Sep-80, HORIZONTAL, 2980, 3, STAR, 100 OHM, F, Zone 2, 400-MS-001, VACUM CONTACTOR, VACUM, T3 | MOTOR,ELECTRIC, OFF SPEC.JET A1 PUMP, IP55, 950 KW, 50 HZ, 3300 V, IP55, ET 630 L2, ELNLB Sep-80,EFNLO Sep-80 |  | MOTOR | M400P019 | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP019-ME1 | INACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-013-M6
935852 | M400MP016A | MOTOR,ELECTRIC, ULG95/ULG98/GAS OIL/JET A1/KEROSENE, IP55, 1560, 50, -, EX (d), 710, EFNLB-11-125,EFNLQ-11-125, HORIZONTAL, 3400, 3, STAR, 312.2, 100 OHM, F, Zone 2, 400-MS-001, SF6, SF6, T3 | MOTOR,ELECTRIC, Variable Speed Drive FOR ALAIN MAIN LINE PUMP JET A1, IP55, 1500 KW, 50 HZ, 3300 V, Ex d, ET 710 V2, EFNLB 11-125,EFNLQ 11-125 |  | MOTOR | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP016A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/10/18 | ME-PM-013-M6
935853 | M400MP016B | MOTOR,ELECTRIC, ULG95/ULG98/GAS OIL/JET A1/KEROSENE, IP55, 1560, 57, 3300, S1, EX (d), ET 710 V2, DE EFNLB11-125,NDE EFNLO-11-125, IM 1001 ,FOOT MOUNTING, 3400, 3, STAR, 312.2, 100 OHM, F, Zone 2, 9500 KG, Oil L-HM46 ISO 3498, 400-MS-001, SF6, SF6, T3 (57 DEG C) | MOTOR,ELECTRIC, Variable Speed Drive MOTOR FOR MAIN LINE PUMP AL AIN, IP55, 1500 KW, 50 HZ, 3300 V, Ex d, ET 710 V2, EF NLB |  | MOTOR | M400P016B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP016B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/11/18 | ME-PM-013-M6
935854 | M400MP018A | MOTOR,ELECTRIC, JET A1, IP55, 265, 50, 3300VOLT V, S1, EX (d), ET 450 L2, NU217C3+3217C3,NU217C3, HORIZONTAL, 2977, 3, ST6AR, 55.4, 100 OHM, F, Zone 2, 400-MS-001, VACUM CONTACTOR, VACUM CONTACTOR, T3 | MOTOR,ELECTRIC, MAIN LINE PUMP JET A1 FOR ADIA, IP55, 265 KW, 50 HZ, 3300 V, Ex d, ET 450 L2, NU217C3+6217C3,NU217C3 |  | MOTOR | M400P018A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP018A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 26/10/18 | ME-PM-013-M6
935855 | M400MP018B | MOTOR,ELECTRIC, JET A1 FOR ADIA, IP55, 265, 50, -, EX (d), 450, NU217C3+6217C3,NU217C3, HORIZONTAL, 2977, 3, STAR, 55.4, 100 OHM, F, Zone 2, 400 MS-001, VACUM CONTACTOR, VACUM, T3 | MOTOR,ELECTRIC, MAIN LINE PUMP JET A1 FOR ADIA, IP55, 265 KW, 50 HZ, 3300 V, EX d, ET 450 L2, NU217C3+6217C3,NU217C3 |  | MOTOR | M400P018B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP018B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/11/18 | ME-PM-013-M6
935856 | M400LF019B | FILTER, OIL | OFF SPEC JET A1 M/L PUMP LUB OIL FILTER |  | VESSEL | M400P019 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935857 | M400LG402 | GLASS, LEVEL GAUGE, REFLEX , B-4 , 34MM WD X 190MM LG X 17MM THK , 100 BAR @ 40 | ULG95/98/GO/JET A1/KEROS M/L PUMP-LEVEL GAUGE | 935826 | INDICATR | M400P016A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935636 | SMTP38 |  | TEST POINT# 38 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935637 | SMTP39 |  | TEST POINT# 39 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935638 | SMTP40 |  | TEST POINT# 40 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935652 | SMLPGTP7 | CP TEST POINT | TEST POINT # 7 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935653 | SMLPGTP8 | CP TEST POINT | TEST POINT # 8 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935667 | SMLPGTP22 | CP TEST POINT | TEST POINT # 22 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935668 | SMLPGTP23 | CP TEST POINT | TEST POINT # 23 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130740 | M400BATT001A | BATTERY,BANK, Ni-Cad | BATTERY BANK 'A' FOR 400DCUPS001 AT MTERMINAL IRP-1 SUBSTATION |  | BATTERY | M400BATT | 1 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400BATT001A-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 07/08/18 | ME-PM-001-M3
969130741 | M400BATT001B | BATTERY,BANK, Ni-Cad | BATTERY BANK 'B' FOR 400DCUPS001 AT MTERMINAL IRP-1 SUBSTATION |  | BATTERY | M400BATT | 1 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400BATT001B-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 14/08/18 | ME-PM-001-M3
969130742 | M400MCCB001A | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB BOX FOR 400-BATT-001A |  | BREAKER | M400BATT | 1 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130743 | M400MCCB001B | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB BOX FOR 400-BATT-001B |  | BREAKER | M400BATT | 1 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130744 | M400TCP001 | CATHODIC PROTECTION, C.P. FOR TANK T-111, 9.6 KVA, OIL COOLED, 240 VOLT, 50 HZ, 1, 100 VOLT, 50 AMPERES, AIR, BS148, 190 LITERS | C.P. RECTIFIER/TRANSFORMER UNIT FOR TANK T-111 |  | CATHPRO | M400T111 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP001-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 17/11/18 | ME-PM-008-M6
969130745 | M400TCP002 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-112, 9.6 KVA, AIR COOLED, 240 VOLT, 50 HZ, 1, 100 VOLT, 50 AMPERES, AIR, BS 148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-112 |  | CATHPRO | M400T112 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP002-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/11/18 | ME-PM-008-M6
969130746 | M400TCP003 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-113, AIR COOLED, 240 VOLT, 50 HZ, 1, 100 VOLT, 50 AMPERES, AIR, BS148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-113 |  | CATHPRO | M400T113 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP003-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 08/12/18 | ME-PM-008-M6
969130747 | M400TCP004 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-114, 240 VOLT, 50 HZ, 1, 100 VOLT, 50 AMPERES, AIR, BS148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-114 |  | CATHPRO | M400T114 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP004-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 15/12/18 | ME-PM-008-M6
969130748 | M400TCP005 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-115, 240 VOLT, 50 HZ, 1, 100 VOLT, 50 AMPERES, AIR | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-115 |  | CATHPRO | M400T115 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP005-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 22/12/18 | ME-PM-008-M6
938678 | M400TT541B | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX NEPTHA/REFORM P/L, JET A1,CUSTODY METERIN | 939201 | TEMP_TX | M400TI541B | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938679 | M400TE541A | ELEMENT, TEMPERATURE, MEASURING , PT100 , 100 OHM @ 0 DEG C , PLATINUM , 305MM L | TEMP.ELEMENT NEPTHA/REFORM P/L, JET A1,CUSTODY MET | 939200 | TEMP_ELE | M400TI541A | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938680 | M400TE541B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP.ELEMENT NEPTHA/REFORM P/L, JET A1,CUSTODY MET | 939201 | TEMP_ELE | M400TI541B | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938681 | M400FC541A | SYSTEM | Metering Skid 400-FT-541A flow |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC541A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/01/19 | MC-PM-002-M6
938682 | M400FC541B | SYSTEM | Metering Skid 400-FT-541B |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC541B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/01/19 | MC-PM-002-M6
938683 | M400FC620A | SYSTEM | FLOW METER SKID RUW-MUS, 400-FT-620A |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC620A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/01/19 | MC-PM-002-M6
938684 | M400FC620B | SYSTEM | FLOW METER SKID RUW-MUS, 400-FT-620B |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC620B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/01/19 | MC-PM-002-M6
938685 | M400FC620C | SYSTEM | FLOW METER SKID RUW-MUS, 400-FT-620C |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC620C-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/01/19 | MC-PM-002-M6
938686 | M400FC771A | SYSTEM | Flow metering skid 400-FT-771A |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC771A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/01/19 | MC-PM-002-M6
938687 | M400FC771B | SYSTEM | Flow metering skid 400-FT-771B |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC771B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM-002-M6
938688 | M400FC772 | SYSTEM | Flow metering skid 400-FT-772 |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC772-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM-002-M6
938689 | M400FC861A | SYSTEM, CORIOLIS MASS FLOW METER | Flow metering skid 400-FT-861A |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC861A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/01/19 | MC-PM-002-M6
938690 | M400FC861B | SYSTEM, CORIOLIS MASS FLOW METER | Flow metering skid 400-FT-861B |  | CLOSLOOP | M400SYS | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FC861B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/01/19 | MC-PM-002-M6
938691 | M400FE861A | SENSOR, DIFFERENTIAL PRESSURE | MUSSAFFAH-TIE IN TO AL-AIN,CUSTODY METERING SYSTEM | 938689 | FL_MTR | M400FC861A | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938692 | M400FE861B | SENSOR, DIFFERENTIAL PRESSURE | MUSSAFFAH-TIE IN TO AL-AIN,CUSTODY METERING SYSTEM | 938690 | FL_MTR | M400FC861B | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938693 | M400FE866 | SYSTEM | Inlet Line Fire Water Tank 400-T-201 | 936603 | ORIFICE | M400FT866 | 3 | FL_MTR | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938694 | M400FY541A | COMPUTER, FLOW | flow computer for Metering Skid 400-FT-541A | 938681 | CLPCPC | M400FC541A | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938695 | M400FY541B | COMPUTER, FLOW | flow computer for Metering Skid 400-FT-541B | 938682 | CLPCPC | M400FC541B | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938696 | M400FY620A | COMPUTER, FLOW | Flow Computer RUW-MUS, Metering Skid 400FT620A. | 938683 | CLPCPC | M400FC620A | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938697 | M400FY620B | COMPUTER, FLOW | Flow Computer RUW-MUS, Metering Skid 400-FT-620B | 938684 | CLPCPC | M400FC620B | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938698 | M400FY620C | COMPUTER, FLOW | Flow Computer RUW-MUS, Metering Skid 400FT620C. | 938685 | CLPCPC | M400FC620C | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938699 | M400FY771A | COMPUTER, FLOW | flow computer for Metering Skid 400-FT-771A | 938686 | CLPCPC | M400FC771A | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938700 | M400FY771B | COMPUTER, FLOW | flow computer for Metering Skid 400-FT-771B | 938687 | CLPCPC | M400FC771B | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938701 | M400FY772 | COMPUTER, FLOW | flow computer for Metering Skid 400-FT-772 | 938688 | CLPCPC | M400FC772 | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938702 | M400FY861A | COMPUTER, FLOW | flow computer for Metering Skid 400-FT-861A | 938689 | CLPCPC | M400FC861A | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938703 | M400FY861B | COMPUTER, FLOW | flow computer forMetering Skid 400-FT-861B | 938690 | CLPCPC | M400FC861B | 3 | PLC_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938704 | M400HS404/DU | SWITCH, SELECTOR | Lube Oil Pump A Duty Selector Switch For 400-P-016 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938705 | M400HS404C/SP | SWITCH, SELECTOR | Lube Oil Pump A Stop Switch For 400-P-016A |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938706 | M400HS404C/ST | SWITCH, SELECTOR | Lube Oil Pump A Start Switch For 400-P-016A |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938707 | M400HS405/DU | SWITCH, SELECTOR | Lube Oil Pump B Duty Selector Switch For 400-P-016 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938708 | M400HS406C/SP | SWITCH, SELECTOR | Lube Oil Cooling Fan A Stop Switch For 400-P-016A |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938709 | M400HS406C/ST | SWITCH, SELECTOR | Lube Oil Cooling Fan A Strat Switch For 400-P-016A |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938710 | M400HS407/DU | SWITCH, SELECTOR | Lube Oil Cooling Fan B Duty Sec.SwitchFor 400-P-01 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938711 | M400HS407C/SP | SWITCH, SELECTOR | Lube Oil Cooling Fan B Stop Switch For 400-P-016A |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938712 | M400HS407C/ST | SWITCH, SELECTOR | Lube Oil Cooling Fan B Strat Switch For 400-P-016A |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938713 | M400HS408B | SWITCH, SELECTOR | Lube Oil Filter Transfer Valve Select Other Filter |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938714 | M400HS419/DU | SWITCH, SELECTOR | Lube Oil Pump A Duty Selector Switch For 400-P-016 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938715 | M400HS419C/SP | SWITCH, SELECTOR | Lube Oil Pump A Stop Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938716 | M400HS419C/ST | SWITCH, SELECTOR | Lube Oil Pump A Start Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938717 | M400HS420/DU | SWITCH, SELECTOR | Lube Oil Pump B Duty Selector Switch For 400-P-016 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938718 | M400HS420C/SP | SWITCH, SELECTOR | Lube Oil Pump B Stop Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938719 | M400HS420C/ST | SWITCH, SELECTOR | Lube Oil Pump B Start Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938720 | M400HS421/DU | SWITCH, SELECTOR | Lube Oil Cooling Fan A Selector Swt. For 400-P-016 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365113 | M410XHD606B | LINEAR HEAT DETECTOR FOR TANK-001 | LINEAR HEAT DETECTOR FOR TANK-001 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365114 | M410XHD608A | LINEAR HEAT DETECTOR FOR TANK-002 | LINEAR HEAT DETECTOR FOR TANK-002 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365115 | M410XHD608B | LINEAR HEAT DETECTOR FOR TANK-002 | LINEAR HEAT DETECTOR FOR TANK-002 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365116 | M410XHD609A | LINEAR HEAT DETECTOR FOR TANK-003 | LINEAR HEAT DETECTOR FOR TANK-003 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365125 | M410XHD613B | LINEAR HEAT DETECTOR FOR TANK-007 | LINEAR HEAT DETECTOR FOR TANK-007 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365126 | M410XHD611A | LINEAR HEAT DETECTOR FOR TANK-008 | LINEAR HEAT DETECTOR FOR TANK-008 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365127 | M410XHD611B | LINEAR HEAT DETECTOR FOR TANK-008 | LINEAR HEAT DETECTOR FOR TANK-008 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365128 | M410XHD615A | LINEAR HEAT DETECTOR FOR TANK-009 | LINEAR HEAT DETECTOR FOR TANK-009 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365129 | M410XHD615B | LINEAR HEAT DETECTOR FOR TANK-009 | LINEAR HEAT DETECTOR FOR TANK-009 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365130 | M410XHD614A | LINEAR HEAT DETECTOR FOR TANK-010 | LINEAR HEAT DETECTOR FOR TANK-010 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365131 | M410XHD614B | LINEAR HEAT DETECTOR FOR TANK-010 | LINEAR HEAT DETECTOR FOR TANK-010 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365132 | M410XHD600B | LINEAR HEAT DETECTOR FOR TANK-011 | LINEAR HEAT DETECTOR FOR TANK-011 |  | FGBHFD | M410T011 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365133 | M410XHD601A | LINEAR HEAT DETECTOR FOR TANK-012 | LINEAR HEAT DETECTOR FOR TANK-012 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365142 | M410XHD667B | LINEAR HEAT DETECTOR FOR FW PUMP-031A | LINEAR HEAT DETECTOR FOR FW PUMP-031A |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365143 | M410XHD668A | LINEAR HEAT DETECTOR FOR FW PUMP-031B | LINEAR HEAT DETECTOR FOR FW PUMP-031B |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365144 | M410XHD668B | LINEAR HEAT DETECTOR FOR FW PUMP-031B | LINEAR HEAT DETECTOR FOR FW PUMP-031B |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365145 | M410XHD669A | LINEAR HEAT DETECTOR FOR FW PUMP-031C | LINEAR HEAT DETECTOR FOR FW PUMP-031C |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365146 | M410XHD669B | LINEAR HEAT DETECTOR FOR FW PUMP-031C | LINEAR HEAT DETECTOR FOR FW PUMP-031C |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365147 | M410XHD670A | LINEAR HEAT DETECTOR FOR FW PUMP-031D | LINEAR HEAT DETECTOR FOR FW PUMP-031D |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365148 | M410XHD670B | LINEAR HEAT DETECTOR FOR FW PUMP-031D | LINEAR HEAT DETECTOR FOR FW PUMP-031D |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365149 | M410XHD671A | LINEAR HEAT DETECTOR FOR FW PUMP-031E | LINEAR HEAT DETECTOR FOR FW PUMP-031E |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365150 | M410XHD671B | LINEAR HEAT DETECTOR FOR FW PUMP-031E | LINEAR HEAT DETECTOR FOR FW PUMP-031E |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365151 | M410XHD672A | LINEAR HEAT DETECTOR FOR FW PUMP-031F | LINEAR HEAT DETECTOR FOR FW PUMP-031F |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365152 | M410XHD672B | LINEAR HEAT DETECTOR FOR FW PUMP-031F | LINEAR HEAT DETECTOR FOR FW PUMP-031F |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365153 | M410XHD673A | LINEAR HEAT DETECTOR FOR FW PUMP-031G | LINEAR HEAT DETECTOR FOR FW PUMP-031G |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365154 | M410XHD673B | LINEAR HEAT DETECTOR FOR FW PUMP-031G | LINEAR HEAT DETECTOR FOR FW PUMP-031G |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365155 | M410XHD653A | LINEAR HEAT DETECTOR FOR PUMP-014A AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-014A AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365156 | M410XHD653B | LINEAR HEAT DETECTOR FOR PUMP-014A AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-014A AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365157 | M410XHD654A | LINEAR HEAT DETECTOR FOR PUMP-014B AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-014B AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365158 | M410XHD654B | LINEAR HEAT DETECTOR FOR PUMP-014B AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-014B AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365159 | M410XHD655A | LINEAR HEAT DETECTOR FOR PUMP-008A AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-008A AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365160 | M410XHD655B | LINEAR HEAT DETECTOR FOR PUMP-008A AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-008A AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365161 | M410XHD656A | LINEAR HEAT DETECTOR FOR PUMP-008B AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-008B AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365162 | M410XHD656B | LINEAR HEAT DETECTOR FOR PUMP-008B AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-008B AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365163 | M410XHD657A | LINEAR HEAT DETECTOR FOR PUMP-007A AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-007A AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195521 | M410FU426 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195605 | M410GAV2353002 | 3/4" Class 800 Gate Valve | 3/4" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195606 | M410GAV2353003 | 1/2" Class 800 Gate Valve | 1/2" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195607 | M410GAV2353004 | 3/4" Class 800 Gate Valve | 3/4" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195608 | M410GAV2353005 | 1" Class 800 Gate Valve | 1" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195609 | M410GAV2353006 | 1/2" Class 800 Gate Valve | 1/2" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195610 | M410GAV2353007 | 3/4" Class 800 Gate Valve | 3/4" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195611 | M410GAV2353008 | 1/2" Class 800 Gate Valve | 1/2" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195612 | M410GAV2353009 | 3/4" Class 800 Gate Valve | 3/4" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195613 | M410GAV2353010 | 1" Class 800 Gate Valve | 1" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195614 | M410GAV2353011 | 1-1/2" Class 800 Gate Valve | 1-1/2" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195522 | M410FU427 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195559 | M400GACP001A | FAST2000 GAS DETECTOR PANEL | FAST2000 GAS DETECTOR PANEL |  | BLDGS | M400SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195560 | M400GACP001B | FAST2000 GAS DETECTOR PANEL | GAS ALARM CONTROL PANEL MCR RACK ROOM |  | BLDGS | M400SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195561 | M400PDB007 | PLCR POWER DISTRIBUTION BOARD CABINET | PLCR POWER DISTRIBUTION BOARD CABINET |  | SWBOARD | M400SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195562 | M410BFV2352001 | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195563 | M410BFV2352002 | 10" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 10" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195564 | M410BFV2352003 | 20" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 20" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195565 | M410BFV2352004 | 24" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 24" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195566 | M410BFV2352005 | 30" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 30" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195567 | M410BFV2352006 | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195568 | M410BFV2352007 | 12" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 12" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195523 | M410FU428 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195570 | M410BFV2352009 | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195571 | M410BFV2352010 | 12" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 12" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195572 | M410BFV2352011 | 4" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 4" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195573 | M410BFV2352012 | 6" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 6" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195574 | M410BFV2352013 | 3" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 3" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195575 | M410BFV2352014 | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 8" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195576 | M410BFV2352015 | 12" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 12" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195577 | M410BFV2352016 | 14" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 14" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195578 | M410BFV2352017 | 16" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 16" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195524 | M410FU429 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195579 | M410BFV2352018 | 30" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG | 30" CONCENTRIC BUTTERFLY VALVE, 150LB, LUG |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195580 | M410CHV2353001 | 1" Class 800 Lift Check Valve | 1" Class 800 Lift Check Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195581 | M410CHV2354001 | 3" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 150# | 3" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195582 | M410CHV2354002 | 6" DUAL PLATE CHECK VALVE, WAFER, 150# | 6" DUAL PLATE CHECK VALVE, WAFER, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195583 | M410CHV2354003 | 12" DUAL PLATE CHECK VALVE, WAFER, 150# | 12" DUAL PLATE CHECK VALVE, WAFER, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195584 | M410CHV2354004 | 14" DUAL PLATE CHECK VALVE, LUGGED WAFER, 150# | 14" DUAL PLATE CHECK VALVE, LUGGED WAFER, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195585 | M410CHV2354005 | 6" DUAL PLATE CHECK VALVE, WAFER, 150# | 6" DUAL PLATE CHECK VALVE, WAFER, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195586 | M410CHV2354006 | 2" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 150# | 2" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
611825 | U51MOV104 | VALVE, BALL, 4" X 3" , 300 LB , RF FLANGE , ASTM A105N , ACTUATOR , 2 PIECE , RE | MOV FOR LPG LINE | EMV19801 | MOV | U5101R01 | 2 | MOV | 623101-610202 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
611826 | U51MOV105 | VALVE, BALL, 8" , 300 LB , RF FLANGE , ASTM A216 GR WCB , ACTUATOR , 1 PIECE , F | MOV FOR LPG TO MUSSAFAH LINE | EMV19802 | MOV | U5101R01 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
611827 | U51MOV106 | BALL VALVE; TRUE UNION MOUNTED, EB TYPE, SIZE 8'' X 6'' , RF X 300 LB | MOV FOR LPG LINE | EMV19803 | MOV | U5101R01 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
611828 | U51MOV115 | U51MOV115;BALL VALVE, SIZE : 8'' X 300 LB ( FB ) , F/F 661MM | MOV FOR LPG TO MUSSAFAH LINE | EMV19793 | MOV | U5101R01 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934812 | AT800TSV101 | VALVE RELIEF | MOT TO ADIA RECV HEADER, JET A1, THRML RLF VALVE. |  | PSV | AT800VALVE | 1 | PSV | 617101-310600 | IRPADIA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934813 | AT800TSV102 | VALVE, SAFETY RELIEF, CONVENTIONAL , JET A1 , 3/4" , 300 , 47 , 87 , FLANGED , A | MOT TO ADIA PIG RECVR, JET A1, THRML RLF VALVE. |  | PSV | AT800VALVE | 3 | PSV | 617101-310600 | IRPADIA | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934814 | AT800TSV103 | VALVE RELIEF | MOT TO ADIA PIG RECVR TK, JET A1, THRML RLF VALVE. |  | PSV | AT800VALVE | 3 | PSV | 617101-310600 | IRPADIA | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934815 | AT800TSV104 | VALVE RELIEF | ADR TO ADIA INLET HEADER, JET A1, THRML RLF VALVE. |  | PSV | AT800VALVE | 3 | PSV | 617101-310600 | IRPADIA | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934822 | M400VA1BA395 | VALVE BALL | BALL VALVE, RB, 150#1" |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934823 | M400VA1BA396 | VALVE BALL | BALL VALVE, 1" NPT, PN25 |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934824 | M400VA1CH094 | VALVE CHECK | CHECK VALVE, 1", PN25 |  | VALCH | M400VALVE | 3 | VALCH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934825 | M400VA12BA396 | VALVE BALL | BALL VALVE, 1/2" NPT, PN25 |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934826 | M400VA2BA395 | VALVE BALL | BALL VALVE, RB, 150#2" |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934827 | M400VA2BA396 | VALVE, BALL, 2" , PN 25, BS 5154 SERIES 'A' , THREADED , 1 PIECE , 2" NPT , 182. | BALL VALVE, 2" NPT, PN25 |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934828 | M400VA2CH395 | VALVE, CHECK, SWING CHECK , 2" , PN 25 , FLANGED , ASTM B148 C95800 , 203.20MM | CHECK VALVE, 2", PN 25 |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934829 | M400VA3BA395 | VALVE BALL | BALL VALVE, RB, 150#3" |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934830 | M400VA34BA395 | VALVE BALL | BALL VALVE, RB, 150#3/4" |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934841 | AA113AT101 | COLORIMETER | MUSSAF.TO AL AIN MULTI PRODUCT,REC.END,COLORIMETER |  |  | AA13MISC | 3 | ANALYSER | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934842 | M400AT851 | PHOTOMETER ANALYZER, DIGITAL , PANEL MOUNT , 0-6 ASTM D1500 | COLORIMETER ANALYZER MSFH-AAIN MLTI PROD TIE-IN. |  | ANALYSER | M400WWTPANALZ | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 |  | M400AT851-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/10/18 | MC-PM-015-M3
934843 | AA13FT101 | SYSTEM | UPGRADTION OF EXISTING CUSTODY METERING SYSTEM |  |  | AA13SYS | 3 | CLN_FLTR | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934848 | M400FT541A | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | NEPTHA/REFORM P/L, JET A1,CUSTODY METERING SYSTEM | 938681 | FL_TX | M400FC541A | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934849 | M400FT541B | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | NEPTHA/REFORM P/L, JET A1, CUSTODY METERING SYSTEM | 938682 | FL_TX | M400FC541B | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934850 | M400FT620A | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | FLOW METER SKID RUW-MUS, CUSTODY METERING SYSTEM |  | FL_TX | M400FC620A | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934851 | M400FT620B | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | FLOW METER SKID RUW-MUS, CUSTODY METERING SYSTEM |  | FL_TX | M400FC620B | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934852 | M400FT620C | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | FLOW METER SKID RUW-MUS, CUSTODY METERING SYSTEM |  | FL_TX | M400FC620C | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934853 | M400FT771A | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | MUSSAFFAH-ADIA JET A1 P/L,CUSTODY METERING SYSTEM |  | FL_TX | M400FC771A | 3 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FT771A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/01/19 | MC-PM-002-Y1
934854 | M400FT771B | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | MUSSAFFAH-ADIA JET A1 P/L,CUSTODY METERING SYSTEM |  | FL_TX | M400FC771B | 3 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | AA213MOV147-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
934855 | M400FT772 | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | FLOW METER SKID 400-FT-772,CUSTODY METERING SYSTEM |  | FL_TX | M400FC772 | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934856 | M400FT861A | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | MUSSAFFAH-TIE IN TO AL-AIN,CUSTODY METERING SYSTEM |  | FL_TX | M400FC861A | 3 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934857 | M400FT861B | METER, FLOW, MASS , FLANGED , 0-300 M3/HR | MUSSAFFAH-TIE IN TO AL-AIN,CUSTODY METERING SYSTEM |  | FL_TX | M400FC861B | 3 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934866 | AT800FT101 | SYSTEM - FLOW TRANSMITER UPGRADE | UPGRADATION OF EXISTING METERING SYSTM (FT-101) |  |  | AT800SYS | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934892 | M30LT161A | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-846MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400-L-006, DISPLACER LVL TRNSMTR | 938875 | DIS_TXTR | M30LIC161A | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934893 | M30LT161B | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-846MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 30-L-006, DISPLACER LVL TRNSMTR | 932607 | DIS_TXTR | M30L006 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934894 | M30LT162A | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-846MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 30-L-007, DISPLACER LVL TRNSMTR | 938876 | DIS_TXTR | M30LIC162A | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934895 | M30LT162B | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-846MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 30-L-007,DISPLACER LVL TRNSMTR | 932608 | DIS_TXTR | M30L007 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934896 | M400LT532 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-654MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L003A, DISPLACER LEVEL TX. | 939715 | DIS_TXTR | M400LI532 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936473 | U29PT644 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 10-3 | PR.TRANS.NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 | 939387 | PRES_TX | U29PI644 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936474 | U29PT645 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 10-3 | PR.TRANS.NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 | 939388 | PRES_TX | U29PI645 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936475 | U29PT646 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 10-3 | PR.TRANS.NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 | 939389 | PRES_TX | U29PI646 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936476 | U29PT647 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 10-3 | PR.TRANS.NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 | 939390 | PRES_TX | U29PI647 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936477 | U29PT648 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 10-3 | From 2902-L Scraper Launcher To SV Station -7 Pr. | 939391 | PRES_TX | U29PI648 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935503 | SALAINCP3IJ2 |  | INSULATION JOINT 2 AT KM 75(C.P.S.# 3 AT KM84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935504 | SALAINCP3RMU1 |  | CP REMOTE MONITORING UNIT (C.P.STATION-3 ATKM84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935505 | SALAINTP51 |  | TEST POINT # 51 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935519 | SALAINTP65 |  | TEST POINT # 65 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935520 | SALAINTP66 |  | TEST POINT # 66 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935521 | SALAINTP67 |  | TEST POINT # 67 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935663 | SMLPGTP18 | CP TEST POINT | TEST POINT # 18 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935664 | SMLPGTP19 | CP TEST POINT | TEST POINT # 19 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935665 | SMLPGTP20 | CP TEST POINT | TEST POINT # 20 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935535 | SALAINTP79 |  | TEST POINT # 79 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935536 | SALAINTP80 |  | TEST POINT # 80 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935537 | SALAINTP81 |  | TEST POINT # 81 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935554 | SALAINTP95 |  | TEST POINT # 95 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935555 | SALAINTP96 |  | TEST POINT # 96 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935570 | SADIATP1 |  | TEST POINT# 1 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935571 | SADIATP2 |  | TEST POINT# 2 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935572 | SADIATP3 |  | TEST POINT# 3 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935454 | SALAINTP9 |  | TEST POINT # 9 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935455 | SALAINTP10 |  | TEST POINT # 10 (C.P. STATION-1 ATKM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935456 | SALAINTP11 |  | TEST POINT # 11 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935470 | SALAINTP22 |  | TEST POINT # 22 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935471 | SALAINTP23 |  | TEST POINT # 23 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935472 | SALAINTP24 |  | TEST POINT # 24 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IAS17007 | U51XP120 | SYSTEM, PRESSURE ALARM AND ESD SHUTDOW, LPG , 20.6 BAR , 17.46 BAR , 70 DEGC, 22 | SIGNAL PIG LAUNCHER 5101-R-01 |  | ALARMANC | U5101R01 | 2 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IAS17008 | U51XP121 | SYSTEM, PRESSURE ALARM AND ESD SHUTDOW, LPG , 20.6 BAR , 17.46 BAR , 70 DEGC, 22 | SIGNAL PIG LAUNCHER 5101-R-01 |  | ALARMANC | U5101R01 | 2 | ALARMANC | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGT59006 | M51TI103 | THERMOMETER, DIAL, 0-100 DEG C , WITHOUT CAPILLARY , 150MM , 1/2" NPT , CENTRE B | TEMP. INDICATOR FOR LPG PIG RECEIVER AT MTF | PGR56198 | INDICATR | M5101R02 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IID58501 | SALAIN12DT101 | DENSITY TRANSDUCER | Density Transducer |  |  | SALAINDMS1 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934922 | M400EPB001 | IRP-1 Emergency DG Set | Emergency DG Set |  | GEN | M400MOTOR | 1 | GENRATOR | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 50 | 50 | 50 | 10 | 10 | 9.0969 | Very High | High | High | y | High Critical | Y | 0 | 12 | m | 0 | y | y | 0 | 0 | 0 | M400EPB001-ME1 | ACTIVE | ELEC | PM | EDS | 1 | WEEKS | 05/08/18 | ME-PM-006-W1
933108 | M400NGR001A | RESISTOR | NEUTRAL EARTHING RESISTOR FOR MUSSAFAH TERMINAL |  | ERTH_NET | M400TMM001A | 3 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400NGR001A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 19/01/19 | ME-PM-LT1-6M
933109 | M400NGR001B | RESISTOR | NEUTRAL EARTHING RESISTOR FOR MUSSAFAH TERMINAL |  | ERTH_NET | M400TMM001B | 2 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400NGR001B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 20/01/19 | ME-PM-LT1-6M
933118 | M400VA2BA491532 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933119 | M400VA2BA491533 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933120 | M400VA2BA491534 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933121 | M400VA2BA491658 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933122 | M400VA2BA491659 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933123 | M400VA2BA491660 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933124 | M400VA2BA491814 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933125 | M400VA2BA491815 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933126 | M400VA2BA491816 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933127 | M400VA2BA591558 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" X 1-1/2" RB 600 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933128 | M400VA2BA591559 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" X 1-1/2" RB 600 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933129 | M400VA2BA591560 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" X 1-1/2" RB 600 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933130 | M400VA2BA691895 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" X 1-1/2" RB 900 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933131 | M400VA2BA691896 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" X 1-1/2" RB 900 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933132 | M400VA2BA691897 | VALVE BALL | BALL VALVE W/LIMIT SWITCH 2" X 1-1/2" RB 900 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933145 | AT800VA2BA391104 | VALVE BALL 2" | BALL VALVE W/LIMIT SWITCH 2" RB 150 RF |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933146 | AA213LT148 | TRANSMITTER, LIQUID LEVEL, 0-13600MMMM , 4-20MA , 240 VAC, +/-10% 50 Hz, +/- 3%U | REC. STATION LEVEL TRANSMITTER for ULG95 Tank 13-T-01C |  | TRANS | AA13LEVEL | 3 | LVL_TX | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933147 | AA313LT150 | TRANSMITTER, LIQUID LEVEL, Servo , 0-13000MMMM , 4-20MA , 240 VAC, +/-10% 50 Hz, | LEVEL TRANSMITTER IN AL AIN RECEIVING STATION for ULG95 Tank 13-T-02E |  | TRANS | AA13LEVEL | 3 | LVL_TX | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933148 | M400LT301 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for ULG95 Tank 400T111 | 939695 | TANKGAUG | M400LI301 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933149 | M400LT303 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for ULG95 Tank 400-T-112 | 939705 | TANKGAUG | M400LI303 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933150 | M400LT305 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for ULG95 Tank 400-T-113 | 939698 | TANKGAUG | M400LI305 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933151 | M400LT307 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for ULG95 Tank 400-T-114 | 939700 | TANKGAUG | M400LI307 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933152 | M400LT309 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for ULG95 Tank 400-T-115 | 939702 | TANKGAUG | M400LI309 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933153 | M400LT311 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for ULG95 Tank 400-T-116 | 939704 | TANKGAUG | M400LI311 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933154 | M400LT313 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for Jet A1 Tank 400-T-117 | 939707 | TANKGAUG | M400LI313 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933155 | M400LT315 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for Jet A1 Tank 400-T-118 | 939709 | TANKGAUG | M400LI315 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933156 | M400LT317 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for Jet A1 Tank 400-T-119 | 939711 | TANKGAUG | M400LI317 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933157 | M400LT319 | TRANSMITTER, LIQUID LEVEL, Servo , 0-17800MMMM , to communication interface , 24 | LEVEL TRANSMITTER for Jet A1 Tank 400-T-120 | 939713 | TANKGAUG | M400LI319 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933158 | M400TGSWS1 | TANK GAUGE SYSTEM WORK STATION | TANK GAUGE SYSTEM WORK STATION |  | STARTERS | M400SCB | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933159 | M400TGSWS2 | TANK GAUGE SYSTEM WORK STATION(REMOTE) | TANK GAUGE SYSTEM WORK STATION(REMOTE) |  | STARTERS | M400SCB | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933165 | M400TML001A | TRANSFORMER,DISTRIBUTION, MTERMINAL IRP -1, 2500 KVA, WELDED COVER TYPE, DYN 11, 50 HZ, 3, 3300, 4330, 437.4 AMP, 3333.4 AMP, 6.45 %, OFF LOAD, ONAN, 6800 KG, 1450 LTR, 45 DEGC, 50 DEGC | 2500KVA,3300/433 VOLT,TRANSFORMER FOR MUSAFFAH TERMINAL IRP - 1 |  | TRANS | M400SCB | 3 | TRANS | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TML001A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 14/01/19 | ME-PM-009-M6
933166 | M400TML001B | TRANSFORMER,DISTRIBUTION, MTERMINAL IRP -1, 2500 KVA, WELDED COVER TYPE, DYN 11, 50 HZ, 3, 3300 V, 1330 V, 437.4 AMP, 3333.4 AMP, 40 AC 10, 6.45 %, OFF LOAD, ONAN, 6800 KG, 1450 LTR, 45 DEGC, 50 DEGC | 2500KVA,3300/433 VOLT,TRANSFORMER FOR MUSAFFAH TERMINAL IRP - 1 |  | TRANS | M400SCB | 2 | TRANS | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TML001B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 18/08/18 | ME-PM-009-M6
933167 | M400TMM001A | TRANSFORMER,DISTRIBUTION, MTERMINAL IRP - 1, 6300 KVA, CONSERVATOR TYPE, DYN 11, 50 HZ, 3, 11000, 3450, 330.7 AMP, 1054.3 AMP, 6.52 %, 4.763 OHM, OLTC, 9, 275, ONAN, 17200 KG KG, 4600 LTR, 45 DEGC, 50 DEGC | TRANSFORMER WITH OLTC,11/3.45KV,6.3MVA,DYN11,ONAN,Z=7.15% |  | TRANS | M400SCB | 3 | TRANS | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TMM001A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 12/11/18 | ME-PM-009-M6
933168 | M400TMM001B | TRANSFORMER,DISTRIBUTION, MTERMINAL IRP -1, 6300 KVA, CONSERVATOR TYPE, DYN 11, 50 HZ, 3, 11000, 3450, 330.7 AMP, 1054.3 AMP, 6.52 %, 4.763 OHM, OLTC, 9, 275, ONAN, 17200 KG KG, 4600 LTR, 45 DEGC, 50 DEGC | TRANSFORMER WITH OLTC,11/3.45KV,6.3MVA,DYN11,ONAN,Z=7.15% |  | TRANS | M400SCB | 2 | TRANS | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TMM001B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 16/12/18 | ME-PM-009-M6
969133170 | M10LZHH063 | SWITCH,LEVEL FLOAT, 2", 316 SS, BASEEFA EXD IIC T6, IP66, SIDE/SIDE, 40 DEG | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-106 | TNK56600 | LVL_SWT | M10T106 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZHH063-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/10/18 | MC-PM-025-M6
969133172 | M10LZHH043 | SWITCH,LEVEL FLOAT, CARBON STEEL, RF FLANGE, ANSI 150, 2", 316 | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-104 | TNK56565 | LVL_SWT | M10T104 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZHH043-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/09/18 | MC-PM-025-M6
TKF13570 | UFORK74105 | 74105 - FORKLIFT 2 TONS | FORKLIFT 3 TONS USE GL ACC.·······51954-6359··-········ |  |  | MREDUNDANT | 3 | 0 | 635901-310600 | MTERMINAL | DECOMMISSIONED | 5 | 5 | 5 | 5 | 5 | 5 | 4.1938 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | UFORK74105UHE | INACTIVE | MECH | PM | EDS | 1 | MONTHS | 08/07/18 | MM-PM-030-M1
XXX935590 | SADIATP21 |  | TEST POINT# 21 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935591 | SADIATP22 |  | TEST POINT# 22 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935592 | SADIATP23 |  | TEST POINT# 23 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130749 | M400TCP006 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-116, 240 VOLT, 50 HZ, 1, 100 VOLT, 50 AMPERES, AIR, BS148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-116 |  | CATHPRO | M400T116 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP006-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 12/01/19 | ME-PM-008-M6
969130750 | M400TCP007 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-117, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-117 |  | CATHPRO | M400T117 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP007-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 13/01/19 | ME-PM-008-M6
969130751 | M400TCP008 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-118, 250 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-118 |  | CATHPRO | M400T118 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP008-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 20/01/19 | ME-PM-008-M6
969130752 | M400TCP009 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-119, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-119 |  | CATHPRO | M400T119 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP009-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 10/08/18 | ME-PM-008-M6
969130753 | M400TCP010 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-120, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-120 |  | CATHPRO | M400T120 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP010-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 17/08/18 | ME-PM-008-M6
969130754 | M400TCP011 | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-201, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS 148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-201 |  | CATHPRO | M400T201 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP011-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/08/18 | ME-PM-008-M6
969130755 | M400TCP012 | CATHODIC PROTECTION, C.P.RECTIFER FOR PIPELINES, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS 148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-210A AT WWTP AREA |  | CATHPRO | M400T210A | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP012-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/09/18 | ME-PM-008-M6
969130759 | M400TCP017 | CATHODIC PROTECTION, C.P.FOR BURRIED PIPELINES, 4.8 KVA, 240 VOLT, 50 HZ, 1, 10 VOLT, 100 AMPERES, AIR, BS 148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR PIPELINES NEAR BATTERY LIMIT AREA |  | CATHPRO | M400SCB | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP017-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 19/10/18 | ME-PM-008-M6
969130761 | M400BATT002A | BATTERY,BANK, Ni-Cad | BATTERY SET FOR 400-UPS-AC-001A AT MTERMINAL IRP-1 CONTROL ROOM |  | BATTERY | M400BATT | 1 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400BATT002A-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 21/08/18 | ME-PM-001-M3
969130762 | M400BATT002B | BATTERY,BANK, Ni-Cad | BATTERY SET FOR 400-UPS-AC-001B AT MTERMINAL IRP-1 CONTROL ROOM |  | BATTERY | M400BATT | 1 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400BATT002B-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 28/08/18 | ME-PM-001-M3
969130763 | M400BATT003A | BATTERY,BANK, Ni-Cad | BATTERY SET FOR 400-UPS-AC-002A AT MTERMINAL IRP-1 CONTROL ROOM |  | BATTERY | M400BATT | 1 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400BATT003A-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 02/09/18 | ME-PM-001-M3
969130764 | M400BATT003B | BATTERY,BANK, Ni-Cad | BATTERY SET FOR 400-UPS-AC-002B AT MTERMINAL IRP-1 CONTROL ROOM |  | BATTERY | M400BATT | 1 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400BATT003B-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 09/09/18 | ME-PM-001-M3
969130765 | M400MCCB002A | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB BOX FOR 400-BATT-002A |  | BREAKER | M400BATT | 1 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130766 | M400MCCB002B | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB BOX FOR 400-BATT-002B |  | BREAKER | M400BATT | 1 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130767 | M400MCCB003A | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB BOX FOR 400BATT-003A |  | BREAKER | M400BATT | 1 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130768 | M400MCCB003B | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB BOX FOR 400-BATT-003B |  | BREAKER | M400BATT | 1 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130769 | M400HVAC001 | PANEL,ELEC POWER, DISTRIBUTION, YES | AHU DISTRIBUTION PANEL AT S/S HVAC ROOM |  | HVAC | M400SCB | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130770 | M400HVAC002 | PANEL,ELEC POWER, DISTRIBUTION, YES | DUCT HEATER DIST.PANEL AT S/S HVAC ROOM |  | HVAC | M400SCB | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130772 | M400HVAC004 | PANEL,ELEC POWER, DISTRIBUTION, YES | DUCT HEATER DIST.PANEL AT CONTROL ROOM HVAC ROOM |  | HVAC | MMCR | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130756 | M400TCP013 | CATHODIC PROTECTION, C.P.RECTIFIER FOR BURRIED PIPELINES AT WWTP AREA, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS 148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR BURRIED PIPELINES AT WWTP AREA |  | CATHPRO | M400T210B | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP013-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 14/09/18 | ME-PM-008-M6
969130757 | M400TCP014 | CATHODIC PROTECTION, C.P.RECTIFER AT WWTP AREA, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS 148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-210C AT WWTP AREA |  | CATHPRO | M400T210C | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP014-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 21/09/18 | ME-PM-008-M6
969130758 | M400TCP016 | CATHODIC PROTECTION, C.P. FOR BURRIED PIPELINES NEAR BATTERY LIMIT, 4.8 KVA, 240 VOLT, 50 HZ, 1, 10 VOLT, 100 AMPERES, AIR, BS 148, 190 LITERS | C.P.RECTIFIER/TRANSFORMER UNIT FOR BURRIED PIPELINES NEAR SLOP PUMP AREA |  | CATHPRO | M400SCB | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400TCP016-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 12/10/18 | ME-PM-008-M6
969130771 | M400HVAC003 | PANEL,ELEC POWER, DISTRIBUTION, YES | AHU DISTRIBUTION PANEL AT CONTROL ROOM HVAC ROOM |  | HVAC | MMCR | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130774 | M400HVAC006 | PANEL,ELEC POWER, DISTRIBUTION, IP 65, YES | DUCT HEATER DIST.PANEL AT ADMIN.BLDG.HVAC ROOM |  | HVAC | MADMIN | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130773 | M400HVAC005 | PANEL,ELEC POWER, DISTRIBUTION, YES | AHU DIST.PANEL AT ADMIN.BLDG.HVAC ROOM |  | HVAC | MADMIN | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131076 | M400PI620A | LOOP,PRESSURE INDICATOR INSTRUMEN | PRESS. INDICATION RUW-MUS, CUSTODY METERING SYSTEM |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131077 | M400PI620B | LOOP,PRESSURE INDICATOR INSTRUMEN | PRESS. INDICATION RUW-MUS, CUSTODY METERING SYSTEM. |  |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131078 | M400PI620C | LOOP,PRESSURE INDICATOR INSTRUMEN | PRESS. INDICATION RUW-MUS, CUSTODY METERING SYSTEM |  | OPENLOOP | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363416 | M410FD637 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006C SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006C SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363417 | M410FD638 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363418 | M410FD639 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363419 | M410FD640 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006C NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006C NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363420 | M410FD641 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-04A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-04A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363421 | M410FD642 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002B NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002B NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363422 | M410FD643 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363423 | M410FD644 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-004A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-004A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363424 | M410FD645 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-004B SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-004B SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363425 | M410FD646 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-004B NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-004B NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363426 | M410FD647 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002B SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-002B SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363427 | M410FD652 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363428 | M410FD653 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024C SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024C SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363429 | M410FD654 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024C NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024C NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281264 | M410TEL002 | SDH/ACS SHARED CABINET | Telephone (Outdoor) | 969195421 | BLDGS | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281265 | PL300RTU001 | RTU Cabinet | SCADA SYSTEM | 936846 | BLDGS | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU001-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 27/03/19 | MC-PM-030-M6
969281266 | PL300RTU002 | RTU Cabinet | SCADA SYSTEM | 936847 | BLDGS | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU002-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 18/04/19 | MC-PM-030-M6
969281267 | PL300RTU003 | RTU Cabinet | SCADA SYSTEM | 936848 | BLDGS | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU003-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 19/04/19 | MC-PM-030-M6
969281268 | PL300RTU004 | RTU Cabinet | SCADA SYSTEM | 936849 | BLDGS | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU004-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 20/04/19 | MC-PM-030-M6
969281269 | PL300RTU005 | RTU Cabinet | SCADA SYSTEM | 936850 | BLDGS | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU005-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 22/05/19 | MC-PM-030-M6
969281270 | PL300RTU006 | RTU Cabinet | SCADA SYSTEM | 936851 | BLDGS | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU006-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 23/05/19 | MC-PM-030-M6
969281274 | M400DCSNC001 | DCS SYSTEM CABINET | DCS SYSTEM CABINET |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281275 | M410PCV921A | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205075 | M410MOV0306 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175579 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0306-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/10/18 | ME-PM-002-M6
969205076 | M410MOV0307 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175580 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0307-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
969205077 | M410MOV0308 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175581 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0308-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/10/18 | ME-PM-002-M6
969205078 | M410MOV0309 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175582 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0309-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
969205079 | M410MOV0310 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175583 | MOV | M410T003 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0310-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
TIS59237 | M10TB233 | TELEPHONE, Ex. PROOF , BUTTON , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIS59238 | M10TB234 | TELEPHONE, Ex. PROOF , BUTTON , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59051 | M50SV131A | VALVE, SOLENOID, 1/2" , 110VDC , BSP , 316 SS , 3-WAY , VENT OPEN ON FAILURE , 1 | FIRE FIGHTING SOLENOID VALVE FOR TANK T-101 | TNK56513 | SOL_VLV | M10T101 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59052 | M50SV131B | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-101 | TNK56513 | SOL_VLV | M10T101 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59073 | M50SV132A | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-102 | TNK56531 | SOL_VLV | M10T102 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59074 | M50SV132B | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-102 | TNK56531 | SOL_VLV | M10T102 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59095 | M50SV133A | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-103 | TNK56547 | SOL_VLV | M10T103 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59096 | M50SV133B | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-103 | TNK56547 | SOL_VLV | M10T103 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59115 | M50SV134W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-104 | TNK56565 | SOL_VLV | M10T104 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59116 | M50SV134F | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-104 | TNK56565 | SOL_VLV | M10T104 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59135 | M50SV135W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-105 | TNK56585 | SOL_VLV | M10T105 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59136 | M50SV135F | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , 316 SS , 3-WAY , 14 KG/M2 , FLAMEPR | FIRE FIGHTING SOLENOID VALVE FOR TANK T-105 | TNK56585 | SOL_VLV | M10T105 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59155 | M50SV136W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | FIRE FIGHTING SOLENOID VALVE FOR TANK T-106 | TNK56600 | SOL_VLV | M10T106 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59156 | M50SV136F | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | FIRE FIGHTING SOLENOID VALVE FOR TANK T-106 | TNK56600 | SOL_VLV | M10T106 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59175 | M50SV137W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | WATERSPRAY SOLENOID VALVE FOR TANK T-107 | TNK56616 | SOL_VLV | M10T107 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59176 | M50SV137F | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | FOAM SOLENOID VALVE FOR TANK T-107 | TNK56616 | SOL_VLV | M10T107 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59193 | M50SV138W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | WATERSPRAY SOLENOID VALVE FOR TANK T-108 | TNK56634 | SOL_VLV | M10T108 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59210 | M50SV139W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | WATERSPRAY SOLENOID VALVE FOR TANK T-109 | TNK56645 | SOL_VLV | M10T109 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59229 | M50SV140W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | WATERSPRAY SOLENOID VALVE FOR TANK T-110 | TNK56656 | SOL_VLV | M10T110 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE59230 | M50SV160W | VALVE, SOLENOID, 1/2" , 110VDC 11.2W , BSP , STEEL , 3-WAY , 14 KG/M2 , FLAMEPRO | FIRE FIGHTING SOLENOID VALVE FOR TANK T-110 | TNK56656 | SOL_VLV | M10T110 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131979 | MQ600MCCB001B | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB FOR 600-BATT-001B |  | BREAKER | MQ600BATT001B | 2 | BREAKER | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131965 | MQ600BATT001B | BATTERY,BANK, Ni-Cad, VN 285-2, 20xVN285-2, 285 AH, 1.14 V, 3079 A, YES | BATTERY FOR 600-UPS-DC-001 |  | BATTERY | MQ600UPSDC001 | 1 | BATTERY | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600BATT001B-ME1 | INACTIVE | ELEC | PM | EDS | 3 | MONTHS | 05/07/18 | ME-PM-001-M3
969131531 | M400XSP109 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CONFERENCE ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131137 | M400LP008B402 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131138 | M400LP011R302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131139 | M400LP011R301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131140 | M400LP011B301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131141 | M400LP011B302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131142 | M400LP011R303 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131143 | M400LP010B503 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR NORTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131144 | M400LP010Y503 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR NORTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131145 | M400LP010R503 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR NORTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131146 | M400LP010R502 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR NORTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131147 | M400LP010B502 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR GATE NO.2 ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131148 | M400LP010Y502 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR NORTH SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131149 | M400LP010R501 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR ADMIN. SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131790 | M400XMC011 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-104 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC011-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131792 | M400XMC013 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-105 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC013-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131793 | M400XMC021 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-106 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC021-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131794 | M400XMC023 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-107 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC023-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131795 | M400XMC031 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-108 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC031-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131796 | M400XMC032 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-109 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC032-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131797 | M400XAC201 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT MAIN LINE PUMP AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC201-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 02/10/18 | MFPS-PM07.M3
969131798 | M400XAC202 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TRANSFER PUMP AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC202-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 02/10/18 | MFPS-PM07.M3
969131799 | M400XAC206 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC206-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 02/10/18 | MFPS-PM07.M3
969131800 | M400XAC207 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC207-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 04/10/18 | MFPS-PM07.M3
969131150 | M400LP010R401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR NORTH SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131151 | M400LP010R402 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR ADMIN SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131152 | M400LP010Y402 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR SECURITY BUILDING ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131153 | M400LP006Y103 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131154 | M400LP006R202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131155 | M400LP006Y202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131156 | M400LP006Y601 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131157 | M400LP006B202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131158 | M400LP006R601 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131159 | M400LP006R604 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131160 | M400LP006B603 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131169 | M400LP006R301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT CONTROL ROOM SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281276 | M410PCV921B | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281277 | M410PCV941A | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281278 | M410PCV941B | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM | LUBE OIL SPILLBACK VALVE, SELF REGULATING, FOR LUBE OIL SYSTEM |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281279 | M410TCV921A | SELF ACTING TEMPERATURE REGULATOR | SELF ACTING TEMPERATURE REGULATOR |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132634 | M400MOV701 | ACTUATOR,ELECTRIC MOTOR | COMPRESSOR VENTING REQ. MOV AT WWTP RECEIVING SUMP CHAIN-1 |  | MOV | M400WWTP | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV701-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/12/18 | ME-PM-002-M6
969283666 | M400PSV203A | VALVE,SAFETY RELIEF | FIRE WATER JOCKEY PUMP A -SAFETY RELIEF VALVE |  | PSV | M400P203A | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969283667 | M400PSV203B | VALVE,SAFETY RELIEF | FIRE WATER JOCKEY PUMP B -SAFETY RELIEF VALVE |  | PSV | M400P203B | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275103 | M410CHV21273001 | 2" Swing Check Valve, BS 5154 Series A, PN 25, Female Threaded End, Union Cover, ASTM B148 Class C95800, Trim Al-Bronze | 2" Swing Check Valve, BS 5154 Series A, PN 25, Female Threaded End, Union Cover, ASTM B148 Class C95800, Trim Al-Bronze |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275104 | M410GAV21223001 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275105 | M410GAV21223002 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275106 | M410GAV21223003 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275107 | M410GAV21223004 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge, UL/FM Approved | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275108 | M410GAV21223005 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275109 | M410GAV21223006 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275110 | M410GAV21223007 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275111 | M410GAV21223008 | 1.5" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1.5" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275112 | M410GAV21223009 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275113 | M410GAV21223010 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275114 | M410GAV21223011 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275115 | M410GAV21223012 | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275116 | M410GAV21223013 | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275117 | M410GAV21223014 | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275118 | M410GAV21223015 | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275119 | M410GAV21223016 | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275120 | M410GAV21223017 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275121 | M410GAV21223018 | 1" Gate Valve, ISO 15761, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge, ASME B16.5 | 1" Gate Valve, ISO 15761, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc, Solid Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275122 | M410GAV21223019 | 1" Gate Valve, ISO 15761, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge, ASME B16.5 | 1" Gate Valve, ISO 15761, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275123 | M410GAV21223020 | 0.75" Gate Valve, ISO 15761, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge, ASME B16.5 | 0.75" Gate Valve, ISO 15761, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275124 | M410GAV21233001 | 2" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132630 | M400MP219A | MOTOR,ELECTRIC, PUMP-A OIL COLLECTION TANK, 1.50 KW, 50 HZ, 415 V, 1440 RPM, 3, 3.73 AMP | MOTOR FOR OIL COLLECTING TANK PUMP-A |  | MOTOR | M400P219A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP219A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 17/11/18 | ME-PM-014-M6
969132631 | M400MP219B | MOTOR,ELECTRIC, PUMP-B OIL COLLECTING TANK, 1.50 KW, 50 HZ, 415 V, 1440 RPM, 3, 3.73 AMP | MOTOR FOR OIL COLLECTING TANK PUMP-A |  | MOTOR | M400P219B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP219B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 18/11/18 | ME-PM-014-M6
969132632 | M400MP220 | MOTOR,ELECTRIC, 1.50 KW, 50 HZ, 415 V, 1440 RPM, 3, 3.73 AMP | MOTOR FOR DISCHARGE PUMP FOR CHEMICAL SLUDGE |  | MOTOR | M400P220 | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP220-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 14/12/18 | ME-PM-014-M6
969132633 | M400MP221 | MOTOR,ELECTRIC, 1.50 KW, 50 HZ, 415 V, 1440 RPM, 3, 3.73 AMP | MOTOR FOR DISCHARGE PUMP FOR OILY SLUDGE |  | MOTOR | M400P221 | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP221-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 15/12/18 | ME-PM-014-M6
969169668 | MFBAY3EGD | FIRE BUILDING BAY#1 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. | FIRE BUILDING BAY#3 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. |  |  | MFBAY3 | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933324 | U29MOV515 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 600, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80EP, IQ20F14B4, IP68, 203Nm | MOV FOR PIG LAUNCHER (NAPHTHA / REF / JET A1 / HSGO, 10" X 8" CL 600) |  | MOV | U2902L | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | U29MOV515-SE1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/10/18 | ME-PM-002-M6
933325 | U29MOV516 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" CL 600, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR PIG LAUNCHER (INAPHTHA / REF / JET A1 / HSGO, 10" CL 600) |  | MOV | U2902L | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | U29MOV516-SE1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/10/18 | ME-PM-002-M6
933326 | AA313MOV150 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | AL AIN RECEIVING STATION ULG 95, 10" X 8" CL 150 |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | AA313MOV150-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933327 | AA313MOV151 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | AL AIN RECEIVING STATION ULG 95, 10" X 8" CL 150 |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | AA313MOV151-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933328 | AA313MOV152 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | AL AIN RECEIVING STATION ULG 95, 12" X 10" CL 150-WITH EXTN LG 1680MM |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | AA313MOV152-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933329 | AA313MOV153 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | AL AIN RECEIVING STATION ULG 95, 12" X 10" CL 150-WITH EXTN LG 2360MM |  | MOV | AA13MOTOR | 3 | MOV | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | AA313MOV153-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933330 | M400MOV001 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-111 OUTLET SHELL VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV001-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
933331 | M400MOV002 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR TANK T-111 OUTLET ISOLATION VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV002-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
933332 | M400MOV003 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14 B4, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-111 OUTLET HEADER VALVE (ULG 95, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV003-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
933333 | M400MOV004 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-111 OUTLET HEADR VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV004-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/10/18 | ME-PM-002-M6
933334 | M400MOV005 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-111 INLET HEADER VALVE (ULG 95, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV005-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/10/18 | ME-PM-002-M6
933335 | M400MOV006 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T- 111 HEADER VALVE (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV006-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/01/19 | ME-PM-002-M6
933336 | M400MOV007 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR TANK T-111 INLET ISOLATION VALVE (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV007-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/09/18 | ME-PM-002-M6
933337 | M400MOV008 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-111 INLET SHELL VALVE (ULG 95, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV008-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/10/18 | ME-PM-002-M6
933338 | M400MOV009 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-112 OUTLET SHELL VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV009-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/10/18 | ME-PM-002-M6
933339 | M400MOV010 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR TANK T- 112 OUTLET ISOLATION VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV010-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
933340 | M400MOV011 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR LOADING PUMP 222A/C/D (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV011-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
933341 | M400MOV012 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-112 OUTLET HEADER VALVE (ULG 95, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV012-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
933342 | M400MOV013 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-112 OUTLET HEADER VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV013-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/10/18 | ME-PM-002-M6
933343 | M400MOV014 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14 B4, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-112 HEADER VALVE (ULG 95, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV014-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
933344 | M400MOV015 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14 B4, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-112 INLET HEADER VALVE (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV015-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/02/19 | ME-PM-002-M6
933345 | M400MOV016 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14 B4, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR TANK T-112 INLET ISOLATION VALVEULG 95, 16" X 14" CL 300 |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV016-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/02/19 | ME-PM-002-M6
933346 | M400MOV017 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-112 INLET SHELL VALVE (ULG 95, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV017-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
933347 | M400MOV018 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR TANK T-113 OUTLET SHELL VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV018-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/10/18 | ME-PM-002-M6
933348 | M400MOV019 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR TANK T-113 OUTLET ISOLATION VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV019-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/12/18 | ME-PM-002-M6
933349 | M400MOV020 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14 B4, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-113 TO LOADING PUMP 222A,C & D (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV020-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/12/18 | ME-PM-002-M6
933350 | M400MOV021 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-113 OUTLET HEADER VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV021-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/09/18 | ME-PM-002-M6
933351 | M400MOV022 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-113 INLET HEADER VALVE (ULG 95, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV022-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/09/18 | ME-PM-002-M6
933352 | M400MOV023 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-113 INLET HEADER VALVE (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV023-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/02/19 | ME-PM-002-M6
933353 | M400MOV024 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-113 INLET ISOLATION VALVE (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV024-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/02/19 | ME-PM-002-M6
933354 | M400MOV025 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-113 INLET SHELL VALVE (ULG 95, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV025-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/09/18 | ME-PM-002-M6
933355 | M400MOV026 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-114 OUTLET SHELL VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV026-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/09/18 | ME-PM-002-M6
933356 | M400MOV027 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-114 OUTLET ISOLATION VALVE (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV027-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
933357 | M400MOV028 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-114 OUTLET MANIFOLD (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV028-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
933358 | M400MOV029 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE 80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-114 OUTLET HEADER (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV029-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
933359 | M400MOV030 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-114 INLET HEADER (ULG 91, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV030-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/09/18 | ME-PM-002-M6
933360 | M400MOV031 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-114 INLET HEADER (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV031-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/01/19 | ME-PM-002-M6
933361 | M400MOV032 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-114 INLET ISOLATION VALVE.(ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV032-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/01/19 | ME-PM-002-M6
933362 | M400MOV033 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-114 INLET SHELL VALVE (ULG 95, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV033-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/09/18 | ME-PM-002-M6
933363 | M400MOV034 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-115 OUTLET SHELL (ULG 91, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV034-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/09/18 | ME-PM-002-M6
933364 | M400MOV035 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-115 OUTLET ISOLATION (ULG 95, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV035-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/12/18 | ME-PM-002-M6
933365 | M400MOV036 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-115 TO LOADING PUMP (222A/B/C) ULG 95, 18" X 16" CL 150 |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV036-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/12/18 | ME-PM-002-M6
933366 | M400MOV037 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-115 OUTLET HEADER (ULG 91, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV037-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
933367 | M400MOV038 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-115 INLET HEADER (ULG 91, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV038-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/09/18 | ME-PM-002-M6
933368 | M400MOV039 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-115 INLET HEADER (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV039-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/02/19 | ME-PM-002-M6
933369 | M400MOV040 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14, SAE 80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-115 INLET ISOLATION VALVE (ULG 95, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV040-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/02/19 | ME-PM-002-M6
933370 | M400MOV041 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-115 INLET SHELL (ULG 91, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV041-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
933371 | M400MOV042 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE 80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T116 OUTLET SHELL -GAS OIL, 18" X 16" CL 150 |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV042-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/09/18 | ME-PM-002-M6
933372 | M400MOV043 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-116 OUTLET ISOLATION (GAS OIL, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV043-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/02/19 | ME-PM-002-M6
933373 | M400MOV044 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-116 OUTLET HEADER (GAS OIL, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV044-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/02/19 | ME-PM-002-M6
933374 | M400MOV045 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-116 PUTLET HEADER (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV045-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/09/18 | ME-PM-002-M6
933375 | M400MOV046 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-116 INLET HEADER (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV046-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/09/18 | ME-PM-002-M6
933376 | M400MOV047 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-116 INLET HEADER (GAS OIL, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV047-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/02/19 | ME-PM-002-M6
933377 | M400MOV048 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-116 INLET ISOLATION (GAS OIL, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV048-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
933378 | M400MOV049 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-116 INLET SHELL.(GAS OIL, 20" X18" CL 300 WITH EXTN LG 1920MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV049-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/09/18 | ME-PM-002-M6
933379 | M400MOV050 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-116 INLET HEADER (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV050-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
933380 | M400MOV051 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-116 TO LOADING PUMP 222A/C & D (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV051-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/12/18 | ME-PM-002-M6
933381 | M400MOV052 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-116 INLET SHELL ,JET MIX (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV052-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/09/18 | ME-PM-002-M6
933382 | M400MOV053 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-116 JET MIXER ISOLATION (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV053-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
933383 | M400MOV058 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-103 JET MIXER ISOLATION.(GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV058-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/02/19 | ME-PM-002-M6
933384 | M400MOV059 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-102 JET MIXER ISOLATION (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV059-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 31/01/19 | ME-PM-002-M6
933385 | M400MOV060 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 JET MIXER ISOLATION (GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV060-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/01/19 | ME-PM-002-M6
933386 | M400MOV061 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 INLET ISOLATION. (GAS OIL, 10" X 8" CL 300 WITH EXTN LG 2590MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV061-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/10/18 | ME-PM-002-M6
933387 | M400MOV062 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 INLET ISOLATION.(GAS OIL, 10" X 8" CL 300 WITH EXTN LG 1830MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV062-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/10/18 | ME-PM-002-M6
933388 | M400MOV063 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 INLET HEADER.(GAS OIL, 10" X 8" CL 300 WITH EXTN LG 1830MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV063-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/01/19 | ME-PM-002-M6
933389 | M400MOV064 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 OUTLET HEADER.(GAS OIL, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV064-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/10/18 | ME-PM-002-M6
934382 | M400TEL002 | CABINET | TELECOM CABINET |  |  | M400TEL | 3 | TELEPHON | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934383 | M400PRC001 | SYSTEM | GPS CLOCK SYSTEM |  |  | M400MUX001 | 1 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934384 | M400TEL001 | CABINET | TELECOM CABINET |  |  | M400TEL | 3 | TELEPHON | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934385 | M400ODF001 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | M400MUX001 | 3 | DCS_PNL | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934386 | M400MDF001 | TELECOM MAIN DISTRIBUTlON FRAME | MAIN DIST. FRAME |  | TELECOM | M400IPX001 | 1 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934387 | PL300ODF007 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | PL300MUX007 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934388 | PL300TEL001 | CABINET | TELECOM CABINET |  |  | PL300MUX001 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934389 | PL300TEL002 | CABINET | TELECOM CABINET |  |  | PL300MUX002 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934390 | PL300TEL003 | CABINET | TELECOM CABINET |  |  | PL300MUX003 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934391 | PL300TEL004 | CABINET | TELECOM CABINET |  |  | PL300MUX004 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934392 | PL300TEL005 | CABINET | TELECOM CABINET |  |  | PL300MUX005 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934393 | PL300TEL006 | CABINET | TELECOM CABINET |  |  | PL300MUX006 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934394 | PL300TEL007 | CABINET | TELECOM CABINET |  |  | PL300MUX007 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934395 | PL300ODF001 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | PL300MUX001 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934396 | PL300ODF002 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | PL300MUX002 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934397 | PL300ODF003 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | PL300MUX003 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934398 | PL300ODF004 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | PL300MUX004 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935484 | SALAINTP36 | TEST POINT # 36 (C.P.STATION-2 AT KM 18.5) | TEST POINT # 36 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935500 | SALAINCP3IJ1 | INSULATION JOINT 1 AT KM 75 (C.P.S.# 3 AT KM84.5) | INSULATION JOINT 1 AT KM 75 (C.P.S.# 3 AT KM84.5) |  |  | SALAINCPS3 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935518 | SALAINTP64 | TEST POINT # 64 (C.P.STATION-3 AT KM 84.5) | TEST POINT # 64 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935533 | SALAINTP78 | TEST POINT # 78 (C.P.STATION-4 AT KM 149) | TEST POINT # 78 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935553 | SALAINTP94 | TEST POINT # 94 (C.P.STATION-4 AT KM 149) | TEST POINT # 94 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935569 | SALAINCP4IJ1 | INULATING JOINT 1 AT KM 149 (C.P.S.# 4 ATKM 149) | INULATING JOINT 1 AT KM 149 (C.P.S.# 4 ATKM 149) |  |  | SALAINCPS4 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132788 | M400POV702 | VALVE,SEQUENCIAL CONTROL/ESD | SLUDGE REMOVING PRESSURE OPERATED VALVE OF DAF IN WASTE WATER TREATMENT PLANT AT MS&P TERMINAL. |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV702-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/11/18 | MC-PM-026-M6
969195587 | M410CHV2354007 | 4" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 150# | 4" CAST STEEL SWING CHECK VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195588 | M410CHV2354008 | 12" DUAL PLATE CHECK VALVE, FLANGE, 150# | 12" DUAL PLATE CHECK VALVE, FLANGE, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195525 | M410FU451 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195526 | M410FU452 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195527 | M410FU453 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195528 | M410STR901B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195529 | M410STR902B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195530 | M410STR903B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195531 | M410FU701 | DELUGE SKID (FOR 410-P-007A/B/C) | DELUGE SKID AT ITTP PUMP HOUSE-IRP-II(410-P-007A/B/C) |  |  | M410FGSC001 | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195532 | M410FU702 | DELUGE SKID (FOR 410-P-008A/B) | FIRE DELUGE SKID - ITT PUMP HOUSE - IRP2. |  |  | M410MISC | 1 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195533 | M410FU703 | DELUGE SKID (FOR 410-P-0014A/B) | DELUGE SKID AT ITTP PUMP HOUSE-IRP-II(410-P-0014A/B) |  |  | M410FGSC001 | 1 | F&G_PNL | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269253 | M410BAV21243061 | 0.5" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved | 0.5" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132699 | M400ME016 | MOTOR,ELECTRIC, GEAR DRIVE MOTOR, 0.37 KW, 50 HZ, 415 V, 1500 RPM, 3, 1.95 AMP, 400MCC001 | GEAR DRIVE MOTOR OIL SKIMMER RECEIVING SUMP-CHAIN I |  | MOTOR | M400WWTP | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400ME016-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 19/01/19 | ME-PM-014-M6
XXX935618 | SMTP19 |  | TEST POINT# 19 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935619 | SMTP20 |  | TEST POINT# 20 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935620 | SMTP21 |  | TEST POINT# 21 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935633 | SMTP35 |  | TEST POINT# 35 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935634 | SMTP36 |  | TEST POINT# 36 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935648 | SMLPGTP3 | CP TEST POINT | TEST POINT # 3 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935649 | SMLPGTP4 | CP TEST POINT | TEST POINT # 4 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131579 | M400XSP169 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN MECHANICAL REPAIR ROOM -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131580 | M400XSP170 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN MECHANICAL REPAIR ROOM -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131581 | M400XSP171 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN STORAGE ROOM -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131582 | M400XSP172 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CHANGE ROOM -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131583 | M400XSP173 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SUPERVISOR'S ROOM -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131584 | M400XSP174 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SUPERVISOR'S ROOM -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131585 | M400XSP175 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SUPERVISOR'S ROOM -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131586 | M400XHE001 | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT BATTERY ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131587 | M400XHE002 | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT BATTERY ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131588 | M400XHE003 | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT BATTERY ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131603 | M400XHE018 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT TRANSFORMER M400-TML001A IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131607 | M400XHE025 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT PANTRY ROOM IN ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131679 | M400XAL033 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT OUTSIDE STAFF OFFICE OF FIRE STATION BUILDING |  | ALARMANC | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131680 | M400XAL034 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT AIR COMPRESSOR ROOM OF FIRE STATION BUILDING |  | ALARMANC | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131681 | M400XAL035 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT FIRE FIGHTING VEHICLE AREA OF FIRE STATION BUILDING |  | ALARMANC | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131682 | M400XAL036 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT PALLET AREA IN WAREHOUSE |  | ALARMANC | M400FACP005 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131683 | M400XAL037 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT PASSAGE WAY IN WAREHOUSE |  | ALARMANC | M400FACP005 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131684 | M400XAL038 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT SUPERISOR ROOM IN WAREHOUSE |  | ALARMANC | M400FACP005 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131685 | M400XLF001 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE,PLANT WIDE SIREN AT BUILDING ROOF AT PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131686 | M400XLF002 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE,PLANT WIDE SIREN AT BUILDING ROOF OF SUB STATION |  | ALARMANC | M400FACP002 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131687 | M400XLF003 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE,PLANT WIDE SIREN AT BUILDING ROOF OF ADMINISTRATION |  | ALARMANC | M400FACP004 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131688 | M400XLF004 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE,PLANT WIDE SIREN AT BUILDING ROOF OF WAREHOUSE |  | ALARMANC | M400FACP005 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131689 | M400XLF005 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE,PLANT WIDE SIREN AT BUILDING ROOF OF FIRE & SAFETY |  | ALARMANC | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131690 | M400XLF201 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE FOR MAIN LINE PUMP AREA |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131604 | M400XHE019 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR FOR 400-EPB-001 IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131624 | M400XAC010 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT NEAR 400EPB001 IN SUB STATION |  | PB_HS-MC | M400FACP002 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC010-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 25/09/18 | MFPS-PM07.M3
969131634 | M400XAC030 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT OUTSIDE ENTRANCE LOBBY OFFIRE STATION BUILDING |  | PB_HS-MC | M400FACP003 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC030-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 21/10/18 | MFPS-PM07.M3
969131723 | M400XHD216A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-117 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD216A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/09/18 | MFPS-PM05.M3
969131724 | M400XHD216B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-117 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD216B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 10/09/18 | MFPS-PM05.M3
969131726 | M400XHD217B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-118 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD217B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 10/09/18 | MFPS-PM05.M3
969131727 | M400XHD218A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-119 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD218A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 12/09/18 | MFPS-PM05.M3
969131729 | M400XHD219A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-120 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD219A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 12/09/18 | MFPS-PM05.M3
969131730 | M400XHD219B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-120 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD219B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 17/09/18 | MFPS-PM05.M3
969131732 | M400XHD221B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR SUMP TANK 400-V-176 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD221B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 17/09/18 | MFPS-PM05.M3
969131736 | M50XES001 | HORN, SOUNDER, YES | SOUNDER NEAR TANK T-101 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131737 | M50XES002 | HORN, SOUNDER, 24VDC, YES | SOUNDER NEAR TANK T-102 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131739 | M50XES011 | HORN, SOUNDER, 24VDC, YES | SOUNDER NEAR TANK NO. T-104 & T-105 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131744 | M400XFB004 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK NO. 108 TO T-110 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131608 | M400XAS001 | HORN, SOUNDER, 24VDC, YES | SOUNDER-AUDIBLE HZARD ALARM AT PLCR-BUILDING ENTRANCE-PLCR |  | LIGHT | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131609 | M400XAS002 | HORN, SOUNDER, 24VDC, YES | SOUNDER-AUDIBLE HAZARD ALARM AT SUB STATION BUILDING ENTRANCE |  | LIGHT | M400FACP002 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131610 | M400XAS003 | HORN, SOUNDER, 24VDC, YES | SOUNDER-AUDIBLE HAZARD ALARM AT ADMINISTRATION BUILDING ENTRANCE |  | LIGHT | M400FACP004 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131611 | M400XAS004 | HORN, SOUNDER, 24VDC, YES | SOUNDER-AUDIBLE HAZARD ALARM AT WAREHOUSE BUILDING ENTRANCE |  | LIGHT | M400FACP005 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP58341 | S21XXT101 | SCRAPPER DETECTOR INDICATION TRANSMITTER | SCRAPPER DETECTOR INDICATION TRANSMITTER | IIP58340 |  | S21XPI101 | 1 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59007 | M51PT119 | TRANSMITTER, PRESSURE, GAUGE , 0-16 BAR , 4-20MA , 10.5-55VDC , 1/2" NPT , M20 X | PR. TRAN. FOR LPG PIG RECEIVER AT MUSSAFAH TERMNL | PGR56198 | PRES_TX | M5101R02 | 2 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M51PT119-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/08/18 | MC-PM-007-M6
IIP59008 | M51PT129 | TRANSMITTER, PRESSURE, GAUGE , 0-16 BAR , 4-20MA , 10.5-55VDC , 1/2" NPT , M20 X | PR. TRAN. FOR LPG PIG RECEIVER AT MUSSAFAH TERMNL | PGR56198 | PRES_TX | M5101R02 | 2 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M51PT129-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/08/18 | MC-PM-007-M6
IIP59017 | M10PT301 | TRANSMITTER, PRESSURE, DIAPHRAGM , 0-10 BAR , 4-20MA+HART PROTOCOL , 10.5-42.4VD | PRESSURE TRANSMITTER MULTIPRODUCT INLET METERING |  | PRES_TX | M10INLETMET | 2 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59022 | M10PT302 | TRANSMITTER, PRESSURE, DIAPHRAGM , 0-10 BAR , 4-20MA+HART PROTOCOL , 10.5-42.4VD | PRESS. TRANSMITTER MULTI PRODUCT I/L METERING SKID |  | PRES_TX | M10INLETMET | 2 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59036 | M10PT011 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , BASEEFA | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-101 | TNK56513 | PRES_TX | M10T101 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275071 | M410BAV21273002 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Flat Face, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Flat Face, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271746 | M410STR040B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271742 | M410STR024A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271743 | M410STR024B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271744 | M410STR024C | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271745 | M410STR040A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147448 | M410P007C | ULG 91/95 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007C-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/11/18 | MM-PM-7-Y1
969147449 | M410P008A | GAS OIL INTER-TANK TRANSFER PUMP | GAS OIL INTER-TANK TRANSFER PUMP |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-4-Y1
969147450 | M410P008B | GAS OIL INTER-TANK TRANSFER PUMP | GAS OIL INTER-TANK TRANSFER PUMP |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 11/11/18 | MM-PM-4-Y1
969147451 | M410P014A | JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-4-Y1
969147452 | M410P014B | JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-4-Y1
969147453 | M410P009 | ULG/GAS OIL SUMP CENTRIFUGAL PUMP ON 410V003. | ULG/GAS OIL SUMP PUMP ON 410V003. |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P009-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-7-Y1
969147454 | M410P010 | JET A1 SUMP CENTRIFUGAL PUMP ON 410V004. | JET A1 SUMP PUMP ON 410V004. |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P010-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-7-Y1
969147455 | M410VH001 | EOT CRANE FOR INTER-TANK TRANSFER PUMPS SHELTER | EOT CRANE FOR INTER-TANK TRANSFER PUMPS SHELTER |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 15/09/18 | ME-PM-007-M6
969147456 | M410VH002 | EOT CRANE FOR FIRE WATER PUMPS SHELTER | EOT CRANE FOR FIRE WATER PUMPS SHELTER |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH002-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 16/09/18 | ME-PM-007-M6
969147457 | M410VH003 | MONORAIL HOIST | MONORAIL HOIST |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH003-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 17/09/18 | ME-PM-007-M6
969147458 | M410EP001 | CONTROL PANEL FOR EMERGENCY DIESEL GENERATOR | CONTROL PANEL FOR EMERGENCY DIESEL GENERATOR |  | GENRATOR | M410MOTOR | 1 | GENRATOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 10 | 10 | 10 | 8.0969 | High | Medium | Medium | y | High Critical | Y | 0 | 6 | e | 0 | y | y | 0 | 0 | 0 | M410EP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 12/12/18 | ME-PNL1-PM-M6
969281280 | M410TCV921B | SELF ACTING TEMPERATURE REGULATOR | SELF ACTING TEMPERATURE REGULATOR |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281281 | M410TCV941A | SELF ACTING TEMPERATURE REGULATOR | SELF ACTING TEMPERATURE REGULATOR |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281282 | M410TCV941B | SELF ACTING TEMPERATURE REGULATOR | SELF ACTING TEMPERATURE REGULATOR |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281283 | M410TT921A | RTD / THERMOWELL / TRANSMITTER | RTD / THERMOWELL / TRANSMITTER |  | TEMP_TX | M410TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281284 | M410TT921B | RTD / THERMOWELL / TRANSMITTER | RTD / THERMOWELL / TRANSMITTER |  | TEMP_TX | M410TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281285 | M410TT941A | RTD / THERMOWELL / TRANSMITTER | RTD / THERMOWELL / TRANSMITTER |  | TEMP_TX | M410TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281286 | M410TT941B | RTD / THERMOWELL / TRANSMITTER | RTD / THERMOWELL / TRANSMITTER |  | TEMP_TX | M410TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281287 | M410PT921AA | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT921AA-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281296 | M410TG921BF | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281297 | M410TG921CF | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281298 | M410TG941AF | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281299 | M410TG941BF | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281300 | M410TG941CF | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281301 | M410TG921AE | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281302 | M410TG921BE | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281303 | M410TG921CE | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281304 | M410TG941AE | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281305 | M410TG941BE | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281306 | M410TG941CE | Bi-METAL TEMERATURE GAUGE | Bi-METAL TEMERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281307 | M410PG921A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281308 | M410PG921B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281309 | M410PG941A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281310 | M410PG941B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281311 | M410PDT921A | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT921A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281312 | M410PDT921B | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT921B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281313 | M410PDT941A | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT941A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281314 | M410PDT941B | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER | LUBE OIL FILTER DIFFERENTIAL PRESSURE TRANSMITTER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT941B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281315 | M410LT921A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | LVL_TX | M410LEVEL | 3 | LVL_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281316 | M410LT921B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | LVL_TX | M410LEVEL | 3 | LVL_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281317 | M410LT941A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | LVL_TX | M410LEVEL | 3 | LVL_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281318 | M410LT941B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | LVL_TX | M410LEVEL | 3 | LVL_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281319 | M410SRV921A | PRESSURE RELIEF VALVE | PRESSURE RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281320 | M410SRV921B | PRESSURE RELIEF VALVE | PRESSURE RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281321 | M410SRV941A | PRESSURE RELIEF VALVE | PRESSURE RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281322 | M410SRV941B | PRESSURE RELIEF VALVE | PRESSURE RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281323 | M410P050BA | LUB OIL PUMP FOR 410-P-002B PUMP | LUBE OIL PUMP FOR 410-P-002B PUMP |  | PUCEOH | M410P002B | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P050BA-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969132648 | M400XHE023 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 15-32VDC, IP43, YES | HEAT DETECTOR AT MTERMINAL IRP-1 EMERGENCY DIESEL GENERATOR CONTAINER |  | FG_DET | M400FACP006 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131118 | M400LP006R101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT EAST SIDE OF SUB STATION 400 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132807 | M400P209B | PUMP, SCREW | FEED PUMP B TO DAF |  | PUSC | M400WWTPPUMP | 2 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P209B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 09/11/18 | ME-PM-014-M6
969132790 | M400POV704 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-INFLOW SAFETY FILTER |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV704-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/12/18 | MC-PM-026-M6
969132740 | M400LSHH730 | SWITCH,LEVEL | LEVEL SWITCH-EFFLUENT STORAGE TANK 2 |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132741 | M400LSHH733 | SWITCH,LEVEL | LEVEL SWITCH - EFFLUENT STORAFGE TANK - 3 |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132804 | M400P208A | PUMP, SUBMERSIBLE | FEED PUMP A - CHAIN - I |  | PUCE | M400WWTPPUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P208A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/11/18 | MM-PM-016-M6
969132806 | M400P209A | PUMP, SCREW | FEED PUMP A TO DAF |  | PUSC | M400WWTPPUMP | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P209A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 08/11/18 | ME-PM-014-M6
XXX935585 | SADIATP16 | TEST POINT# 16 (C.P. AT A.D. INT'L AIRPORT) | TEST POINT# 16 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935601 | SMTP2 | TEST POINT# 2 ( MUSSAFAH PRODUCT TRANS. P.L.) | TEST POINT# 2 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935617 | SMTP18 | TEST POINT# 18 ( MUSSAFAH PRODUCT TRANS. P.L.) | TEST POINT# 18 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935632 | SMTP34 | TEST POINT# 34 ( MUSSAFAH PRODUCT TRANS. P.L.) | TEST POINT# 34 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935647 | SMLPGTP2 | CP TEST POINT | TEST POINT # 2 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935662 | SMLPGTP17 | CP TEST POINT | TEST POINT # 17 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935678 | SMLPGTP33 | CP TEST POINT | TEST POINT # 33 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935693 | SMLPGTP48 | CP TEST POINT | TEST POINT # 48 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57573 | MLIGHTPOLE01 | LIGHT, SODIUM VAPOUR , 240VAC , WHITE | POLE LIGHT AT TANK 110 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57574 | MLIGHTPOLE02 | LIGHT, SODIUM VAPOUR , 240VAC , WHITE | POLE LIGHT AT TANK 108 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57575 | MLIGHTPOLE03 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT AT TANK 107 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57576 | MLIGHTPOLE04 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET. TANK 105 & 106 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57577 | MLIGHTPOLE05 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET. TANK 104 & 105 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57578 | MLIGHTPOLE06 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET. TANK 103 & 104 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57579 | MLIGHTPOLE07 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT TANK 103 FENCE CORNER. |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57580 | MLIGHTPOLE08 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET. TANK 102 & 103 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57581 | MLIGHTPOLE09 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET. TANK 101 & 102 FENCE SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57582 | MLIGHTPOLE010 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET. TANK 101 & FUTURE TANK |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57583 | MLIGHTPOLE011 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT AT PIG RECEIVE AREA WALL CORNER |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937253 | M400P020 | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 79MM , SILICON CARBIDE , 316 SS , FLUOROELA | OFF SPEC JET A1 BOOSTER PUMP TO RUWAIS. | 933878 | PUMPS | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P020MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/12/18 | MM-PM-001-M6
937254 | M400P017B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 79MM , SILICON CARBIDE , 316 SS , FLUOROELA | JET A1 BOOSTER PUMP-B TO ADIA. | 933877 | PUMPS | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P017BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/11/18 | MM-PM-004-M6
937255 | M400P017A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 79MM , SILICON CARBIDE , 316 SS , FLUOROELA | JET A1 BOOSTER PUMP-A TO ADIA. | 933876 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P017AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/10/18 | MM-PM-004-M6
937256 | M400P015B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 50MM , SILICON CARBIDE , 316 SS , FLUOROELA | ULG95/ULG98/GAS OIL/JET A1/KEROSENE BOOSTER PUMPS | 933875 | PUMPS | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | m | 0 | N | N | 0 | 0 | 0 | M400P015B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/11/18 | MM-PM-007-M6
937257 | M400P015A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 50MM , SILICON CARBIDE , 316 SS , FLUOROELA | ULG95/GAS OIL/JET A1/KEROSENE BOOSTER PUMP- AL AIN | 933874 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P015A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/10/18 | MM-PM-007-M6
938615 | M400ME010 | HVAC | HVAC |  | HVAC |  | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938616 | M400DI303 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for ULG 95 Tank 400-T-112 |  | ANALYSER | M400T112 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI303-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 15/08/18 | MC-PM-014-M3
938617 | M400DI305 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for ULG 95 Tank 400-T-113 |  | ANALYSER | M400T113 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI305-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/08/18 | MC-PM-014-M3
938618 | M400DI307 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for ULG 95 Tank 400-T-114 |  | ANALYSER | M400T114 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI307-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/08/18 | MC-PM-014-M3
938619 | M400DI309 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for ULG 95 Tank 400-T-115 |  | ANALYSER | M400T115 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI309-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/08/18 | MC-PM-014-M3
938620 | M400DI311 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for ULG 95 Tank 400-T-116 |  | ANALYSER | M400T116 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI311-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 21/08/18 | MC-PM-014-M3
938621 | M400DI313 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for ULG 95 Tank 400-T-117 |  | ANALYSER | M400T117 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938622 | M400DI315 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for JET A1 Tank 400-T-118 |  | ANALYSER | M400T118 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI315-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/08/18 | MC-PM-014-M3
938623 | M400DI317 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for JET A1 Tank 400-T-119 |  | ANALYSER | M400T119 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI317-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 24/08/18 | MC-PM-014-M3
938624 | M400DI319 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for JET A1 Tank 400-T-120 |  | ANALYSER | M400T120 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI319-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/08/18 | MC-PM-014-M3
938626 | M400DI541A | ANALYSER, DENSITY | Metering Skid 400-FT-541A | 938681 | ANALYSER | M400FC541A | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI541A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/09/18 | MC-PM-014-M3
938627 | M400DI541B | ANALYSER, DENSITY | Metering Skid 400-FT-541B | 934849 | ANALYSER | M400FC541B | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI541B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 02/09/18 | MC-PM-014-M3
938628 | M400DI620A | ANALYSER, DENSITY | FLOW METER SKID RUW-MUS, CUSTODY METERING SYSTEM | 934850 | ANALYSER | M400FC620A | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI620A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/09/18 | MC-PM-014-M3
938629 | M400DI620B | ANALYSER, DENSITY | FLOW METER SKID RUW-MUS, CUSTODY METERING SYSTEM | 934851 | ANALYSER | M400FC620B | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI620B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/09/18 | MC-PM-014-M3
938630 | M400DI620C | ANALYSER, DENSITY | FLOW METER SKID RUW-MUS, CUSTODY METERING SYSTEM | 934852 | ANALYSER | M400FC620C | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI620C-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/09/18 | MC-PM-014-M3
938631 | M400ME011 | HVAC | HVAC |  | HVAC |  | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938632 | M400DI771A | ANALYSER, DENSITY | Density flow metering skid 400-F-771A | 934853 | ANALYSER | M400FC771A | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI771A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/09/18 | MC-PM-014-M3
938633 | M400DI771B | ANALYSER, DENSITY | Density flow metering skid 400-F-771B | 934854 | ANALYSER | M400FC771B | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI771B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 02/09/18 | MC-PM-014-M3
938634 | M400DI772 | ANALYSER, DENSITY | MUSSAFFAH-ADIA JET A1 P/L,CUSTODY METERING SYSTEM | 934855 | ANALYSER | M400FC772 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI772-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/09/18 | MC-PM-014-M3
938635 | M400ME012 | HVAC | HVAC |  | HVAC |  | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938636 | M400DI861A | ANALYSER, DENSITY | MUSSAFFAH-TIE IN TO AL-AIN,CUSTODY METERING SYSTEM | 934856 | ANALYSER | M400FC861A | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI861A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/09/18 | MC-PM-014-M3
938637 | M400DI861B | ANALYSER, DENSITY | MUSSAFFAH-TIE IN TO AL-AIN,CUSTODY METERING SYSTEM | 934857 | ANALYSER | M400FC861B | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DI861B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/09/18 | MC-PM-014-M3
938638 | M400PT461 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-10 BAR , 4-20mA , 10.5-30 | PR.TR. DISCHARGE LUBE OIL PUMP (M400P019) | 939783 | PRES_TX | M400PI461C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938639 | M400PT462 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-10 BAR , 4-20mA , 10.5-30 | PR.TR. DISCHARGE LUBE OIL PUMP (M400P019) | 939784 | PRES_TX | M400PI462C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938640 | M400PG463 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS , SS | PRESSURE GAUGE FOR M400P019 | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938641 | M400TG465 | THERMOMETER, DIAL, 0-120 DEG C , BIMETAL , 100MM , 1/2" NPT , BOTTOM , 304 SS , | LUBE OIL RETURN MAIN MOTOR BEARING NDE (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938642 | M400TG461 | THERMOMETER, DIAL, BIMETALLIC TEMPERATURE GAUGE , 0-100 DEG C | TEMPERATURE GAUGE OIL RESEVOIR (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938643 | M400TG463 | THERMOMETER, DIAL, 0-120 DEG C , BIMETAL , 100MM , 1/2" NPT , BOTTOM , 304 SS , | LUBE OIL RETURN MAIN MOTOR BEARING CE (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938644 | M400ME014 | HVAC FOR GUARD HOUSE BUILDING | HVAC FOR GUARD HOUSE BUILDING |  | HVAC |  | 4 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938645 | M400V117 | U/G POTABLE WATER STORAGE TANK | U/G POTABLE WATER STORAGE TANK |  | TK | M400TANKS | 3 | TK | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 1 | 1 | 1 | 5 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938646 | M400T202 | O/H WATER STORAGE TANK ON ADMIN. BUILDING | O/H WATER STORAGE TANK ON ADMIN. BUILDING |  | TK |  | 3 | TK | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 1 | 1 | 1 | 5 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938647 | M400TE620A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP. ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 939207 | TEMP_ELE | M400TI620A | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938648 | M400TT620A | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX RUW-MUS, CUSTODY METERING SYSTEM | 939207 | TEMP_TX | M400TI620A | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938649 | M400PDT620A | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | Diff. Pr. TRANSMITTR RUW-MUS, Metering Skid 400FT620A. | 939740 |  | M400PDI620A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938650 | M400PT620A | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX RUW-MUS, CUSTODY METERING SYSTEM | 934850 | PRES_TX | M400PI620A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938651 | M400FE620A | METER, FLOW, MASS | D.P. TX ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 934850 | ORIFICE | M400FC620A | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938652 | M400TT620B | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX RUW-MUS, CUSTODY METERING SYSTEM | 939208 | TEMP_TX | M400TI620B | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938653 | M400TT620C | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX RUW-MUS, CUSTODY METERING SYSTEM | 939209 | TEMP_TX | M400TI620C | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938654 | M400TE620B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP. ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 939208 | TEMP_ELE | M400TI620B | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938655 | M400TE620C | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP. ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 939209 | TEMP_ELE | M400TI620C | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938656 | M400FE620B | SENSOR, DIFFERENTIAL PRESSURE | D.P. TX ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 934851 | ORIFICE | M400FC620B | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938657 | M400FE620C | SENSOR, DIFFERENTIAL PRESSURE | D.P. TX ELEMENT RUW-MUS, CUSTODY METERING SYSTEM | 934852 | ORIFICE | M400FC620C | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938658 | M400PT620B | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX RUW-MUS, CUSTODY METERING SYSTEM | 934851 | PRES_TX | M400PI620B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938659 | M400PT620C | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX RUW-MUS, CUSTODY METERING SYSTEM | 934852 | PRES_TX | M400PI620C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938660 | M400PDT620B | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | Diff. Pr. RUW-MUS, Metering Skid 400FT620B. | 939741 |  | M400PDI620B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938661 | M400PDT620C | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | Diff. Pr. RUW-MUS, Metering Skid 400FT620C. | 939742 | PRES_TX | M400PDI620C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938662 | M400FE772 | SENSOR, DIFFERENTIAL PRESSURE | FLOW METER 400-FT-772,CUSTODY METERING SYSTEM | 934855 | FL_MTR | M400FC772 | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938663 | M400PT772 | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX 400-FT-772,CUSTODY METERING SYSTEM | 934855 | PRES_TX | M400FC772 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT772-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/06/19 | MC-PM-007-Y1
938664 | M400PDT771A | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | PRESS. DIFFERENTIAL TX MUSSAFAH ALAIN P/L | 939747 |  | M400PDI771A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938665 | M400TT772 | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX SKID 400-FT-772,CUSTODY METERING SYSTEM | 939218 | TEMP_TX | M400TI772 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938666 | M400TE772 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP.ELEMENT 400-FT-772,CUSTODY METERING SYSTEM | 939218 | TEMP_ELE | M400TI772 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938670 | M400PT541A | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX NEPTHA/REFORM P/L, JET A1,CUSTODY METER | 938681 | PRES_TX | M400PI541A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938671 | M400PT541B | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX NEPTHA/REFORM P/L, JET A1,CUSTODY METER | 934849 | PRES_TX | M400PI541B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938672 | M400FE541A | METER, FLOW, MASS , 10" ANSI 300 LB RF FLANGE , 316 SS | FLOW METER NEPTHA/REFORM P/L, JET A1,CUSTODY METE | 938681 | FL_MTR | M400FC541A | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938674 | M400PDT541A | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 4-20MA , 10.5-42.4VDC , 1000 PS | D.P. TX NEPTHA/REFORM P/L, JET A1,CUSTODY METERIN | 939736 |  | M400PDI541A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938675 | M400PDT541B | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 4-20MA , 10.5-42.4VDC , 1000 PS | D.P. TX NEPTHA/REFORM P/L, JET A1,CUSTODY METERIN | 939737 |  | M400PDI541B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938676 | M400FE541B | METER, FLOW, MASS , 10" ANSI 300 LB RF FLANGE , 316 SS | FLOW METER NEPTHA/REFORM P/L, JET A1,CUSTODY METE | 934849 | FL_MTR | M400FC541B | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938677 | M400TT541A | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX NEPTHA/REFORM P/L, JET A1,CUSTODY METERIN | 939200 | TEMP_TX | M400TI541A | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939124 | M400TI303 | INDICATOR, TEMPERATURE | Temp. for ULG 95 Tank 400-T-112 |  |  | M400T112 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI303-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/05/19 | MC-PM-010-Y1
939125 | M400TI305 | INDICATOR, TEMPERATURE | Temp for ULG 95 Tank 400-T-113 |  |  | M400T113 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI305-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/05/19 | MC-PM-010-Y1
939126 | M400TI307 | INDICATOR, TEMPERATURE | Temp for ULG 95 Tank 400-T-114 |  |  | M400T117 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI307-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/05/19 | MC-PM-010-Y1
939127 | M400TI309 | INDICATOR, TEMPERATURE | Temp for ULG 95 Tank 400-T-115 |  |  | M400T115 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI309-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/05/19 | MC-PM-010-Y1
939128 | M400TI311 | INDICATOR, TEMPERATURE | Temp. for Gas Oil Tank 400-T-116 |  |  | M400T116 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI311-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/05/19 | MC-PM-010-Y1
939129 | M400TI313 | INDICATOR, TEMPERATURE | Temp. for Jet A1 Tank 400-T-117 |  |  | M400T117 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI313-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/05/19 | MC-PM-010-Y1
939130 | M400TI315 | INDICATOR, TEMPERATURE | Temp. for Jet A1 Tank 400-T-118 |  |  | M400T118 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI315-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/05/19 | MC-PM-010-Y1
939131 | M400TI317 | INDICATOR, TEMPERATURE | Temp. for Jet A1 Tank 400-T-119 |  |  | M400T119 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI317-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/05/19 | MC-PM-010-Y1
939132 | M400TI319 | INDICATOR, TEMPERATURE | Temp. for Jet A1 Tank 400-T-120 |  |  | M400T120 | 3 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TI319-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/05/19 | MC-PM-010-Y1
939133 | M400TI401 | INDICATOR, TEMPERATURE | Main E-MOTOR 'U' Winding For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI401-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/09/18 | MC-PM-010-Y1
939134 | M400TI402 | INDICATOR, TEMPERATURE | Main E-MOTOR 'U' Winding For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI402-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/09/18 | MC-PM-010-Y1
939135 | M400TI403 | INDICATOR, TEMPERATURE | Main E-MOTOR 'V' Winding For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI403-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/09/18 | MC-PM-010-Y1
939136 | M400TI403C | INDICATOR, TEMPERATURE | Lube Oil Heater Trip for 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI403C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/09/18 | MC-PM-010-Y1
939137 | M400TI404 | INDICATOR, TEMPERATURE | Main E-MOTOR 'V' Winding For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI404-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/09/18 | MC-PM-010-Y1
939138 | M400TI405 | INDICATOR, TEMPERATURE | Main E-MOTOR 'W' Winding For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI405-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/09/18 | MC-PM-010-Y1
939139 | M400TI406 | INDICATOR, TEMPERATURE | Main E-MOTOR 'W' Winding For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI406-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/09/18 | MC-PM-010-Y1
939140 | M400TI407A | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing NCE For Pump 400-P-016 | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI407A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/09/18 | MC-PM-010-Y1
939141 | M400TI407B | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing NCE For Pump 400-P-016 | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI407B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/09/18 | MC-PM-010-Y1
939142 | M400TI408A | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing CE For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI408A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/09/18 | MC-PM-010-Y1
939143 | M400TI408B | INDICATOR, TEMPERATURE | Main E-MOTOR Radial Bearing CE For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI408B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/10/18 | MC-PM-010-Y1
939144 | M400TI409A | INDICATOR, TEMPERATURE | Pump Radial Bearing D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI409A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/10/18 | MC-PM-010-Y1
939145 | M400TI409B | INDICATOR, TEMPERATURE | Pump Radial Bearing D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI409B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/10/18 | MC-PM-010-Y1
939146 | M400TI410A | INDICATOR, TEMPERATURE | Casing For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI410A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/10/18 | MC-PM-010-Y1
939147 | M400TI411A | INDICATOR, TEMPERATURE | Pump Radial Bearing N.D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI411A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/10/18 | MC-PM-010-Y1
939148 | M400TI411B | INDICATOR, TEMPERATURE | Pump Radial Bearing N.D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI411B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/10/18 | MC-PM-010-Y1
939149 | M400TI412A | INDICATOR, TEMPERATURE | Thrust Bearing D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI412A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/10/18 | MC-PM-010-Y1
939150 | M400TI412B | INDICATOR, TEMPERATURE | Thrust Bearing D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI412B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/10/18 | MC-PM-010-Y1
939151 | M400TI413A | INDICATOR, TEMPERATURE | Thrust Bearing N.D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI413A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/10/18 | MC-PM-010-Y1
939152 | M400TI413B | INDICATOR, TEMPERATURE | Thrust Bearing N.D.E. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI413B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/10/18 | MC-PM-010-Y1
939153 | M400TI414C | INDICATOR, TEMPERATURE | Lube Oil Header Temp. For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI414C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/10/18 | MC-PM-010-Y1
939154 | M400TI416 | INDICATOR, TEMPERATURE | Main E-MOTOR 'U' Winding For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI416-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/10/18 | MC-PM-010-Y1
939155 | M400TI417 | INDICATOR, TEMPERATURE | Main E-MOTOR 'U' Winding For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI417-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/10/18 | MC-PM-010-Y1
939156 | M400TI418 | INDICATOR, TEMPERATURE | Main E-MOTOR 'V' Winding For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI418-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/10/18 | MC-PM-010-Y1
939157 | M400TI418C | INDICATOR, TEMPERATURE | Main E-MOTOR 'U' Winding For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI418C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/10/18 | MC-PM-010-Y1
939269 | M400VI463Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing D.E. 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI463Y-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939270 | M400VI464X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing N.D.E. 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI464X-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939271 | M400VI464Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing N.D.E. 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI464Y-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
938996 | M400PSL833 | SWITCH, PRESSURE | Switch Pressure, M/L Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSL833-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 30/12/18 | MC-PM-009-M6
938997 | M400PSL834 | SWITCH, PRESSURE | Switch Pressure, Booster Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSL834-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 30/12/18 | MC-PM-009-M6
938998 | M400PT015A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | MP Booster pump 400-P-015A Seal Pr. | 933874 | PRES_TX | M400P015A | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT015A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/09/18 | MC-PM-007-Y1
938999 | M400PT015B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | MP Booster pump 400-P-015B Seal Pr. | 933875 | PRES_TX | M400P015B | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT015B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/09/18 | MC-PM-007-Y1
939000 | M400PT017A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Seal System Pressure (M400P017A) | 933876 | PRES_TX | M400P017A | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT017A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/11/18 | MC-PM-007-Y1
939001 | M400PT017B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Seal System Pressure (M400P017B) | 933877 | PRES_TX | M400P017B | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT017B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/11/18 | MC-PM-007-Y1
939002 | M400PT021A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | ULG 95/98 transfer pump 400-P-021ASeal Pr. tx. | 939766 | PRES_TX | M400PI021A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939003 | M400PT021B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | ULG 95/98 transfer pump 400-P-021BSeal Pr. tx. | 939767 | PRES_TX | M400PI021B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939004 | M400PT022A/1 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Seal System Pressure-DE (M400P022A) press, tx. | 939769 | PRES_TX | M400PI022A | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939005 | M400PT022A/2 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Seal System Pressure-NDE (M400P022A) press. tx. | 939769 | PRES_TX | M400PI022A | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939006 | M400PT022B/1 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Seal System Pressure-DE (M400P022A) press. tx. | 939770 | PRES_TX | M400PI022B | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939007 | M400PT022B/2 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Seal System Pressure-NDE (M400P022B) press. tx. | 939770 | PRES_TX | M400PI022B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939008 | M400PT024A | TRANSMITTER, PRESSURE, SMART, 4-20MA, 24V DC, 2 WIRE, 1/ | Slop transfer pump 400-P-024A Seal Pr. transmitter | 939771 | PRES_TX | M400PI024A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939009 | M400PT024B | TRANSMITTER, PRESSURE, SMART, 4-20MA, 24VDC, 2 WIRE, 1/ | Slop transfer pump 400-P-024B Seal Pr. transmitter | 939772 | PRES_TX | M400PI024B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939010 | M400PT075 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 10.5-30 VDC , 1/2" | Seal System Pressure (M400P075) | 933010 | PRES_TX | M400P075 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT075-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/02/19 | MC-PM-007-Y1
939011 | M400PT076 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20MA , 10.5-30 VDC , 1/2" | Seal System Pressure (M400P076) | 933011 | PRES_TX | M400P076 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT076-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/02/19 | MC-PM-007-Y1
939012 | M400PT651A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-10 BAR , 4-20mA , 24V DC, | Ruwais Mussafah MP P/L receiving end. |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT651A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/03/19 | MC-PM-007-Y1
939013 | M400PV929 | VALVE, CONTROL, GLOBE RECIPROCATING , 87 , A216 GR WCC , A564 GR630 , 17-4PH SS | Fire Water Systems Pump Discharge | 938973 | CNTR_VLV | M400PIC929 | 1 | CNTR_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939014 | M400PY536 | SWITCH, SELECTOR | Auto/ manual selection 400-PV-536 | 933027 |  | M400PV536 | 3 | PB_HS-MC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939015 | M400PY561 | SWITCH, SELECTOR | A/M selector switch 400-PV-561 | 933028 |  | M400PV561 | 3 | PB_HS-MC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939016 | M400PY670 | SWITCH, SELECTOR | Auto manual selection 400-PV-670 | 933029 |  | M400PV670 | 3 | PB_HS-MC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939017 | M400PY813 | SWITCH, SELECTOR | Auto/Manual Selector Switch (M400PV813) | 933030 |  | M400PV813 | 3 | PB_HS-MC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939018 | M400PY894 | SWITCH, SELECTOR | Auto/Manual selector switch 400-PV-894 | 933031 |  | M400PV894A | 3 | PB_HS-MC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939019 | M400QI301 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for ULG 95 Tank 400-T-111 |  | TNK_GUG | M400T111 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939020 | M400QI303 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for ULG 95 Tank 400-T-112 |  | TNK_GUG | M400T112 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939387 | U29PI644 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-15 | PR.TRANS.NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 |  | OPENLOOP | U2902L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI644-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/11/18 | MC-PM-007-Y1
939388 | U29PI645 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-15 | PR.TRANS.NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 |  | OPENLOOP | U2902L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI645-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/11/18 | MC-PM-007-Y1
939389 | U29PI646 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-15 | PR..NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 |  | OPENLOOP | U2902L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI646-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/11/18 | MC-PM-007-Y1
939390 | U29PI647 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-15 | PR.NAPHTHA REFORMATE/HSGO LINE-OUTLET PV686 |  | OPENLOOP | U2902L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI647-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/11/18 | MC-PM-007-Y1
939391 | U29PI648 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-15 | From 2902-L Scraper Launcher To SV Station -7 Pr. |  | OPENLOOP | U2902L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI648-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/11/18 | MC-PM-007-Y1
939408 | U29PI668 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP75-1BC1WB1HF1BU , 0-15 | PR.TRASMTR. 29-EOV-507 OUTLET |  | OPENLOOP | U2903L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI668-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/11/18 | MC-PM-007-Y1
939409 | U29PI669 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP75-1BC1WB1HF1BU , 0-15 | PR. 29-EOV-507 OUTLET |  | OPENLOOP | U2903L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI669-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/11/18 | MC-PM-007-Y1
939411 | U29PI670 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP75-1BC1WB1HF1BU , 0-15 | SRR Main Pumps 2937-JA/B/C to 2903-L/302-PL-002 |  | OPENLOOP | U2903L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI670-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/11/18 | MC-PM-007-Y1
939412 | U29PI671 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP75-1BC1WB1HF1BU , 0-15 | SRR Main Pumps 2937-JA/B/C to 2903-L/302-PL-002 Pr |  | OPENLOOP | U2903L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI671-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/11/18 | MC-PM-007-Y1
939413 | U29PI672 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP75-1BC1WB1HF1BU , 0-15 | PR. SCRAPER LAUNCHER 2903L- SV STATN-7 SRR | 933174 | OPENLOOP | U2903L | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29PI672-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/05/19 | MC-PM-007-Y1
938877 | M400MOV598 | ACTUATOR,ELECTRIC MOTOR, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 48RPM, 39 SEC, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68 | MOV FOR RUWAIS MUSSAFAH SRR PIPE LINE. |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938878 | M400LT416 | TRANSMITTER, LIQUID LEVEL, 4-20MA , 24VDC | LUBE OIL RESEVOIR (M400P016B) | 938741 | LVL_TX | M400LI416C | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938879 | M400PDT464 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , 1/2" NPT | LUBE OIL FILTER (M400P019) | 935830 | LVL_TX | M400P019 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDT464-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
938883 | M400TT429 | TRANSMITTER, TEMPERATURE, RTD , 0-100 DEG C , 4-20MADC , 24VDC , M20X1.5 , ALUM | LUBE OIL HEADER TEMP. M400P016B | 935827 | TEMP_TX | M400P016B | 1 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 5 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 1 | 0 | M400TT429-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/11/18 | MC-PM-010-Y1
938898 | M400VE418X | PROBE, VIBRATION , 8MM , 0.5 M | (M400P016B) MAIN MOTOR RADIAL BEARING D.E | 939257 | VIBRE_TX | M400VI418X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938899 | M400VE418Y | PROBE, VIBRATION , 8MM , 0.5 M | (M400P016B) MAIN MOTOR RADIAL BEARING D.E | 939258 | VIBRE_TX | M400VI418Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938900 | M400VE417X | PROBE, VIBRATION , 8MM , 0.5 M | MAIN MOTOR RADIAL BEARING D.E (M400P016B) | 939255 | VIBRE_TX | M400VI417X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938901 | M400VE417Y | PROBE, VIBRATION , 8MM , 0.5 M | (M400P016B) MAIN MOTOR RADIAL BEARING D.E | 939256 | VIBRE_TX | M400VI417Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938902 | M400VE419X | PROBE, VIBRATION , 8MM , 0.5 M | (M400P016B) MAIN MOTOR RADIAL BEARING N.D.E | 939259 | VIBRE_TX | M400VI419X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938903 | M400VE419Y | PROBE, VIBRATION , 8MM , 0.5 M | (M400P016B) MAIN MOTOR RADIAL BEARING N.D.E | 939260 | VIBRE_TX | M400VI419Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938904 | M400PT466A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-4 BAR , 4-20mA , 10.5-30 V | PR.TR. DISCHARGE LUBE OIL P (M400P019) | 939785 | PRES_TX | M400PI466C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938905 | M400PT466B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-4 BAR , 4-20mA , 10.5-30 V | PR.TR. DISCHARGE LUBE OIL P (M400P019) | 939785 | PRES_TX | M400PI466C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938906 | M400LT461 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 4-20MA , 24VDC , 3/4"NPT | LEVELTR. OIL RESEVOIR (M400P019) | 938816 | LVL_TX | M400LI461C | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938907 | M400ZE461A | PROBE, VIBRATION , 8MM , 0.5 M | Pump - Thrust Bearing - 1st "Z" Plane for M400P019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400ZE461A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
938908 | M400ZE461B | PROBE, VIBRATION , 8MM , 0.5 M | Pump - Thrust Bearing - 2ND "Z" Plane for M400P019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400ZE461B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939021 | M400QI305 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for ULG 95 Tank 400-T-113 |  | TNK_GUG | M400T113 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939022 | M400QI307 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for ULG 95 Tank 400-T-114 |  | TNK_GUG | M400T114 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939023 | M400QI309 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for ULG 95 Tank 400-T-115 |  | TNK_GUG | M400T115 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939024 | M400QI311 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for Gas Oil Tank 400-T-116 |  | TNK_GUG | M400T116 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939025 | M400QI313 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for Jet A1 Tank 400-T-117 |  | TNK_GUG | M400T117 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939026 | M400QI315 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for Jet A1 Tank 400-T-118 |  | TNK_GUG | M400T118 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939027 | M400QI317 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for Jet A1 Tank 400-T-119 |  | TNK_GUG | M400T119 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939028 | M400QI319 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | Level for Jet A1 Tank 400-T-120 |  | TNK_GUG | M400T120 | 1 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939029 | M400TE401 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'U' Winding For Pump 400-P-016A |  | TEMP_ELE | M400TI401 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939030 | M400TE402 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'U' Winding For Pump 400-P-016A |  | TEMP_ELE | M400TI402 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939031 | M400TE403 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'V' Winding For Pump 400-P-016A |  | TEMP_ELE | M400TI403 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939032 | M400TE403C | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Lube Oil Heater Tripped for 400-P-016A |  | TEMP_ELE | M400TI403C | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939033 | M400TE404 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'V' Winding For Pump 400-P-016A |  | TEMP_ELE | M400TI404 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939034 | M400TE405 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'W' Winding For Pump 400-P-016A |  | TEMP_ELE | M400TI405 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939035 | M400TE406 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'W' Winding For Pump 400-P-016A |  | TEMP_ELE | M400TI406 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939036 | M400TE407A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing NCE For Pump 400-P-016 |  | TEMP_ELE | M400TI407A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939037 | M400TE407B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing NCE For Pump 400-P-016 |  | TEMP_ELE | M400TI407B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939038 | M400TE408A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing CE For Pump 400-P-016A |  | TEMP_ELE | M400TI408A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278595 | PL312CCTV023 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278596 | PL312CCTV024 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278597 | PL312CCTV025 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278598 | PL312CCTV026 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278599 | PL312CCTV027 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278600 | PL312CCTV028 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278601 | PL312CCTV029 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278602 | PL312CCTV030 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278603 | PL312CCTV031 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278604 | PL312CCTV032 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278605 | PL312CCTV033 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278606 | PL312CCTV034 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278607 | PL312CCTV035 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278608 | PL312CCTV036 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278609 | PL312CCTV037 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278610 | PL312CCTV038 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278611 | PL312CCTV039 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278612 | PL312CCTV040 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278613 | PL312CCTV041 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278614 | PL312CCTV042 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278615 | PL312CCTV043 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278616 | PL312CCTV044 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278617 | PL312CCTV045 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
931209 | U51AT103 | DETECTOR, COMBUSTIBLE GAS , 8-30VDC, 4-20MA OUTPUT | GAS DETECTOR LPG PIG LAUNCHER AREA |  | FG_DET | U5101R01 | 1 | FG_DET | 623101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | U51AT103-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 09/08/18 | MFPS-PM02.M3
935095 | M400MCC001 | MOTOR,CONTROL CENTER, 415, FLOOR MOUNTED, 3 | 415V, 3ph+N,50Hz, 630A, LV SWITCHGEAR |  | MCC_SWBD | M400WWTP | 2 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935096 | M400PC001 | SWITCHGEAR, 4000, 415, FLOOR MOUNTED, 3, 4, YES, YES, 4000, 80 Ka, Back to Back, Air, 800 A / 2000 A, 176, 40 | 415V LV SWITCHGEAR AT S/S-400 MTERMINAL |  | SWBOARD | M400SUBSTN | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935097 | MQ600PC001 | SWITCHGEAR, 250, 415, FLOOR, 3, 4, 250, 25, SINGLE FRONT, Air, 52 | 415V, 3ph+N,50Hz, 250A, LV SWITCHGEAR |  | SWBOARD | MQ600MISC | 2 | MCC_SWBD | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936654 | M400PT551 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-12 KG/CM2, 0-70.3 KG/CM2 , | PRESS. TR. OUTLET LINE METERING SKID 400-FT-772 | 938969 | PRES_TX | M400PIC551 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936655 | M400PT553 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 15 , 4-20mA , 10.5-30 VD | PR.TR. ULG 98 LINE TO STORAGE TANK FROM 400-ME-003 | 939802 | PRES_TX | M400PI553 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936656 | M400PT554 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PR.TR. SUCTION LINE MAIN LINE PUMP 400-P-019 | 939799 | PRES_TX | M400PI554 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936657 | M400PT555 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 15 , 4-20mA , 24V DC, 2 | PR.TR. JET A1 LINE TO STORAGE TANK FROM 400-ME-001 | 939803 | PRES_TX | M400PI555 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936658 | M400PT556 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 150 , 4-20mA , 24V DC, 2 | PR.TR. DISCHARGE LINE MAIN LINE PUMP 400-P-019 | 939804 | PRES_TX | M400PI556 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936659 | M400PT557 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 150 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. AT INLET LINE OF 400-PV-561 | 939805 | PRES_TX | M400PI557 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936660 | M400PT558 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 150 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. OUTLET 400-PV-561 | 939806 | PRES_TX | M400PI558 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936661 | M400PT559 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 150 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. OUTLET PRESSURE 400-PV-561 | 939807 | PRES_TX | M400PI559 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936662 | M400PT560 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 150 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. OUTLET PRESSURE 400-PV-561 | 938869 | PRES_TX | M400PI560 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936663 | M400PT561 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. AT OUTLET LINE OF 400-PV-561 | 938869 | PRES_TX | M400PIC561 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936664 | M400PT565 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 15 , 4-20mA , 24V DC, 2 | PR.TR. ULG 95 LINE TO STORAGE TANK FROM 400-ME-002 | 939810 | PRES_TX | M400PI565 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936665 | M400PT566 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 BAR , 4-20MADC , 24V D | PRESS. TRANSMTR. SCRAPER RECEIVER SRR P/L | 939811 | PRES_TX | M400PI566 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936666 | M400PT571 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 24VDC, 2 WIRES , 2 | PR.TR. ISOLATION LINE OF SCRAPER RECEIVER SRR P/L | 939812 | PRES_TX | M400PI571 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936667 | M400PT576 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 24VDC, 2 WIRES , 2 | PRESS. TRANSMTR. SCRAPER LAUNCHER SRR P/L | 939813 | PRES_TX | M400PI576 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936668 | M400PT651 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24VDC, 2 | PR.TR. RUWAIS MUSSAFAH MP P/L RECEIVING END | 939816 | PRES_TX | M400PI651 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936669 | M400PT654 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | PR.TR. RUWAIS MUSSAFAH MP P/L SCRAPER RECEIVER ISO |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT654-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/03/19 | MC-PM-007-Y1
936670 | M400PT656 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. AT INLET LINE 400-PV-670 | 938970 | PRES_TX | M400PIC656 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936671 | M400PT658 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 25 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. OUTLET 400-PV-670 |  | PRES_TX | M400PRESS | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT658-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/03/19 | MC-PM-007-Y1
936672 | M400PT659 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 25 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. OUTLET 400-PV-670 |  | PRES_TX | M400PRESS | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT659-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/03/19 | MC-PM-007-Y1
936673 | M400PT660 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 25 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. OUTLET 400-PV-670 |  | PRES_TX | M400PRESS | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT660-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/03/19 | MC-PM-007-Y1
936675 | M400PT752 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PR.TR. JET A1 STORAGE TANK- BOOSTER PUMP 400P017 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT752-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/03/19 | MC-PM-007-Y1
936676 | M400PT754 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PR.TR. JET A1 STORAGE TANK-BOOSTER PUMP 400P017 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT754-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/03/19 | MC-PM-007-Y1
936677 | M400PT755 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1) - (+3) , 24V DC, 2 WIRE | PR.TR. SUCTION LINE BOOSTER PUMP 400-P-017A | 933876 | PRES_TX | M400P017A | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT755-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/11/18 | MC-PM-007-Y1
936678 | M400PT756 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1) - (+3) , 24V DC, 2 WIRE | PR.TR. SUCTION LINE BOOSTER PUMP 400-P-017B | 933877 | PRES_TX | M400P017B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT756-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/11/18 | MC-PM-007-Y1
936679 | M400PT760 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 12 , 4-20mA , 24V DC, 2 | PR.TR.O/L LINE OF FILTR COALESCER SEPARATR JET A1 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT760-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/03/19 | MC-PM-007-Y1
936680 | M400PT761 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-12 KG/CM2, 0-70.3 KG/CM2 , | PR.TR. DISCHARGE LINE BOOSTER PUMP 400-P-017A | 933876 | PRES_TX | M400P017A | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT761-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/11/18 | MC-PM-007-Y1
936681 | M400PT762 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-12 KG/CM2, 0-70.3 KG/CM2 , | PR.TR. DISCHARGE LINE BOOSTER PUMP 400-P-017B | 933877 | PRES_TX | M400P017B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT762-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/11/18 | MC-PM-007-Y1
936682 | M400PT801 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | Outlet line Pr. tx. from metering skid to ML pump. | 938971 | PRES_TX | M400PIC801 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936683 | M400PT804 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 10.5-30 VD | PR.TR. SUCTION LINE MAIN LINE PUMP 400-P-018A | 935828 | PRES_TX | M400P018A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT804-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/11/18 | MC-PM-007-Y1
936684 | M400PT807 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-50 MBAR , 4-20mA , 24V DC, | PR.TR. DISCHARGE LINE MAIN LINE PUMP 400-P-018A | 935828 | PRES_TX | M400P018A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT807-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/11/18 | MC-PM-007-Y1
936685 | M400PT808 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PR.TR. SUCTION LINE MAIN LINE PUMP 400-P-018B | 935829 | PRES_TX | M400P018B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT808-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/12/18 | MC-PM-007-Y1
936686 | M400PT811 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 50 , 4-20mA , 24V DC, 2 | PR.TR. DISCHARGE LINE MAIN LINE PUMP 400-P-018B | 935829 | PRES_TX | M400P018B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT811-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/12/18 | MC-PM-007-Y1
936687 | M400PT812 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 50 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. AT OUTLET LINE 400-PV-813 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT812-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/03/19 | MC-PM-007-Y1
936688 | M400PT813 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 25 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. AT INLET LINE OF 400-PV-813 | 938871 | PRES_TX | M400PIC813 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936689 | M400PT814 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 60 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. INLET 400-PV-801 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT814-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/03/19 | MC-PM-007-Y1
936690 | M400PT815 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 60 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. INLET 400-PV-801 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT815-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/03/19 | MC-PM-007-Y1
939097 | M400TE311 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. for Gas Oil Tank 400-T-116 | 939128 | TANKGAUG | M400TI311 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939098 | M400TE313 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. for Jet A1 Tank 400-T-117 | 939129 | TANKGAUG | M400TI313 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939099 | M400TE315 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. for Jet A1 Tank 400-T-118 | 939130 | TANKGAUG | M400TI315 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939100 | M400TE317 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. for Jet A1 Tank 400-T-119 | 939131 | TANKGAUG | M400TI317 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939101 | M400TE319 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. for Jet A1 Tank 400-T-120 | 939132 | TANKGAUG | M400TI319 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939102 | M400TE502 | SKIN ELEMENT, TEMP. THERMORESISTANCE , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. Between ADR 10" & Ruwais 10" Naphtha P/L | 939198 | TEMP_ELE | M400TI502 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939103 | M400TE501 | SKIN ELEMENT, TEMP. THERMORESISTANCE , SINGLE RTD | SKIN Temp. ELEMENT FOR ADR 10" N/R P/L | 939197 | TEMP_ELE | M400TI501 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939104 | M400TE503 | SKIN ELEMENT, TEMP. THERMORESISTANCE , SINGLE RTD | PIG Indication for To/From Ruwais 10" Naphtha P/L | 939199 | TEMP_ELE | M400TI503 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939105 | M400TE550 | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD | Temp. Between ADR 10" & Ruwais 10" Naphtha P/L | 939202 | TEMP_ELE | M400TI550 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939106 | M400TE552 | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD | Temp. outlet of 400-PV-561 | 939203 | TEMP_ELE | M400TI552 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939107 | M400TE566 | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD | Temp.ADR Ruwais SRR P/L to Scr. Rec. 400-PLR-006 | 939204 | TEMP_ELE | M400TI566 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939108 | M400TE567 | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD | Temp. ADR Ruwais SRR P/L to Ruwais Recpt. Terminal | 939205 | TEMP_ELE | M400TI567 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939109 | M400TE568 | SKIN ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | SKIN Temp. ADR Ruwais SRR P/L from 400-PLR-007 | 939206 | TEMP_ELE | M400TI568 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939110 | M400TE651 | SKIN ELEMENT, TEMP. THERMORESISTANCE , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. Rws-Mussafah MP P/L to Scr. Recvr. 400-PLR-0 | 939210 | TEMP_ELE | M400TI651 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939111 | M400TE652 | ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | Ruwais Mussafah MP P/L scr. reciver isolation lin | 939211 | TEMP_ELE | M400TI652 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939112 | M400TE751 | ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | Temp. at Jet A1 P/L from storage tanks | 939214 | TEMP_ELE | M400TI751 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939113 | M400TE752 | ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | Temp.at Suct. side of 400-G-017B in Jet A1 P/L | 939215 | TEMP_ELE | M400TI752 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939114 | M400TE771A | ELEMENT, TEMPERATURE, THERMORESISTANCE , DOUBLE RTD, 3-WIRE , 0-200 DEG C , PLAT | Temp. at 400-FT-771A in Mussafah - ADIA JET A1 P/L | 939216 | TEMP_ELE | M400TI771A | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939115 | M400TE771B | ELEMENT, TEMPERATURE, THERMORESISTANCE , DOUBLE RTD, 3-WIRE , 0-200 DEG C , PLAT | Temp. at 400-FT-771A in Mussafah - ADIA JET A1 P/L | 939217 | TEMP_ELE | M400TI771B | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939116 | M400TE801 | ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | Temp. at Muss. Adia Jet A1 P/L from 400-P-018A/B | 939219 | TEMP_ELE | M400TI801 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939117 | M400TE802 | SKIN ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | TEMP.ELE. MUSSAFAH TERMINAL FOR JET A1 P/L TO ADIA | 939220 | TEMP_ELE | M400TI802 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939118 | M400TE851 | ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | Temp. Mussafah-Al Ain MP Tie-In P/L to 400-P-015A/ | 939221 | TEMP_ELE | M400TI851 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939119 | M400TE861A | ELEMENT, TEMPERATURE, THERMORESISTANCE , DOUBLE RTD, 3-WIRE , 0-200 DEG C , PLAT | Mussafah - TIE In MP P/L | 939222 | TEMP_ELE | M400TI861A | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939120 | M400TE861B | ELEMENT, TEMPERATURE, THERMORESISTANCE , DOUBLE RTD, 3-WIRE , 0-200 DEG C , PLAT | Mussafah - TIE In MP P/L (TEMPERATURE ELEMENT) | 939223 | TEMP_ELE | M400TI861B | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939121 | M400TE881 | ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | Temp. at Mussafah-Al Ain MP Tie-In P/L | 939224 | TEMP_ELE | M400TI881 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939122 | M400TE882 | SKIN ELEMENT, TEMP.THERMORESISTANCE , SINGLE RTD | Temp. at Muss.-Al Ain MP Tie-In P/L to tie in poin | 939225 | TEMP_ELE | M400TI882 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939123 | M400TI301 | INDICATOR, TEMPERATURE | Temp. for ULG 95 Tank 400-T-111 |  |  | M400T111 | 3 | TANKGAUG | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M400TI301-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/05/19 | MC-PM-010-Y1
EMV57530 | M50MOV126B | ACTUATOR, ELECTRIC MOTOR, WATER , REMOTE CONTROL , MAR 100 / 19.2 , 415 V, 3 , 5 | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-103. |  | MOV | M10T103 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV126B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/09/18 | ME-PM-002-M6
EMV57533 | M10MOV571 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-104 |  | MOV | M10T104 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935679 | SMLPGTP34 | CP TEST POINT | TEST POINT # 34 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935680 | SMLPGTP35 | CP TEST POINT | TEST POINT # 35 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935485 | SALAINTP37 |  | TEST POINT # 37 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935486 | SALAINTP38 |  | TEST POINT # 38 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935487 | SALAINTP39 |  | TEST POINT # 39 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936691 | M400PT816 | TRANSMITTER, PRESSURE, SMART, 0-60, 4-20mA, 24V DC, 2 | PRESS. TRANSMTR. INLET 400-PV-801 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT816-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/03/19 | MC-PM-007-Y1
936692 | M400PT818 | TRANSMITTER, PRESSURE, SMART, 0-50, 4-20mA, 24V DC, 2 | PR.TR. MUSSAFAH ADIA JET A1 P/L SCRAPER LAUNCHER |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT818-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/03/19 | MC-PM-007-Y1
936693 | M400PT819 | TRANSMITTER, PRESSURE, SMART, 0-50, 4-20mA, 24V DC, 2 | PR.TR. MUSSAFAH TERMINAL FOR JET A1 P/L TO ADIA |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT819-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/03/19 | MC-PM-007-Y1
936694 | M400PT852 | TRANSMITTER, PRESSURE, SMART, (-1)-(+3) KG/CM2, 4-20MA | PR.TR. MUSSAFAH AL AIN MP TIE IN COMMON LINE |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT852-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/03/19 | MC-PM-007-Y1
936695 | M400PT853 | TRANSMITTER, PRESSURE, SMART (-1)-(+3), 24V DC, 2 WIRE | PR.TR. SUCTION LINE BOOSTER PUMP 400-P-015A | 933874 | PRES_TX | M400P015A | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PT853-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/09/18 | MC-PM-007-Y1
936696 | M400PT854 | TRANSMITTER, PRESSURE, SMART, (-1)-(+3), 24V DC, 2 WIRE | PR.TR. SUCTION LINE BOOSTER PUMP 400-P-015B | 933875 | PRES_TX | M400P015B | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PT854-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/09/18 | MC-PM-007-Y1
936697 | M400PT857 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 15 , 4-20mA , 24V DC, 2 | PR.TR. DISCHARGE LINE BOOSER PUMP 400-P-015A | 933874 | PRES_TX | M400P015A | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PT857-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/09/18 | MC-PM-007-Y1
936698 | M400PT858 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 15 , 4-20mA , 24V DC, 2 | PR.TR. DISCHARGE LINE BOOSER PUMP 400P015B. | 933875 | PRES_TX | M400P015B | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PT858-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/09/18 | MC-PM-007-Y1
936699 | M400PT860 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PR.TR. OUTLET LINE OF METERING SKID 400-FT-861 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT860-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/03/19 | MC-PM-007-Y1
936700 | M400PT881 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PR.TR. OUTLET LINE OF METERING SKID 400-FT-861 | 938972 | PRES_TX | M400PIC881 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936701 | M400PT884 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PR.TR. SUCTION LINE MP MAIN LINE PUMP 400-P-016A | 935826 | PRES_TX | M400P016A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT884-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/09/18 | MC-PM-007-Y1
936702 | M400PT886 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-200 BAR , 4-20mA , 10.5-30 | PR.TR. DISCHARGE LINE MAIN LINE PUMP 400-P-016A | 935826 | PRES_TX | M400P016A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT886-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/09/18 | MC-PM-007-Y1
936703 | MREDUNDANT | TO BE DELETED | Redundant Location (Mussafah Terminal) |  | PRES_TX | MTERMINAL | 4 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936704 | M400PT887 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-200 BAR , 4-20mA , 10.5-30 | PR.TR. SUCTION LINE MAIN LINE PUMP 400-P-016B | 935827 | PRES_TX | M400P016B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT887-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/10/18 | MC-PM-007-Y1
936705 | M400PT893 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 200 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. OUTLET LINE OF 400-PV-894 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT893-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/03/19 | MC-PM-007-Y1
936706 | M400PT894 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 200 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. INLET LINE OF 400-PV-894 | 938872 | PRES_TX | M400PIC894 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936707 | M400PT895 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 200 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. INLET 400-PV-894 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT895-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/04/19 | MC-PM-007-Y1
936708 | M400PT896 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 200 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. INLET 400-PV-894 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT896-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/04/19 | MC-PM-007-Y1
936709 | M400PT897 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 200 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. INLET 400-PV-894 |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT897-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/04/19 | MC-PM-007-Y1
936710 | M400PT899 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 200 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. MUSSAFAH AL AIN MP PIPELINE |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT899-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/03/19 | MC-PM-007-Y1
936711 | M400PT900 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 200 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. MUSSAFAH AL AIN MP PIPELINE | 939815 | PRES_TX | M400PI900 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936712 | M400PT928 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 15 , 4-20mA , 24V DC, 2 | PR.TR. O/L CORROSION INHIBITOR AT MUSSAFAH MP P/L |  | PRES_TX | M400PRESS | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PT928-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/04/19 | MC-PM-007-Y1
936713 | M400PT929 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 25 , 4-20mA , 24V DC, 2 | PR.TR. FOR COMMON HEADER TO FIRE WATER PUMP | 938973 | PRES_TX | M400PIC929 | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936714 | M400PT930 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. INSTRUMENT AIR SUPPLY PRESSURE |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT930-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/04/19 | MC-PM-007-Y1
936715 | M400PT950 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PRESS. TRANSMTR. PUMP 400-P-204A/B DISCHARGE |  | PRES_TX | M400PRESS | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT950-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/04/19 | MC-PM-007-Y1
936716 | M400TT501 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0-100 DEG C , 4-20mA W | TEMP.TR. SCRAPER RECEIVER NAPHTHA REFORMATE P/L | 939197 | TEMP_TX | M400TI501 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936717 | M400TT502 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP.TRANSMTR. NAPHTHA REFORMATE P/L | 939198 | TEMP_TX | M400TI502 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936718 | M400TT503 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. SCRAPER RECEIVER NAPHTHA REFORMATE P/L | 939199 | TEMP_TX | M400TI503 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936719 | M400TT550 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP. TRANSMTR. OFF SPEC JET A1 LINE TO 40-P-020 | 939202 | TEMP_TX | M400TI550 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936720 | M400TT552 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP. TRANSMTR. OUTLET OF 400-PV-561 | 939203 | TEMP_TX | M400TI552 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936721 | M400TT566 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SCRAPER RECEIVER SRR P/L | 939204 | TEMP_TX | M400TI566 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936722 | M400TT567 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -120 , 4-20mA WITH H | TEMP.TR.ISOLATION LINE OF SCRAPER RECEIVER SRR P/L | 939205 | TEMP_TX | M400TI567 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936723 | M400TT568 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. ADR RUWAIS SRR P/L FROM 400-PLR | 939206 | TEMP_TX | M400TI568 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936724 | M400TT651 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP. TR. RUWAIS-MUSSAFAH MP P/L TO SCRAPER RECVR | 939210 | TEMP_TX | M400TI651 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936725 | M400TT652 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP.TR.RUWAIS MUSSAFAH MP P/L SCRAPER RECEIVER | 939211 | TEMP_TX | M400TI652 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936726 | M400TT751 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0-100 DEG C , 4-20mA W | TEMP.TR. JET A1 STORAGE TANK-BOOSTER PUMP 400P017 | 939214 | TEMP_TX | M400TI751 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936727 | M400TT752 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0-100 DEG C , 4-20mA W | TEMP.TR.JET A1 STORAGE TANK-BOOSTER PUMP 400-P-017 | 939215 | TEMP_TX | M400TI752 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936728 | M400TT801 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP.TR. MUSSFAH ADIA JET A1 P/L SCRAPER LAUNCHER | 939219 | TEMP_TX | M400TI801 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936729 | M400TT802 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. MUSSAFAH TERMINAL FOR JET A1 P/L TO ADIA | 939220 | TEMP_TX | M400TI802 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936730 | M400TT851 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP.TR. MUSSAFAH-AL AIN MP TIE IN P/L TO 400P017A | 939221 | TEMP_TX | M400TI851 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936731 | M400TT881 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP. TR. AT MUSSAFAH-AL AIN MP TIE IN P/L | 939224 | TEMP_TX | M400TI881 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936732 | M400TT882 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. MUSSAFAH AL AIN MP TIE IN PIPELINE | 939225 | TEMP_TX | M400TI882 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936733 | MQ600PT001 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 160 , 4-20mA , 24V DC, 2 | PRESS.TR. AT MUSSAFAH-AL AIN MULTIPRODUCT TIE-IN |  | TRANS | MQ600PRESS | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600PT001-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-007-M6
936734 | MQ600PT006 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 160 , 4-20mA , 24V DC, 2 | PRESS.TR. AT MUSSAFAH-AL AIN MULTIPRODUCT TIE-IN |  | TRANS | MQ600PRESS | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600PT006-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-007-M6
936735 | MQ600PT007 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 160 , 4-20mA , 24V DC, 2 | PRESS.TR. AT MUSSAFAH-AL AIN MULTIPRODUCT TIE-IN |  | TRANS | MQ600PRESS | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600PT007-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-007-M6
936736 | MQ600PT016 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 160 , 4-20mA , 24V DC, 2 | PR.TR.EXISTING ADR-ALAIN MULTIPRODUCT TO 600PLR015 |  | TRANS | MQ600PRESS | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600PT016-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-007-M6
936737 | MQ600TT001 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 60 , 4-20mA WITH H | TEMP.TR. MULTIPRODUCT TIE-IN P/L I/L TO 600PLR013 |  |  | MQ600TEMP | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600TT001-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-010-M6
937600 | M400T301 | ADDITIVE MIXING TANK FOR PPD | ADDITIVE MIXING TANK FOR PPD |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 50 | 5 | 5 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937601 | M400T302 | LUBRICITY IMPROVER TANK IRP MUSSAFAH TERMINAL. | LUBRICITY IMPROVER TANK IRP MUSSAFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 50 | 5 | 5 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937604 | M400BD001A | BUSBAR, ELECTRIC | BUSBAR,ELECTRIC |  | BREAKER | M400SCB | 3 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937605 | M400BD001B | BUS | BUSBAR,ELECTRIC |  | BREAKER | M400SCB | 2 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937608 | PL300SPS001 | SYSTEM | SOLAR POWER SYSTEMS FOR SV-1 |  |  | PL300SVS1 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SPS001-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 09/08/18 | ME-PM-010-M2
937609 | PL300SPS002 | SYSTEM | SOLAR POWER SYSTEMS FOR SV-2 |  |  | PL300SVS2 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SPS002-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 12/10/18 | ME-PM-010-M2
937610 | PL300SPS003 | SYSTEM | SOLAR POWER SYSTEMS FOR SV-3 |  |  | PL300SVS3 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SPS003-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 08/09/18 | ME-PM-010-M2
937611 | PL300SPS004 | SYSTEM | SOLAR POWER SYSTEMS FOR SV-4 |  |  | PL300SVS4 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SPS004-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 26/08/18 | ME-PM-010-M2
937612 | PL300SPS005 | SYSTEM | SOLAR POWER SYSTEMS FOR SV-5 |  |  | PL300SVS5 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SPS005-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 15/10/18 | ME-PM-010-M2
937613 | PL300SPS006 | SYSTEM | SOLAR POWER SYSTEMS FOR SV-6 |  |  | PL300SVS6 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SPS006-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 19/09/18 | ME-PM-010-M2
937614 | PL300SPS007 | SYSTEM | SOLAR POWER SYSTEMS FOR SV-7 |  |  | PL300SVS7 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SPS007-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 21/09/18 | ME-PM-010-M2
937615 | M400CCTV001 | CAMERA, CLOSED CIRCUIT TELEVISION | CLOSED CIRCUIT TELEVISION SYSTEM ABOVE TANK T-118 |  | CCTVSEC | M400CCTV | 1 | CCTVSEC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400CCTV001-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
937616 | M400CCTV002 | CAMERA, CLOSED CIRCUIT TELEVISION | CLOSED CIRCUIT TELEVISION SYSTEM ABOVE TANK T-112 |  | CCTV_SYS | M400CCTV | 1 | CCTVSEC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400CCTV002-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
937617 | M400CCTV003 | CAMERA, CLOSED CIRCUIT TELEVISION | CLOSED CIRCUIT TELEVISION SYSTEM ABOVE TANK T-106 |  | CCTV_SYS | M400CCTV | 1 | CCTVSEC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400CCTV003-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
937618 | M400CCTV004 | CAMERA, CLOSED CIRCUIT TELEVISION | CLOSED CIRCUIT TELEVISION SYSTEM ABOVE TANK T-103 |  | CCTV_SYS | M400CCTV | 1 | CCTVSEC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400CCTV004-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
937621 | M400ME006 | CLEAN AGENT SYSTEM CONTROL ROOM- MUSSAFAH | CLEAN AGENT SYSTEM CONTROL ROOM- MUSSAFAH |  |  | M400SYS | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937622 | M400ME007 | CLEAN AGENT SYSTEM CONTROL ROOM- MUSSAFAH | CLEAN AGENT SYSTEM CONTROL ROOM- MUSSAFAH |  |  | M400SYS | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937623 | MQ600ME002 | SYSTEM | CLEAN AGENT SYSTEM ELECTRICAL BUILDING MAQTA |  |  | MQ600SYS | 1 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937628 | M400T80 | TANK STORAGE | CORROSION INHIBTOR DOSING TANK |  | TK | M400CINJ | 1 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937629 | M400V175 | SUMP TANK SRR PIPELINE | SUMP TANK SRR PIPELINE |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 10 | 10 | 10 | 5 | 5 | 5 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937630 | M400V176 | SUMP TANK MULTIPRODUCT PIPELINE | SUMP TANK MULTIPRODUCT PIPELINE |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 10 | 10 | 10 | 5 | 5 | 5 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937631 | MQ600D77 | TANK STORAGE | SUMP TANK-MP PIPELINE |  | TK | MQ600VESSEL | 3 | TK | 616101-310600 | IRPMAQTA | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937634 | M400ME030A | PPD INJECTION SKID 16" HEADER | PPD INJECTION SKID 16" HEADER |  | PACKAGE | M400CINJ | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937635 | M400ME030B | PPD INJECTION SKID 10" HEADER | PPD INJECTION SKID 10" HEADER |  | PACKAGE | M400CINJ | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937636 | M400ME031A | LUBRICITY IMPROVER ADDITIVE DOSING PACKAGE | LUBRICITY IMPROVER ADDITIVE DOSING PACKAGE |  | PACKAGE | M400CINJ | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937637 | M400ME031B | SYSTEM | LUBRICITY INJECTION SKID 10" HEADER |  |  | M400CINJ | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937638 | M400P301A | PPD INJECTION PUMP 16" HEADER | PPD INJECTION PUMP 16" HEADER |  | PURE | M400CINJ | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P301A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/08/18 | MM-PM-008-M6
937639 | M400P301B | PPD INJECTION PUMP 16" HEADER | PPD INJECTION PUMP 16" HEADER |  | PURE | M400CINJ | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P301B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 04/09/18 | MM-PM-008-M6
937640 | M400P302A | PPD INJECTION PUMP 10" HEADER | PPD INJECTION PUMP 10" HEADER |  |  | M400CINJ | 3 | PUMPS | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 5 | 10 | 10 | 6.3979 | Non Critical | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P302A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 08/08/18 | MM-PM-008-M6
937641 | M400P302B | PPD INJECTION PUMP 10" HEADER | PPD INJECTION PUMP 10" HEADER |  | PURE | M400CINJ | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P302B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/09/18 | MM-PM-008-M6
937642 | M400P303A | LUBRICITY IMPROVER INJECTION PUMP 16" HEADER | LUBRICITY IMPROVER INJECTION PUMP 16" HEADER |  | PURE | M400CINJ | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | M400P303A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 09/08/18 | MM-PM-009-M6
937643 | M400P303B | LUBRICITY IMPROVER INJECTING PUMP, IRP MUSSAFAH TERM. | LUBRICITY IMPROVER INJECTING PUMP, IRP MUSSAFAH TERM. |  | PURE | M400T302 | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | M400P303B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/09/18 | MM-PM-009-M6
937644 | M400P304A | LUBRICITY INJECTION PUMP 10" HEADER | LUBRICITY INJECTION PUMP 10" HEADER |  | PURE | M400CINJ | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | M400P304A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 10/08/18 | MM-PM-009-M6
937645 | M400P304B | LUBRICITY INJECTION PUMP 10" HEADER | LUBRICITY INJECTION PUMP 10" HEADER |  | PURE | M400CINJ | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | M400P304B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/09/18 | MM-PM-009-M6
XXX935694 | SMLPGCP1IJ1 | INSULATING JOINT | INSULATING JOINT 1 AT KM 0 (MUSSAFAH LPG P.L.) |  |  | SMLPGPIPE | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935695 | SMLPGCP1IJ2 | INSULATING JOINT | INSULATING JOINT 2 AT KM 16.9 (MUSSAFAH LPG P.L.) |  |  | SMLPGPIPE | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59037 | M10PT012 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , EEx ib | HYDRO STATICPRESSURE TRANSMITTER(TOP)FOR TANKT-101 | TNK56513 | PRES_TX | M10T101 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59058 | M10PT021 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , BASEEFA | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-102 | TNK56531 | PRES_TX | M10T102 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59059 | M10PT022 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , EEx ib | HYDRO STATICPRESSURE TRANSMITTER(TOP)FOR TANKT-102 | TNK56531 | PRES_TX | M10T102 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59080 | M10PT031 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , FLANGE , M20 X 1.5 , BASEE | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-103 | TNK56547 | PRES_TX | M10T103 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59081 | M10PT032 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , EEx ib | HYDRO STATICPRESSURE TRANSMITTER(TOP)FOR TANKT-103 | TNK56547 | PRES_TX | M10T103 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59101 | M10PT041 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA+HART PROTOCOL , 24VDC , FLANGE , M20 X | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-104 | TNK56565 | PRES_TX | M10T104 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59121 | M10PT051 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , FLANGE , M20 X 1.5 , EEx i | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-105 | TNK56585 | PRES_TX | M10T105 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59141 | M10PT061 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , FLANGE , M20 X 1.5 , EEx i | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-106 | TNK56600 | PRES_TX | M10T106 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59161 | M10PT071 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , FLANGE , M20 ISO , EEx ib | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-107 | TNK56616 | PRES_TX | M10T107 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59182 | M10PT081 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , FLANGE , M20 ISO , EEx ib | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-108 | TNK56634 | PRES_TX | M10T108 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59183 | M10PT082 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , EEx ib | HYDRO STATICPRESSURE TRANSMITTER(TOP)FOR TANKT-108 | TNK56634 | PRES_TX | M10T108 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59199 | M10PT091 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , FLANGE , M20 X 1.5 , EEx i | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-109 | TNK56645 | PRES_TX | M10T109 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59200 | M10PT092 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , EEx ib | HYDRO STATICPRESSURE TRANSMITTER(TOP)FOR TANKT-109 | TNK56645 | PRES_TX | M10T109 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59217 | M10PT101 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , FLANGE , M20 X 1.5 , EEx i | HYDRO STATIC PRESS. TRANSMITTER BOTOM TANK T-110 | TNK56656 | PRES_TX | M10T110 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP59218 | M10PT102 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , FLANGE , M20 X 1.5 , EEx ib | HYDRO STATICPRESSURE TRANSMITTER(TOP)FOR TANKT-110 | TNK56656 | PRES_TX | M10T110 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 1 | 1 | 1 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932791 | M400BD08511051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932792 | M400BD08611051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932793 | M400BD08711051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932794 | M400BD08811051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934054 | M400P022A | PUMP, CENTRIFUGAL, HORIZONTAL BB2 , GAS OIL INTER TANK TRANSFER PUMPS , CENTERL | GAS OIL INTERNAL TANK TRANSFER PUMP-A. |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P022AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/12/18 | MM-PM-006-M6
934055 | M400P022B | PUMP, CENTRIFUGAL, HORIZONTAL BB2 , GAS OIL INTER TANK TRANSFER PUMPS , CENTERL | GAS OIL INTERNAL TANK TRANSFER PUMP-B. |  | PUCE | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P022BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-006-M6
934056 | M400P024A | PUMP, CENTRIFUGAL, VERTICAL, VS 6 , SLOP TRANSFER PUMPS , SEPARATE MOUNTING PLAT | SLOP TRANSFER PUMP-A. |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P024A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/12/18 | MM-PM-007-M6
934057 | M400P024B | PUMP, CENTRIFUGAL, VERTICAL, VS 6 , SLOP TRANSFER PUMPS , SEPARATE MOUNTING PLAT | SLOP TRANSFER PUMPS |  | PUCE | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P024B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-007-M6
934060 | M400P080A | PUMP, DIAPHRAGM, Diaphragm , 1/2" , 5 M3/Hr , 300# | CORROSION INHIBITOR CHEMICAL DOSING PUMP A. |  | PURE | M400PUMP | 1 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P080A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/12/18 | MM-PM-009-M6
934061 | M400P080B | PUMP, DIAPHRAGM, Diaphragm , 1/2" , 5 M3/Hr , 300# | CORROSION INHIBITOR CHEMICAL DOSING PUMP B. |  | PURE | M400PUMP | 1 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P080B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-009-M6
934062 | M20PI165 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Suction Pressure at 20-P-227A | 934049 |  | M20P227A | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934063 | M20PI166 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Suction Pressure at 20-P-227B | 934050 |  | M20P227B | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934064 | M20PI167 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , 1/2" MNPT , SS 316L , 316L S | Discharge Pressure at 20-P-227A | 934049 |  | M20P227A | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934065 | M20PI168 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Pressure at 20-P-227B | 934050 |  | M20P227B | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934066 | M20PI169 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pressure at Jet A1 Tanker Off-loading Area |  |  | M20PRESS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939770 | M400PI022B | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-25 | Seal System Pressure-DE (M400P022B) | 934055 |  | M400P022B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI022B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/02/19 | MC-PM-007-Y1
939771 | M400PI024A | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-25 | Slop transfer pump 400-P-024A Seal Pr. | 934056 |  | M400P024A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI024A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/02/19 | MC-PM-007-Y1
939772 | M400PI024B | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-25 | Slop transfer pump 400-P-024B Seal Pr. | 934057 |  | M400P024B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI024B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/02/19 | MC-PM-007-Y1
939773 | M400PI204A | LOOP, PRESSURE INDICATOR INSTRUMEN, 24 VDC V, 4-20 MA | Potable Water Pump 400-P-204A Seal Pr. | 933006 |  | M400P204A | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI204A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/02/19 | MC-PM-007-Y1
939774 | M400PI204B | LOOP, PRESSURE INDICATOR INSTRUMEN, 24 VDC V, 4-20 MA | Potable Water Pump 400-P-204B Seal Pr. | 933007 |  | M400P204B | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI204B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/02/19 | MC-PM-007-Y1
939775 | M400PT204A | TRANSMITTER, PRESSURE, SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Potable Water Pump 400-P-204a Seal Pr. transmitter | 939773 | PRES_TX | M400PI204A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939776 | M400PT204B | TRANSMITTER, PRESSURE, SMART , 4-20MA , 24V DC, 2 WIRE , 1/ | Potable Water Pump 400-P-204B Seal Pr. transmitter | 939774 | PRES_TX | M400PI204B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939777 | M400PI401C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EJA 530 , 0-10 KG/CM2 , 24 VDC | Lube Oil Pump A - Discharge Press. For 400-P-016A | 935826 | OPENLOOP | M400P016A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI401C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/09/18 | MC-PM-007-Y1
939778 | M400PI402C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EJA 530 , 0-10 KG/CM2 , 24 VDC | Lube Oil Pump B - Discharge Press. For 400-P-016A | 935826 | OPENLOOP | M400P016A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI402C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/09/18 | MC-PM-007-Y1
939779 | M400PI406C | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-2 | Lube Oil Header - Press. For 400-P-016A | 935826 | OPENLOOP | M400P016A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI406C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/09/18 | MC-PM-007-Y1
939780 | M400PI416C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EBS7N-07DN/KU2/D4/M15 , 0-10 KG | Lube Oil Pump A - Discharge Press. For 400-P-016B | 935827 | OPENLOOP | M400P016B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI416C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/10/18 | MC-PM-007-Y1
939781 | M400PT406 | TRANSMITTER, PRESSURE, GAGE , 4-20MADC , 10.5-30 VDC , 1/2" NPT , M20 X 1.5 , IP | Lube Oil Header - Press. For 400-P-016A |  | PRES_TX | M400PI406C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939782 | M400PI417C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EJA 530EBS7N-07DN/KU2/D4/M15 , | Lube Oil Pump B - Discharge Press. For 400-P-016B | 935827 | OPENLOOP | M400P016B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI417C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/10/18 | MC-PM-007-Y1
939783 | M400PI461C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EJA 530 , 0-10 KG/CM2 , 24VDC V | Lube Oil Pump A - Discharge Press. For 400-P-019 | 935830 | OPENLOOP | M400P019 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI461C-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
939784 | M400PI462C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EJA 530 , 0-10 KG/CM2 , 24VDC V | Lube Oil Pump B - Discharge Press. For 400-P-019 | 935830 | OPENLOOP | M400P019 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI462C-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
939785 | M400PI466C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EJA 530 , 0-4 KG/CM2 , 24VDC V, | Lube Oil Header - Press. For 400-P-019 | 935830 | OPENLOOP | M400P019 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI466C-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
932607 | M30L006 | COALESCER | FILTER COALESCER SEPARATOR-JET A1 LOADING BAY-H |  |  | M30FILTER | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932608 | M30L007 | COALESCER | FILTER COALESCER SEPARATOR-JET A1 LOADING BAY-J |  |  | M30FILTER | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932609 | M400L003A | 16 COALESCER / 8 SEPATRATOR ELEMENTS FILTER. | COALESCER FILTER & SEPARATOR RUWAIS-MUSSAFAH. |  |  | M400FILTER | 3 | CLN_FLTR | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 50 | 10 | 1 | 10 | 5.699 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932610 | M400L003B | 16 COALESCER/ 8 SEPATRATOR ELEMENTS FILTER. | COALESCER FILTER & SEPARATOR RUWAIS-MUSSAFAH. |  |  | M400FILTER | 3 | CLN_FLTR | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 50 | 10 | 1 | 10 | 5.699 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932611 | M400L004A | 8 FILTER COALESCER 4 SEPARATOR - MUSSAFAH-ADIA JET A1 PIPE LINE. | COALESCER FILTER & SEPARATOR - MUSSAFAH-ADIA JET A1 PIPE LINE |  | VESSEL | M400FILTER | 3 | VESSEL | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 50 | 10 | 50 | 1 | 10 | 7.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933807 | M400P55191051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933808 | M400P61511051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933809 | M400P61611051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933810 | M400P61711051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933811 | M400P61811051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933812 | M400P61911051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933813 | M400P628151051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933814 | M400P629151051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933815 | M400P63011051XV | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933816 | M400P63111051XV | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933817 | M400P75411051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933818 | M400P75511051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933819 | M400P80331051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933820 | M400P80431051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933821 | M400P85611051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933822 | M400P85711051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933823 | M400P881151051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933824 | M400P883151051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933842 | M400ASP001 | ANNUNCIATOR | ANNUNCIATOR |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933957 | M400VA34GL091 | GLOBE VALVE | GLOBE VALVE, 3/4" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933958 | M400VA34GL191 | GLOBE VALVE | GLOBE VALVE, 3/4" 1500 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933959 | M400VA4CH391 | VALVE, CHECK, SWING , 4" , 150 LB , 425 DEG C MAX , RF FLANGE , ASTM A216 GR WCB | CHECK VALVE, 4" 150 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933960 | M400VA4CH491 | VALVE CHECK | CHECK VALVE, 4" 300 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933961 | M400VA4GA391 | GATE VALVE | GATE VALVE, 4" 150 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933962 | M400VA4GL391 | GLOBE VALVE | GLOBE VALVE, 4" 150 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933963 | M400VA6CH392 | VALVE CHECK | CHECK VALVE, WAFER DOUBLE DISC, 6" 150 LB |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933964 | M400VA6GL391 | GLOBE VALVE | GLOBE VALVE, 6" 150 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933965 | M400VA8CH392 | VALVE CHECK | CHECK VALVE, WAFER DOUBLE DISC, 8" 150 LB |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933966 | M400VA8GL391 | GLOBE VALVE | GLOBE VALVE, 8" 150 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933967 | M400VA8GL491 | GLOBE VALVE | GLOBE VALVE, 8" 300 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933968 | M400VA8GL591 | GLOBE VALVE | GLOBE VALVE,8" 600 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933969 | M400VA8GL691 | GLOBE VALVE | GLOBE VALVE, 8" 900 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933970 | MQ600VA1GA091 | GATE VALVE | GATE VALVE, 1" 800 LB, SW |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933971 | MQ600VA112GA091 | GATE VALVE | GATE VALVE, 1-1/2" 800 LB, SW |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933972 | MQ600VA12GA092 | GATE VALVE | GATE VALVE, 1/2" 800 LB, SW+NPT |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933973 | MQ600VA12GA191 | GATE VALVE | GATE VALVE, 1/2" 1500 LB, SW |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933974 | MQ600VA2GA691 | GATE VALVE | GATE VALVE, 2" 900 LB, RF FLG |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933975 | MQ600VA2GL391 | GLOBE VALVE | GLOBE VALVE, 2" 150 LB, RF FLG |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933976 | MQ600VA2GL691 | GLOBE VALVE | GLOBE VALVE, 2" 900 LB, RF FLG |  | VALVE | MQ600VALVE | 3 | VALVE | 617101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969133171 | M10LZHH073 | SWITCH,LEVEL FLOAT, 2", 316 SS, BASEEFA EXD IIC T6 | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-107 | TNK56616 | LVL_SWT | M10T107 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZHH073-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/10/18 | MC-PM-025-M6
933286 | U29MOV327 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F 14, OIL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR STATION (NAPHTHA / REF / JET A1 / HSGO, 10" CL 600) |  | MOV | U2902L | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | U29MOV327-SE1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
933759 | AT800MOV406 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" CL 300, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV AT ADIA JET A1, 10" CL 300 |  | MOV | AT800MOTOR | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 |  | AT800MOV406-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933760 | AT800MOV407 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 72RPM, 15 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV AT ADIA,,JET A1, 10" X 8" CL 300 |  | MOV | AT800MOTOR | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | AT800MOV407-ME1 | INACTIVE |  | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933761 | AA13FI11518100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933762 | AA13FI12118100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933763 | AA13FI12518100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933764 | AA13FI13018100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933765 | AA13FW11718100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933766 | AA13FW11818100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933767 | AA13FW12018100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933768 | AA13FW12418100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933769 | AA13FW12618100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933770 | AA13FW12718100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933771 | AA13FW13018100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933772 | AA13FW15518100XV | STRAINER | FIRE WATER STRAINER |  |  | AA13FILTER | 3 | CLN_FLTR | 617101-310510 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933787 | M400CH92613091XV | STRAINER | CHEMICAL(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933788 | M400CH92713091XV | STRAINER | CHEMICAL(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933789 | M400DW00617050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933790 | M400DW00717050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933791 | M400DW00817050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933792 | M400DW00917050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933793 | M400DW01017050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933794 | M400DW02917050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933795 | M400DW99517050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933796 | M400DW99617050N | STRAINER | POTABLE WATER STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933797 | M400FW10618100XN | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933798 | M400FW10718100XN | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933799 | M400FW10818100XN | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933800 | M400FW15018100XV | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933801 | M400FW15118100XV | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933802 | M400FW15218100XV | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933803 | M400FW15318100XV | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933804 | M400FW15418100XV | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933805 | M400FW15518100XV | STRAINER | FIRE WATER STRAINER |  |  | M400FILTER | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933806 | M400P54811051ZS | STRAINER | HC(L) STRAINER |  |  | M400FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132034 | PL300BATT002B | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V | BATTERY BANK-B =38 Nos FOR SV-2. |  | BATTERY | PL300BAT002 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933470 | M400MOV156 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-022B DISCHARGE (GAS OIL, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV156-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/12/18 | ME-PM-002-M6
933471 | M400MOV181 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-119 OUTLET SHELL (JET A1, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV181-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933472 | M400MOV182 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-119 OUTLET ISOLATION VALVE (JET A1, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV182-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/09/18 | ME-PM-002-M6
933473 | M400MOV183 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-119 TO LOADING PUMP 227A/B/C (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV183-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/01/19 | ME-PM-002-M6
933474 | M400MOV184 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-119 OUTLET HEADER (JET A1, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV184-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/10/18 | ME-PM-002-M6
933475 | M400MOV185 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ18F10B4, IP68, 203Nm | MOV FOR T-119 OUTLET HEADER (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV185-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/01/19 | ME-PM-002-M6
933476 | M400MOV186 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 12 SEC, 6" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-119 INLET HEADER (JET A1, 6" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV186-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933477 | M400MOV187 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-119 INLET HEADER (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV187-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/09/18 | ME-PM-002-M6
933478 | M400MOV188 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-119 INLET ISOLATION (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV188-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/09/18 | ME-PM-002-M6
933479 | M400MOV189 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 54 SEC, 20" X 18" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-119 INLET SHELL (JET A1, 20" X 18" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV189-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/04/19 | ME-PM-002-M6
933480 | M400MOV190 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-120 OUTLET SHELL (JET A1, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV190-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/10/18 | ME-PM-002-M6
933481 | M400MOV191 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 18" X 16" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-120 OUTLET ISOLATION (JET A1, 18" X 16" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV191-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
XXX935669 | SMLPGTP24 | CP TEST POINT | TEST POINT # 24 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935682 | SMLPGTP37 | CP TEST POINT | TEST POINT # 37 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935683 | SMLPGTP38 | CP TEST POINT | TEST POINT # 38 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935684 | SMLPGTP39 | CP TEST POINT | TEST POINT # 39 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935557 | SALAINTP97 |  | TEST POINT # 97 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935558 | SALAINTP98 |  | TEST POINT # 98 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935559 | SALAINTP99 |  | TEST POINT # 99 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935574 | SADIATP5 |  | TEST POINT# 5 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935575 | SADIATP6 |  | TEST POINT# 6 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935576 | SADIATP7 |  | TEST POINT# 7 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932643 | PL300VA2BA591 | VALVE, BALL, 2" X 1-1/2" , 600 # , Flanged,RF , ASTM A 216 WCB , Trunnion Mounte | BALL VALVE 2"X1-1/2" RB 600RF TRUNNION MOUNT |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932644 | PL300VA4BA591 | VALVE, BALL, 4" X 3" , 600 # , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ba | BALL VALVE 4"X3" RB 600RF TRUNNION MOUNT GEAR OPR |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932645 | PL300VA4BA691 | VALVE, BALL, 4" X 3" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Bal | BALL VALVE 4"X3" RB 900RF TRUNNION MOUNT GEAR OPR |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932646 | PL300VA8BA591 | VALVE, BALL, 8" X 6" , 600 # , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ba | BALL VALVE 8"X6" RB 600RF TRUNNION MOUNT GEAR OPR |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932647 | M400VA1BA391 | VALVE, BALL, 1" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 1" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932648 | M400VA1BA394 | VALVE, BALL, 1" , 150 # , Flanged , RF , ASTM A 351 Gr. CF8M , 0.5"to6" Floating | BALL VALVE 1" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932649 | M400VA1BA398 | VALVE, BALL, 1" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 1" FB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932650 | M400VA12BA391 | VALVE, BALL, 1/2" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" | BALL VALVE 1/2" RB 150RF |  | VALVE | M400VALVE | 4 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Low | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932651 | M400VA12BA394 | VALVE, BALL, 1/2" , 150 # , Flanged , RF , ASTM A 351 Gr. CF8M , 0.5"to6" Floati | BALL VALVE 1/2" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932652 | M400VA10BA391 | VALVE, BALL, 10" X 8" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; | BALL VALVE 10"X8" RB 150RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932653 | M400VA10BA491 | VALVE, BALL, 10" X 8" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floatin | BALL VALVE 10"X8"RB 300RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932654 | M400VA10BA591 | VALVE, BALL, 10" X 8" , 600 # , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted B | BALL VALVE 10"X8" RB 600RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932655 | M400VA10BA691 | VALVE, BALL, 10" X 8" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ba | BALL VALVE 10"X8" RB 900RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932656 | M400VA10BA791 | VALVE, BALL, 10" X 8" , 1500# , Butt Weld , ASTM A 216 WCB , Trunnion Mounted Ba | BALL VALVE 10"X8"RB 1500RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932657 | M400VA12BA391 | VALVE, BALL, 12" X 10" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating | BALL VALVE 1/2" RB 150RF |  | VALVE | M400VALVE | 4 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Low | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932658 | M400VA12BA691 | VALVE, BALL, 12" X 10" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted B | BALL VALVE 12"X10"RB 900RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932659 | M400VA14BA391 | VALVE, BALL, 14" X 10" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating | BALL VALVE 14"X10"RB 150RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932660 | M400VA16BA391 | VALVE, BALL, 16" X 12" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating | BALL VALVE 16"X12"RB 150RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932661 | M400VA16BA491 | VALVE, BALL, 16" X 12" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floati | BALL VALVE 16"X12"RB 300RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932662 | M400VA16BA691 | VALVE, BALL, 16" X 12" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted B | BALL VALVE 16"X12"RB 900RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932663 | M400VA18BA392 | VALVE, BALL, 18" X 14" , 150 # , Flanged , RF , ASTM A 216 WCB , Trunnion Mounte | BALL VALVE 18"X14"RB 150RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932664 | M400VA2BA391 | VALVE, BALL, 2" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 2" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932665 | M400VA2BA393 | VALVE, BALL, 2" , 150 # , Flanged , RF , ASTM A 216 WCB , Floating Ball Valves , | BALL VALVE 2" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932666 | M400VA2BA394 | VALVE, BALL, 2" , 150 # , Flanged , RF , ASTM A 351 Gr. CF8M , 0.5"to6" Floating | BALL VALVE 2" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932667 | M400VA2BA398 | VALVE, BALL, 2" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 2" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932668 | M400VA2BA491 | VALVE, BALL, 2" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating ; 8" | BALL VALVE 2" RB 300RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932669 | M400VA2BA591 | VALVE, BALL, 2" X 1-1/2" , 600 # , Flanged,RF , ASTM A 216 WCB , Trunnion Mounte | BALL VALVE 2"X1-1/2"RB 600RF TRUNNION MOUNT |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932670 | M400VA2BA691 | VALVE, BALL, 2" X 1-1/2" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted | BALL VALVE 2"X1-1/2"RB 900RF TRUNNION MOUNT |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932671 | M400VA2BA791 | VALVE, BALL, 2" X 1-1/2" , 1500# , Butt Weld , ASTM A 216 WCB , Trunnion Mounted | BALL VALVE 2"X1-1/2"RB 1500 BW TRUNNION MOUNT |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932672 | M400VA3BA391 | VALVE, BALL, 3" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 3" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932673 | M400VA3BA398 | VALVE, BALL, 3" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 3" RB 150RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932674 | M400VA3BA491 | VALVE, BALL, 3" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating ; 8" | BALL VALVE 3" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932675 | M400VA3BA691 | VALVE, BALL, 3" X 2" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Bal | BALL VALVE 3"X2" RB 900RF TRUNNION MOUNT |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932676 | M400VA4BA391 | VALVE, BALL, 4" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 4" RB 150 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932677 | M400VA4BA394 | VALVE, BALL, 4" , 150 # , Flanged , RF , ASTM A 351 Gr. CF8M , 0.5"to6" Floating | BALL VALVE 4" RB 150 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932678 | M400VA4BA398 | VALVE, BALL, 4" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 4" FB 150 FF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932679 | M400VA4BA491 | VALVE, BALL, 4" , 300 LB , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating ; 8 | BALL VALVE 4" RB 300 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932680 | M400VA4BA591 | VALVE, BALL, 4" X 3" , 600 # , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ba | BALL VALVE 4"X3" RB 600RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932681 | M400VA4BA691 | VALVE, BALL, 4" X 3" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Bal | BALL VALVE 4"X3" RB 900RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932682 | M400VA6BA391 | VALVE, BALL, 6" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 6" RB 150 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932683 | M400VA6BA394 | VALVE, BALL, 6" , 150 # , Flanged , RF , ASTM A 351 Gr. CF8M , 0.5"to6" Floating | BALL VALVE 6" RB 150 RF |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932684 | M400VA6BA398 | VALVE, BALL, 6" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 6" FB 150 FF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932685 | M400VA6BA691 | VALVE, BALL, 6" X 4" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Bal | BALL VALVE 6"X4"RB 900RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932686 | M400VA8BA391 | VALVE, BALL, 8" X 6" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; | BALL VALVE 8"X6"RB 150RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932687 | M400VA8BA491 | VALVE, BALL, 8" X 6" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating | BALL VALVE 8"X6"RB 300 RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932688 | M400VA8BA591 | VALVE, BALL, 8" X 6" , 600 # , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ba | BALL VALVE 8"X6"RB 600RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932689 | M400VA8BA691 | VALVE, BALL, 8" X 6" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Bal | BALL VALVE 8"X6"RB 900RF TRUNNION MOUNT GEAR OPR |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932690 | MQ600VA2BA491 | VALVE, BALL, 2" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating ; 8" | BALL VALVE 2" RB 300 RF |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932691 | MQ600VA2BA691 | VALVE, BALL, 2" X 1-1/2" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted | BALL VALVE 2"X1-1/2"RB 900 RF TRUNNION MOUNT |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932692 | MQ600VA3BA391 | VALVE, BALL, 3" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 3" RB 150 RF |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932693 | MQ600VA3BA691 | VALVE, BALL, 3" X 2" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Bal | BALL VALVE 3"X2"RB 900 RF TRUNNION MOUNT |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932694 | MQ600VA4BA391 | VALVE, BALL, 4" , 150# , Flanged RF , ASTM A 216 WCB , 0.5"to6" Floating ; 8" to | BALL VALVE 4" RB 150 RF |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932695 | MQ600VA4BA393 | VALVE, BALL, 4" , 150 # , Flanged , RF , ASTM A 216 WCB , Floating Ball Valves , | BALL VALVE 4" FB 150 RF |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932696 | MQ600VA4BA691 | VALVE, BALL, 4" X 3" , 900# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Bal | BALL VALVE 4"X3" RB 900 RF TRUNNION MOUNTED |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933311 | U29MOV352 | ACTUATOR,ELECTRIC MOTOR, SRR / GO, 94, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 34 SEC, 12" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80EP, IQ25F14B4, IP68, 203Nm | MOV FOR PIG LAUNCHER (SRR / GO, 12" CL 600) |  | MOV | U2903L | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | U29MOV352-SE1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/02/19 | ME-PM-002-M6
933312 | U29MOV353 | ACTUATOR,ELECTRIC MOTOR, SRR / HSGO, 94, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 34 SEC, 12" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ25F14B4, IP68, 203Nm | MOV FOR STATION (SRR / GO, 12" CL 600 WITH STEM EXTENSION) |  | MOV | U2903L | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | U29MOV353-SE1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/09/18 | ME-PM-002-M6
969275155 | M410GLV21273001 | 0.5" Globe Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Plug Disc | 0.5" Globe Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Plug Disc |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275156 | M410GLV21273002 | 2" Globe Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Plug Disc | 2" Globe Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Plug Disc |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275157 | M410MOV115 | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269932 | CONTHNDV | M410MOV | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV115-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275158 | M410MOV125 | Valve, Ball. 20", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269933 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV125-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/06/19 | ME-PM-002-M6
969275159 | M410MOV161A | Valve, Ball. 18", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269934 | CONTHNDV | M410P001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV161A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275160 | M410MOV161B | Valve, Ball. 18", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269935 | CONTHNDV | M410P001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV161B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275161 | M410MOV162A | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269936 | CONTHNDV | M410P001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV162A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275162 | M410MOV162B | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269937 | CONTHNDV | M410P001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV162B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275163 | M410MOV163A | Valve, Ball. 20", 200#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269938 | CONTHNDV | M410P005A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV163A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275164 | M410MOV163B | Valve, Ball. 20", 200#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269939 | CONTHNDV | M410P005B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV163B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275165 | M410MOV163C | Valve, Ball. 20", 200#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269940 | CONTHNDV | M410P005C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV163C-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275166 | M410MOV164A | Valve, Ball. 16", 160#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269941 | CONTHNDV | M410P005A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV164A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275167 | M410MOV164B | Valve, Ball. 16", 160#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269942 | CONTHNDV | M410P005B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV164B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275168 | M410MOV164C | Valve, Ball. 16", 160#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269943 | CONTHNDV | M410P005C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV164C-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275169 | M410MOV184 | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269944 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV184-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275170 | M410MOV190 | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269945 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV190-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275171 | M410MOV203AA | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269946 | CONTHNDV | M410FT203A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV203AA-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969275172 | M410MOV203AB | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269947 | CONTHNDV | M410FT203A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275173 | M410MOV203BA | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269948 | CONTHNDV | M410FT203B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275174 | M410MOV203BB | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269949 | CONTHNDV | M410FT203B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275175 | M410MOV206AA | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269950 | CONTHNDV | M410FT206A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275176 | M410MOV206AB | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269951 | CONTHNDV | M410FT206A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275177 | M410MOV206BA | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269952 | CONTHNDV | M410FT206B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275178 | M410MOV206BB | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269953 | CONTHNDV | M410FT206B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275179 | M410MOV209AA | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269954 | CONTHNDV | M410FT209A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275180 | M410MOV209AB | Valve, Ball. 10", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269955 | CONTHNDV | M410FT209A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275181 | M410MOV209BA | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269956 | CONTHNDV | M410FT209B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275182 | M410MOV209BB | Valve, Ball. 10", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269957 | CONTHNDV | M410FT209B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275183 | M410MOV211AA | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269958 | CONTHNDV | M410FT211A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275184 | M410MOV211AB | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269959 | CONTHNDV | M410FT211A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275185 | M410MOV211BA | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269960 | CONTHNDV | M410FT211B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275186 | M410MOV211BB | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269961 | CONTHNDV | M410FT211B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275187 | M410MOV218 | Valve, Ball. 18", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269962 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275188 | M410MOV219 | Valve, Ball. 18", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269963 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 4 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275189 | M410MOV222A | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269964 | CONTHNDV | M410P002A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275190 | M410MOV222B | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269965 | CONTHNDV | M410P002B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275191 | M410MOV223A | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269966 | CONTHNDV | M410P002A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275192 | M410MOV223B | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269967 | CONTHNDV | M410P002B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275193 | M410MOV229 | Valve, Ball. 12", 1500#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269968 | CONTHNDV | M410L008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275194 | M410MOV230 | Valve, Ball. 12", 1500#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269969 | CONTHNDV | M410L008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275195 | M410MOV2301A | Valve, Ball. 12", 1500#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269970 | CONTHNDV | M410P023A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275196 | M410MOV2301B | Valve, Ball. 12", 1500#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269971 | CONTHNDV | M410P023B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275197 | M410MOV2301C | Valve, Ball. 12", 1500#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269972 | CONTHNDV | M410P023C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275198 | M410MOV2302A | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269973 | CONTHNDV | M410P023A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275199 | M410MOV2302B | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269974 | CONTHNDV | M410P023B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275200 | M410MOV2302C | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269975 | CONTHNDV | M410P023C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275201 | M410MOV231 | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269976 | CONTHNDV | M410L008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275487 | PL312PG002BA | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275488 | PL312PG002BB | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275489 | PL312PG003 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275490 | PL312PG004 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275491 | PL312PG007 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275492 | PL312PG008 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275493 | PL312PG009 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275494 | PL312PG010 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275495 | PL312PG013 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275496 | PL312PG014 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275497 | PL312PG30304C | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275498 | PL312PG31201A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275499 | PL312PG31201B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275500 | PL312PG31202A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275501 | PL312PG31202B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275502 | PL312PG31203A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275503 | PL312PG31203B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275504 | PL312PG31204A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275505 | PL312PG31204B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275506 | PL312PG31204C | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275507 | PL312PG31205A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275508 | PL312PG31205B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275509 | PL312PG31206A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275510 | PL312PG31206B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275511 | PL312PG31301A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275512 | PL312PG31301B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275513 | PL312PG31302A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275514 | PL312PG31302B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275515 | PL312PG31303A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275516 | PL312PG31303B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275517 | PL312PG31304A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275518 | PL312PG31304B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275519 | PL312PG31304C | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275520 | PL312PG31305A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275521 | PL312PG31305B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275522 | PL312PG31306A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275523 | PL312PG31306B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275524 | PL312PLR001 | Scraper LAUNCHER ULG PIPLINE | Scraper LAUNCHER ULG PIPLINE |  | PIPING | PL312MISC | 3 | PIPING | 0 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Non Critical | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275525 | PL312PLR002 | Scraper LAUNCHER GAS OIL PIPLINE | Scraper LAUNCHER GAS OIL PIPLINE |  | PIPING | PL312MISC | 3 | PIPING | 0 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Non Critical | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275526 | PL312PT001A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275527 | PL312PT001B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275528 | PL312PT002A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275529 | PL312PT002B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275530 | PL312PT005 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275531 | PL312PT006 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275532 | PL312PT011 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275533 | PL312PT012 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275534 | PL312PT31201A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969133390 | M400GAP001 | PANEL,FIRE ALARM, TYCO, GAS DETECTION, TYCO, OPTICAL/PHOTO, TYCO, HEAT DETECTION | GAS ALARM PANEL MCR |  | F&G_PNL | MMCR | 1 | GASDETEC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132814 | M400P213A | PUMP, CENTRIFUGAL | RECIRCULATION PUMP - A |  | PUCE | M400WWTPPUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P213A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/12/18 | MM-PM-018-M6
969132815 | M400P213B | PUMP, CENTRIFUGAL | RECIRCULATION PUMP - B |  | PUCE | M400WWTPPUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P213B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 08/12/18 | MM-PM-018-M6
969132816 | M400P214A | PUMP, SUBMERSIBLE | FEED PUMP A - CHAIN II |  | PUCE | M400WWTPPUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P214A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-016-M6
969132817 | M400P214B | PUMP, SUBMERSIBLE | FEED PUMP A - CHAIN II |  | PUCE | M400WWTPPUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P214B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/12/18 | MM-PM-016-M6
969132818 | M400P215A | PUMP, SCREW | EVACUATION PUMP - A |  | PUSC | M400WWTPPUMP | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P215A-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 10/07/19 | MM-PM-015-Y1
969132819 | M400P215B | PUMP, SCREW | EVACUATION PUMP - B |  | PUSC | M400WWTPPUMP | 2 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P215B-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 11/07/19 | MM-PM-015-Y1
969132820 | M400P216A | PUMP, SCREW | FEED PUMP A TO STRIPPER |  | PUSC | M400WWTPPUMP | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P216A-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 15/05/19 | MM-PM-015-Y1
969132821 | M400P216B | PUMP, SCREW | FEED PUMP B TO STRIPPER |  | PUSC | M400WWTPPUMP | 2 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P216B-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 16/05/19 | MM-PM-015-Y1
969132822 | M400P217A | PUMP, CENTRIFUGAL | FEED PUMP A TO AC FILTER |  | PUCE | M400WWTPPUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P217A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/12/18 | MM-PM-016-M6
969132823 | M400P217B | PUMP, CENTRIFUGAL | FEED PUMP B TO AC FILTER |  | PUMPS | M400WWTPPUMP | 2 | PUMPS | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 5 | 5 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400P217B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 13/12/18 | MM-PM-016-M6
969130833 | M400MP083A | MOTOR,ELECTRIC, CHEMICAL DOSING PUMP, 0.37 KW, 50 HZ, 415 V, M3GP 80MA 4B5, 6205 2ZC3/6204 2ZC3, 1421 RPM, 3, 0.9 AMP | CHEMICAL DOSING PUMP'A' BLUE DYE INJECTION PUMP 'A' |  | MOTOR | M400P083A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP083A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/01/19 | ME-PM-014-M6
969130839 | M400MP305 | MOTOR,ELECTRIC, PPD TRANSFER PUMP, 5.5 KW, 50 HZ, 415 V, 132SMB 2B3, 6208C3/6208C3, 2911 RPM, 3, 10.1 AMP | MOTOR FOR PPD TRANSFER PUMP |  | MOTOR | M400P305 | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP305-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/09/18 | ME-PM-014-M6
969130840 | M400MP306 | MOTOR,ELECTRIC, LUBRICITY TRANSFER PUMP, 4 KW, 50 HZ, 415 V, 112SMB 2B3, 6206 2Z C3/6206 2Z C3, 2906 RPM, 3, 7.1 AMP | MOTOR FOR LUBRICITY TRANSFER PUMP |  | MOTOR | M400T302 | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP306-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 22/10/18 | ME-PM-014-M6
969130946 | U29TCP001 | CATHODIC PROTECTION, C.P. FOR BURRIED PIPELINES, 4.8 KVA, OIL COOLED, ADVANCE ELECTRONIC SYSTEM, OILAES IRP-TRU-OC-10V-100A, 240 VOLT, 50 HZ, 1, 10 VOLT, 100 AMPERES, ONAN, BS148, 250 LITERS, 29SWB29/3,INCOMER-1, 4AF3, YES | CATHODIC PROTECTION RECTIFIER / TRANSFORMER UNIT FOR BURRIED PIPELINES |  | CATHPRO | U2903L | 1 | CATHPRO | 623101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | U29TCP001-SE1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/11/18 | ME-PM-008-M6
969131612 | M400XAS005 | HORN, SOUNDER, 24VDC, YES | SOUNDER-AUDIBLE HAZARD ALARM AT FIRE & SAFETY BUILDING ENTRANCE |  | LIGHT | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131613 | M400XAS201 | HORN, SOUNDER, 24VDC, YES | FIRE WARNING SIREN AT MAIN LINE PUMP AREA |  | LIGHT | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131614 | M400XAS202 | HORN, SOUNDER, 24VDC, YES | FIRE WARNING SIREN AT MAIN LINE PUMP AREA |  | LIGHT | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131615 | M400XAS206 | HORN, SOUNDER, 24VDC, YES | FIRE WARNING SIREN AT TANK FARM AREA |  | LIGHT | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131616 | M400XAS207 | HORN, SOUNDER, 24VDC, YES | FIRE WARNING SIREN AT TANK FARM AREA |  | LIGHT | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131617 | M400XAS208 | HORN, SOUNDER, 24VDC, YES | FIRE WARNING SIREN AT TANK FARM AREA |  | LIGHT | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131618 | M400XAS210 | HORN, SOUNDER, 24VDC, YES | FIRE WARNING SIREN AT SCRAPPER AREA |  | LIGHT | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131619 | M400XAC001 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT HVAC ROOM-PLCR |  | PB_HS-MC | M400FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC001-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 24/09/18 | MFPS-PM07.M3
969131620 | M400XAC002 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT ENTRANCE - PLCR. |  | PB_HS-MC | M400FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC002-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 24/09/18 | MFPS-PM07.M3
969131621 | M400XAC003 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT HVAC ROOM-PLCR |  | PB_HS-MC | M400FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC003-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 24/09/18 | MFPS-PM07.M3
969131640 | M400XAC041 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT WEST SIDE OF WAREHOUSE |  | PB_HS-MC | M400FACP005 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC041-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 23/10/18 | MFPS-PM07.M3
969131660 | M400XAL001 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT RACK ROOM-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131667 | M400XAL007 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT LOBBY-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131668 | M400XAL008 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT CORRIDOR-PLCR |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131676 | M400XAL030 | ALARM, FIRE, 24VDC, AUDIBLE & VISUAL, RED | AUDIO VISUAL INDICATOR AT CO2 &N2 ROOM OF FIRE STATION BUILDING |  | ALARMANC | M400FACP003 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131745 | M400XFB005 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK NO. T-103 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131746 | M400XFB011 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK T-104 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131749 | M400XFB022 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK NO. T-107 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131786 | M400XMC003 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-102 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC003-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131787 | M400XMC004 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-102 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC004-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
IPS59239 | M10L100 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR FUTURE TANK |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59240 | M10L101 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK101 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59241 | M10L102 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK102 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59242 | M10L103 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK103 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59243 | M10L104 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK104 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59244 | M10L105 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK105 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59245 | M10L106 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK106 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59246 | M10L107 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK107 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59247 | M10L108 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK108 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932730 | AT800VA10BA491 | VALVE, BALL, 10" X 8" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floatin | BALL VALVE 10"X8"RB 300RF TRUNNION MOUNT GEAR OPR |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932731 | AT800VA2BA491 | VALVE, BALL, 2" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating ; 8" | BALL VALVE 2" RB 300 RF |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932732 | AT800VA4BA398 | VALVE, BALL, 4" , 150# , Flanged,RF , ASTM A 216 WCB , Trunnion Mounted Ball Val | BALL VALVE 4" FB 150 FF |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932733 | AT800VA4BA491 | VALVE, BALL, 4" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating ; 8" | BALL VALVE 4" RB 300 RF |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932734 | AT800VA8BA491 | VALVE, BALL, 8" X 6" , 300 # , Flanged , RF , ASTM A 216 WCB , 2" to 6" Floating | BALL VALVE 8"X6"RB 300RF TRUNNION MOUNT GEAR OPR |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935256 | M10OGV102 | OUTLET GATE VALVE - 16" | OUTLET GATE VALVE - 16" FOR TANK T -102 |  | VALVE | M10TANKS | 3 | VALVE | 617101-310600 | MTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935259 | M10VRV012A | VALVE, SAFETY RELIEF, FIG 121 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935260 | M10VRV012B | VALVE, SAFETY RELIEF, FIG 121 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935261 | M10VRV012C | VALVE, SAFETY RELIEF, FIG 301 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935262 | M10VRV012D | VALVE, SAFETY RELIEF, FIG 121 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935263 | M10VRV013A | VALVE, SAFETY RELIEF, FIG 121 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-103 |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935264 | M10VRV013B | VALVE, SAFETY RELIEF, FIG 121 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-103 |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935265 | M10VRV013C | VALVE, SAFETY RELIEF, FIG 301 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-103. |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935266 | M10VRV013D | VALVE, SAFETY RELIEF, FIG 121 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUME RELIEF VALVE FOR TANK T-103. |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935275 | M10NRVO101 | OUTLET NON-RETURN VALVE -16" | OUTLET NON-RETURN VALVE -16" FOR TANK T - 101 |  | VALCH | M10T101 | 3 | VALCH | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935442 | SALAINCP1GB1 |  | GROUND BED (C.P.STATION- 1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935443 | SALAINCP1RMU1 |  | CP REMOTE MONITORING UNIT(C.P STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935444 | SALAINCP1IJ2 |  | INSULATION JOINT 2 AT KM 0.75 (C.P.S.# 1 AT KM3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132601 | M400MP205B | MOTOR,ELECTRIC, EFFLUENT OILY WATER PUMP, IP55, 18.5 KW, 50 HZ, 415 V, S1, Exn A II T3, 180 MLB, DE-6310/C3 , NDE-6309/C3, VERTICAL, 3, STAR, 34 AMP, F, II T3, 214 KG KG | MOTOR FOR OILY EFFLUENT PUMP-B |  | MOTOR | M400P205B | 1 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MP205B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
XXX935467 | SALAINTP19 |  | TEST POINT # 19 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935468 | SALAINTP20 |  | TEST POINT # 20 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935565 | SALAINTP105 |  | TEST POINT # 105 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935567 | SALAINCP4GB1 |  | GROUND BED (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935568 | SALAINCP4RMU1 |  | CP REMOTE MONITORING UNIT(C.P.STATION-4 ATKM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INZ59026 | M10QIA303 | METER, ANALYSER , PANEL MOUNT | COLOUR METER PANEL1 FOR MULTIPRODUCT INLETMETERING |  | ANALYSER | M10INLETMET | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INZ59027 | M10QIA304 | METER, ANALYSER , PANEL MOUNT | COLOUR METER PANEL2 FOR MULTIPRODUCT INLETMETERING |  | ANALYSER | M10INLETMET | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935543 | SALAINTP86 |  | TEST POINT # 86 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935560 | SALAINTP100 |  | TEST POINT # 100 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935577 | SADIATP8 |  | TEST POINT# 8 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935593 | SADIACP1IJ1 |  | INSULATING JOINT 1 AT KM 0 (A.D.INT'L AIRPORT) |  |  | SADIAPIPE | 1 | PIPING | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 5 | 1 | 1 | 5 | 3.0969 | Low | Low | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935609 | SMTP10 |  | TEST POINT# 10 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935624 | SMTP25 |  | TEST POINT# 25 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935639 | SMTP41 |  | TEST POINT# 41 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935654 | SMLPGTP9 | CP TEST POINT | TEST POINT # 9 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935670 | SMLPGTP25 | CP TEST POINT | TEST POINT # 25 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935685 | SMLPGTP40 | CP TEST POINT | TEST POINT # 40 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP97807 | U51PI145 | LOOP, PRESSURE INDICATOR INSTRUMEN, LPG , 20.6 BAR , 17.46 BAR , 20-22 DEGC DE | LPG TO MUSSAFFAH |  | OPENLOOP | U5101R01 | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935462 | SALAINCP1IJ1 |  | INSULATION JOINT 1 AT KM 0 (C.P.S.# 1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935463 | SALAINCP2GB1 |  | GROUND BED (C.P.STATION-2 AT KM18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935464 | SALAINCP2RMU1 |  | CP REMOTE MONITORING UNIT(C.P.STATION-2 AT KM18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938721 | M400HS421C/SP | SWITCH, SELECTOR | Lube Oil Cooling Fan A Stop Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938722 | M400HS421C/ST | SWITCH, SELECTOR | Lube Oil Cooling Fan A Strat Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938723 | M400HS422/DU | SWITCH, SELECTOR | Lube Oil Cooling Fan B Duty Sec.SwitchFor 400-P-01 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938724 | M400HS422C/S | SWITCH, SELECTOR | Lube Oil Cooling Fan B Strat Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938725 | M400HS422C/SP | SWITCH, SELECTOR | Lube Oil Cooling Fan B Stop Switch For 400-P-016B |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938726 | M400HS423B | SWITCH, SELECTOR | Lube Oil Filter Transfer Valve Select Other Filter |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938727 | M400HS464/DU | SWITCH, SELECTOR | Lube Oil Pump A Duty Selector Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938728 | M400HS464C/SP | SWITCH, SELECTOR | Lube Oil Pump A Stop Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938729 | M400HS464C/ST | SWITCH, SELECTOR | Lube Oil Pump A Start Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938730 | M400HS465/DU | SWITCH, SELECTOR | Lube Oil Pump B Duty Selector Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938731 | M400HS465C/SP | SWITCH, SELECTOR | Lube Oil Pump B Stop Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938732 | M400HS465C/ST | SWITCH, SELECTOR | Lube Oil Pump B Start Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938733 | M400HS466/DU | SWITCH, SELECTOR | Lube Oil Cooling Fan A Selector Swt. For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938734 | M400HS466C/SP | SWITCH, SELECTOR | Lube Oil Cooling Fan A Stop Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938735 | M400HS466C/ST | SWITCH, SELECTOR | Lube Oil Cooling Fan A Strat Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938736 | M400HS467/DU | SWITCH, SELECTOR | Lube Oil Cooling Fan B Duty Sec.SwitchFor 400-P-01 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938737 | M400HS467C/SP | SWITCH, SELECTOR | Lube Oil Cooling Fan B Stop Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938738 | M400HS467C/ST | SWITCH, SELECTOR | Lube Oil Cooling Fan B Strat Switch For 400-P-019 |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938739 | M400HS468B | SWITCH, SELECTOR | Lube Oil Filter Transfer Valve Select Other Filter |  | PB_HS-MC | M400SYS | 3 | PB_HS-MC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938740 | M400LI401C | INDICATOR | Lube Oil Reservoir - Level For 400-P-016A | 935826 | OPENLOOP | M400P016A | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI401C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/09/18 | MC-PM-004-Y1
938741 | M400LI416C | INDICATOR | Lube Oil Reservoir - Level For 400-P-016B | 935827 | OPENLOOP | M400P016B | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI416C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/10/18 | MC-PM-004-Y1
938742 | M400LIC540 | LOOP, LEVEL CONTROL, JET A1 , 0.841 , 0.751 , 87 DEG.C , MASONEILAN ****, 88-211 | On/Off Valve for 400-L-0003A |  | CLOSLOOP | M400LEVEL | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LIC540-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 02/12/18 | MC-PM-005-M6
938743 | M400LIC541 | LOOP, LEVEL CONTROL, JET A1 , 0.841 , 0.751 , 87 DEG.C , MASONEILAN ****, 88-211 | On/Off Valve for 400-L-003B |  | CLOSLOOP | M400LEVEL | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LIC541-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/12/18 | MC-PM-005-M6
938744 | M400LIC751 | LOOP, LEVEL CONTROL, JET A1 , .841 , .751 , 45 DEG.C , DRESSER ****, 88-21114 , | Level for Filter Coalescer 400-L-004A |  | CLOSLOOP | M400LEVEL | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LIC751-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/12/18 | MC-PM-005-M6
938745 | M400LT804 | TRANSMITTER, LEVEL , 4-20MA , 10-32VDC | Dye Injection Package 400-ME-003 | 932934 | LVL_TX | M400ME003 | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | M400LT804-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/09/18 | MC-PM-004-Y1
938746 | M400LT931 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 4-20MA | Gas Oil Storage Tank 400-V-179 | 939724 | LVL_TX | M400LI931 | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938747 | M400PDI404 | GAUGE, DIFFERENTIAL PRESSURE, 0-2.5 BAR , 100MM , 1/2" FNPT , 304 SS , NiCrCo-AL | Lube Oil Filter - Press. Drop For 400-P-016A | 935826 | OPENLOOP | M400P016A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938748 | M400PDI419 | GAUGE, DIFFERENTIAL PRESSURE, 0-2.5 BAR , 100MM , 1/2" FNPT , 304 SS , NiCrCo-AL | Lube Oil Filter - Press. Drop For 400-P-016B | 935827 |  | M400P016B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938749 | M400PDI464 | GAUGE, DIFFERENTIAL PRESSURE, 100MM , 1/2" FNPT , 304 SS , NiCrCo-ALLOY (DURATHE | Lube Oil Filter - Press. Drop For 400-P-019 | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938752 | M400PDI926 | GAUGE, DIFFERENTIAL PRESSURE, 100MM , SS , 316 SS , SS , BOTTOM , DIRECT | Diff. Pressure at 400-P-080A | 934060 |  | M400P080A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI926-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/10/18 | MC-PM-011-M3
938753 | M400PDI927 | GAUGE, DIFFERENTIAL PRESSURE, 100MM , SS , 316 SS , BOTTOM , DIRECT | Diff. Pressure at 400-P-080B | 934061 |  | M400P080B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI927-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/10/18 | MC-PM-011-M3
938754 | M400FAH541 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Metering Skid 400-FT-541A/B |  | ALARMANC | M400SYS | 2 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FAH541-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/04/19 | MC-PM-003-Y1
938755 | M400FAH620 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Metering Skid RUW-MUS, 400-FT-620A/B/C |  | ALARMANC | M400SYS | 2 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FAH620-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/04/19 | MC-PM-003-Y1
938756 | M400FAH771 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-771A/B |  | ALARMANC | M400SYS | 2 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FAH771-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/04/19 | MC-PM-003-Y1
938757 | M400FAH772 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-772 |  | ALARMANC | M400SYS | 2 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FAH772-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/04/19 | MC-PM-003-Y1
938758 | M400FAH861 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-861A/B |  | ALARMANC | M400SYS | 2 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400FAH861-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/04/19 | MC-PM-003-Y1
938759 | M400FALL001 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | 400-P-021A Discharge Flow |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL001-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/04/19 | MC-PM-003-Y1
938760 | M400FALL002 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | 400-P-021B Discharge Flow |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL002-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/04/19 | MC-PM-003-Y1
938761 | M400FALL003 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | 400-P-021C Discharge Flow |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL003-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/04/19 | MC-PM-003-Y1
938762 | M400FALL004 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Gas Oil Intertank Transfer Pumps Discharge Flow |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL004-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/04/19 | MC-PM-003-Y1
938763 | M400FALL008 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Slop Pump 400-P-024A Disch. Flow |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL008-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/04/19 | MC-PM-003-Y1
938764 | M400FALL009 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Slop Pump 400-P-024B Disch. Flow |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL009-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/04/19 | MC-PM-003-Y1
938765 | M400FALL771A | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-771A |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL771A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/04/19 | MC-PM-003-Y1
938766 | M400FALL771B | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-771B |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL771B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/04/19 | MC-PM-003-Y1
939865 | M400SE401 | PROBE, VIBRATION , 8MM , 0.5 M | Pump-Keyphasor FOR M400P016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400SE401-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 26/01/19 | MC-PM-012-M3
939866 | M400SE416 | PROBE, VIBRATION , 8MM , 0.5 M | Pump-Keyphasor FOR M400P016B | 935827 | VIBRE_TX | M400P016B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400SE416-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 26/01/19 | MC-PM-012-M3
939867 | M400TG402 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSE-NCE (M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939868 | M400TG403 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSEN -CE (M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939869 | M400TG404 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSEN -DE (M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939870 | M400TG405 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSEN- NDE (M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939871 | M400TG420 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSEN -NDE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939872 | M400TG417 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSE-NCE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939873 | M400TG419 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSEN -DE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939874 | M400TG418 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | L/O RETURN -BEARING HOUSEN -CE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37089 | UTOYOTA97281 | 97281 - TOYOTA PICK-UP ( MUSSAFAH OPRN.) | TOYOTA PICK-UP 97281 ( MUSSAFAH OPRN.) |  |  | MREDUNDANT | 4 | 0 | 648701-610920 | MTERMINAL | DECOMMISSIONED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA97281UHE | INACTIVE | MECH | PM | EDS | 1 | MONTHS | 05/07/18 | MM-PM-029-M1
VHC37090 | UNISSAN51042 | 51042 - NISSAN X-TERRA ( P/LINE SUPERVISOR ) | NISSAN X-TERRA 51042 ( P/LINE SUPERVISOR ) |  |  | MREDUNDANT | 3 | 0 | 648701-610920 | MTERMINAL | DECOMMISSIONED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UNISSAN51042UHE | INACTIVE | MECH | PM | EDS | 1 | MONTHS | 05/07/18 | MM-PM-029-M1
933527 | M400MOV314 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-107 OUTLET SHELL (ULG 98, 12" X 10" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV314-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/02/19 | ME-PM-002-M6
933528 | M400MOV315 | ACTUATOR,ELECTRIC MOTOR, SLOP, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-109 INLET SHELL (SLOP, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV315-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
933529 | M400MOV316 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-109 OUTLET SHELL (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV316-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
933530 | M400MOV317 | ACTUATOR,ELECTRIC MOTOR, SLOP, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-110 INLET SHELL (SLOP, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV317-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/09/18 | ME-PM-002-M6
933531 | M400MOV318 | ACTUATOR,ELECTRIC MOTOR, SLOP, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-110 OUTLET SHELL (SLOP, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV318-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/01/19 | ME-PM-002-M6
933532 | M400MOV319 | ACTUATOR,ELECTRIC MOTOR, KEROSENE, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-108 INLET SHELL (KEROSENE, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV319-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/02/19 | ME-PM-002-M6
933533 | M400MOV320 | ACTUATOR,ELECTRIC MOTOR, KEROSENE, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 18RPM, 23 SEC, 8" x 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR T-108 OUTLET SHELL (KEROSENE, 8" X 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV320-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/02/19 | ME-PM-002-M6
933534 | M400MOV501 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR BATTERY LIMIT VALVE RECEIVER.(NAPHTHA / REF / JET A1 / HSGO, 10" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV501-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/12/18 | ME-PM-002-M6
933535 | M400MOV502 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" CL 600, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR ISOLATION VALVE RECEIVER (NAPHTHA / REF / JET A1 / HSGO, 10" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV502-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
933536 | M400MOV503 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 600, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR BYPASS VALVE RECEIVER (NAPHTHA / REF / JET A1 / HSGO, 10" X 8" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV503-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/12/18 | ME-PM-002-M6
933537 | M400MOV504 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 600, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV SRR BYPASS VALVE (NAPHTHA / REFORMATE/ JET A1 / HSGO,10" X 8" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV504-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/11/18 | ME-PM-002-M6
933538 | M400MOV505 | ACTUATOR,ELECTRIC MOTOR, JET A1, 95.5, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 600, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV, SRR, LAUNCHER TO JET A1(JET A1, 10" X 8" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV505-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/10/18 | ME-PM-002-M6
933539 | M400MOV506 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 600, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV SRR, BATTERY LIMIT LAUNCHER (NAPHTHA / REF / JET A1 / HSGO, 10" X 8" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV506-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
933540 | M400MOV507 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" CL 600, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR ISOLATION LAUNCHER (NAPHTHA / REF / JET A1 / HSGO, 10" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV507-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
933541 | M400MOV508 | ACTUATOR,ELECTRIC MOTOR, NAPHTHA / REF / JET A1 / HSGO, 95.5, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV SRR, BATTERY LIMIT.(NAPHTHA / REF / JET A1 / HSGO, 10" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV508-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/10/18 | ME-PM-002-M6
933542 | M400MOV532 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-INLET TO FLOW METERING (JET A1, 10" X 8" CL 300 WITH EXTN LG 1430MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV532-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/10/18 | ME-PM-002-M6
933543 | M400MOV533 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR OUTLET TO FLOW METERING (JET A1, 10" X 8" CL 300 WITH EXTN LG 1430MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV533-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/01/19 | ME-PM-002-M6
933544 | M400MOV534 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR INLET FILTER COALESCER (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV534-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933545 | M400MOV535 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR OUTLET FILTER COALESCER (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV535-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/01/19 | ME-PM-002-M6
933546 | M400MOV536 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR INLET FILTER COALESCER (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV536-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933547 | M400MOV537 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR OUTLET FILTER COALESCER (JET A1, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV537-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/01/19 | ME-PM-002-M6
933548 | M400MOV538 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR FCS OUTLET MANIFOLD (JET A1, 16" X14" CL 300 WITH EXTN LG 1730MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV538-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/10/18 | ME-PM-002-M6
933549 | M400MOV547 | ACTUATOR,ELECTRIC MOTOR, OFF SPEC. JET A1, 18.4, MOTORISED, AUDCO, IQ18, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F10, SAE-80EP, IQ18F10B4, IP68, 203Nm | MOV FOR M400-P-020 SUCTION LINE (OFF SPEC. JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV547-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933550 | M400MOV548 | ACTUATOR,ELECTRIC MOTOR, OFF SPEC. JET A1, 18.4, MOTORISED, AUDCO, IQ12F10B4, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F10, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-MP-020,BOOSTER PUMP OFF SPEC.JET-A1, DISCHARGE (OFF SPEC. JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV548-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933551 | M400MOV549 | ACTUATOR,ELECTRIC MOTOR, OFF SPEC. JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT 772 INLET (OFF SPEC.JET A1, 10" X 8" CL 150 WITH EXTN LG 1470) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV549-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/12/18 | ME-PM-002-M6
933552 | M400MOV550 | ACTUATOR,ELECTRIC MOTOR, OFF SPEC. JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT 772 OUTLET (OFF SPEC.JET A1, 10" X 8" CL 150 WITH EXTN LG 1470) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV550-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/12/18 | ME-PM-002-M6
933553 | M400MOV551 | ACTUATOR,ELECTRIC MOTOR, OFF SPEC. JET A1, 143, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 900, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR 400-P-019 SUCTION LINE (OFF SPEC. JET A1, 10" X 8" CL 900) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV551-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
934897 | M400LT534 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-654MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L003A, DISPLACER LEVEL TX. | 939716 | DIS_TXTR | M400LI534 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934898 | M400LT540 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-654MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L003A, DISPLACER LEVEL TX. | 938742 | DIS_TXTR | M400LIC540 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934899 | M400LT541 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-654MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L003B, DISPLACER LEVEL TX. | 938743 | DIS_TXTR | M400LIC541 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934900 | M400LT576 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-2180MM , 4-20mA + HART , 24 V D | SUMP TANK SRR P/L 400V175, WAVE RADAR LEVEL TX. | 939717 | RDR_TXTR | M400LI576 | 2 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934901 | M400LT577 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-2180MM , 4-20mA + HART , 24 V D | SUMP TANK SRR P/L 400V175, WAVE RADAR LEVEL TX. | 939718 | RDR_TXTR | M400LI577 | 2 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934902 | M400LT578 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-2180MM , 4-20mA + HART , 24 V D | SUMP TANK SRR P/L 400V176, WAVE RADAR LEVEL TX. | 939719 | RDR_TXTR | M400LI578 | 2 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934903 | M400LT579 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-2180MM , 4-20mA + HART , 24 V D | SUMP TANK SRR P/L 400V176, WAVE RADAR LEVEL TX. | 939720 | RDR_TXTR | M400LI579 | 2 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934904 | M400LT751 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-888MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L004A, DISPLACER LEVEL TX. | 938744 | DIS_TXTR | M400LIC751 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934905 | M400LT752 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-888MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L004A, DISPLACER LEVEL TX. | 939721 | DIS_TXTR | M400LI752 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934906 | M400LT753 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-888MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L004B, DISPACER LEVEL TX. | 938874 | LVL_TX | M400LIC753 | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934907 | M400LT754 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0-888MM , 4-20mA + HART , 24V DC, 2 WI | FILTER COALESCER 400L004B, DISPLACER LEVEL TX. | 939722 | DIS_TXTR | M400LI754 | 2 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934908 | M400LT928 | TRANSMITTER, LIQUID LEVEL, FLOAT AND TAPE , MM , 4-20mA , 24V DC, 2 WIRE , 2", 3 | LEVEL TRANSMITTER OF FIRE WATER TANK 400T201, FLOAT LEVEL TX. | 939726 | LVL_TX | M400T201 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LT928-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/08/18 | MC-PM-004-Y1
934909 | M400LT930 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-3080MM , 4-20mA + HART , 24 V D | POTABLE WATER VESSEL GUIDED WAVE RADAR LEVEL TX. | 939723 | RDR_TXTR | M400LI930 | 2 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934910 | MQ600LT001 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-2180MM , 4-20mA + HART , 24 V D | SUMP TANK 600-D-077,GUIDED WAVE RADAR LVL TRNSMTR |  | RDR_TXTR | MQ600LEVEL | 2 | RDR_TXTR | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600LT001-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-004-M6
934911 | MQ600LT002 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-2180MM , 4-20mA + HART , 24 V D | SUMP TANK 600-D-077,GUIDED WAVE RADAR LVL TRNSMTR |  | RDR_TXTR | MQ600LEVEL | 2 | RDR_TXTR | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600LT002-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-004-M6
IIF59009 | M51FQRAL103 | LOOP, FLOW INDICATOR INSTRUMENT, MULTOPRODUCT , 170 M3H , 45 DEGC, CMF-300-M-4 | PIG RECEIVER AT MUSSAFAH TERMINAL | PGR56198 | OPENLOOP | M5101R02 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59010 | M51FT103 | METER, FLOW, MASS | FLOW. TRAN. FOR LPG PIG RECEIVER AT MTF | IIF59009 | FL_TX | M51FQRAL103 | 2 | FL_TX | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59011 | M51FE103 | SENSOR, FLOWMETER | FLOW. TRAN. FOR LPG PIG RECEIVER AT MTF | IIF59009 | FL_MTR | M51FQRAL103 | 2 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59016 | M10FQRAL301 | LOOP, FLOW INDICATOR INSTRUMENT, MULTI PRODUCT , 170 M3H , 45 DEG.C DEGC, CMF3 | GAS OIL FROM ADRD INLET METERING |  | OPENLOOP | M10INLETMET | 3 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59018 | M10FT301 | METER, FLOW, MASS | FLOW TRANSMITTER GAS OIL INLET METERING. | IIF59016 | FL_TX | M10FQRAL301 | 2 | FL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59019 | M10FE301 | SENSOR, FLOWMETER , 240VAC 50HZ, 4-20MA OUTPUT | CORIOLIS METER FOR MULTIPRODUCT INLETMETERING SKID | IIF59016 | FL_MTR | M10FQRAL301 | 2 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59021 | M10FQRAL302 | LOOP, FLOW INDICATOR INSTRUMENT, MULTI PRODUCT , 170 M3/H , 45 DEGC, CMF300M42 | MULTI PRODUCT INLETMETERING |  | OPENLOOP | M10INLETMET | 3 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59023 | M10FT302 | METER, FLOW, MASS | FLOW TRANSMITTER FOR GAS OIL INLET METERING SKID. | IIF59021 | FL_TX | M10FQRAL302 | 2 | FL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF59025 | M10FE302 | SENSOR, FLOWMETER , 240VAC 50HZ, 4-20MA OUTPUT | CORIOLIS METER FOR MULTIPRODUCT INLETMETERING SKID | IIF59021 | FL_MTR | M10FQRAL302 | 2 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IDG30451 | U51AE103 | SENSOR, COMBUSTIBLE GAS , 0-100 Perc. LEL | GAS SENSOR FOR LPG PIG LAUNCHER | 931209 | FG_DET | U51AT103 | 1 | FG_DET | 623101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269347 | M410PG764A | A/B TOWER & PURGE PRESSURE GAUGE | A/B TOWER & PURGE PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269348 | M410PG764B | A/B TOWER & PURGE PRESSURE GAUGE | A/B TOWER & PURGE PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269349 | M410PG765A | A/B TOWER & PURGE PRESSURE GAUGE | A/B TOWER & PURGE PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269350 | M410PG765B | A/B TOWER & PURGE PRESSURE GAUGE | A/B TOWER & PURGE PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269351 | M410EA092A | AFTER COOLER FOR COMPRESSOR | AFTER COOLER FOR COMPRESSOR |  | HEATEXHR | M410K001A | 3 | HEATEXHR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA092A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269352 | M410EA092B | AFTER COOLER FOR COMPRESSOR | AFTER COOLER FOR COMPRESSOR |  | HEATEXHR | M410K001B | 3 | HEATEXHR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA092B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269353 | M410L094A | AFTER-FILTERS | AFTER-FILTERS |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269354 | M410L094B | AFTER-FILTERS | AFTER-FILTERS |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269355 | M410K001A | AIR COMPRESSOR | AIR COMPRESSOR |  | COMPRS | M410COMP | 3 | COMPRS | 617101-310600 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 2 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269356 | M410K001B | AIR COMPRESSOR | AIR COMPRESSOR |  | COMPRS | M410COMP | 3 | COMPRS | 617101-310600 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269357 | M410IAC001A | AIR COPMPRESSORS CONTROL PANEL | AIR COPMPRESSORS CONTROL PANEL |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269358 | M410IAC001B | AIR COPMPRESSORS CONTROL PANEL | AIR COPMPRESSORS CONTROL PANEL |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269359 | M410XV763A | ON-OFF BALL VALVE FOR AIR DRYER PURGE | ON-OFF BALL VALVE FOR AIR DRYER PURGE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269360 | M410XV763B | ON-OFF BALL VALVE FOR AIR DRYER PURGE | ON-OFF BALL VALVE FOR AIR DRYER PURGE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269361 | M410XV764A | ON-OFF BALL VALVE FOR AIR DRYER PURGE | ON-OFF BALL VALVE FOR AIR DRYER PURGE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269362 | M410XV764B | ON-OFF BALL VALVE FOR AIR DRYER PURGE | ON-OFF BALL VALVE FOR AIR DRYER PURGE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269363 | M410D094A | AIR DRYERS | AIR DRYERS |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269364 | M410D094B | AIR DRYERS | AIR DRYERS |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269365 | M410D095A | AIR DRYERS | AIR DRYERS |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269366 | M410D095B | AIR DRYERS | AIR DRYERS |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269367 | M410VT753A | AIR END VIBRATION SENSOR WITH TRANSMITTER | AIR END VIBRATION SENSOR WITH TRANSMITTER |  | VIBRMON | M410K001A | 2 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269368 | M410VT753B | AIR END VIBRATION SENSOR WITH TRANSMITTER | AIR END VIBRATION SENSOR WITH TRANSMITTER |  | VIBRMON | M410K001B | 2 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269369 | M410XV761A | ON-OFF BALL VALVE FOR AIR INLET SERVICE | ON-OFF BALL VALVE FOR AIR INLET SERVICE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269370 | M410XV761B | ON-OFF BALL VALVE FOR AIR INLET SERVICE | ON-OFF BALL VALVE FOR AIR INLET SERVICE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269371 | M410XV762A | ON-OFF BALL VALVE FOR AIR INLET SERVICE | ON-OFF BALL VALVE FOR AIR INLET SERVICE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269372 | M410XV762B | ON-OFF BALL VALVE FOR AIR INLET SERVICE | ON-OFF BALL VALVE FOR AIR INLET SERVICE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269373 | M410ARV001A | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-001A (MUSSAFAH-ADIA NORTH) |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269374 | M410ARV001B | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-001B (MUSSAFAH-ADIA NORTH) |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269375 | M410ARV001C | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-001C (MUSSAFAH-ADIA NORTH) |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269376 | M410ARV001D | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-001D (MUSSAFAH-ADIA NORTH) |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269377 | M410ARV005A | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-005A |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269378 | M410ARV005B | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-005B |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269379 | M410ARV005C | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-005C |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269380 | M410ARV005D | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-005D |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269381 | M410ARV005E | Air Release Valve 2" | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-005E |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269382 | M410ARV011A | Air Release Valve 2" | AIR RELEASE VALVE 2", JP-8 FILTER COALESCERS 410-L-011A (MUSSAFAH-AL DHAFRA) |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269383 | M410ARV011B | Air Release Valve 2" | AIR RELEASE VALVE 2", JP-8 FILTER COALESCERS 410-L-011B (MUSSAFAH-AL DHAFRA) |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269384 | M410STA001 | Air Release Valve 3/4" | Air Release Valve 3/4" |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 12 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269385 | M410JBE761A | ANALOGUE JUNCTION BOX FOR AIR DRYER | ANALOGUE JUNCTION BOX FOR AIR DRYER |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269386 | M410JBE761B | ANALOGUE JUNCTION BOX FOR AIR DRYER | ANALOGUE JUNCTION BOX FOR AIR DRYER |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269388 | M410P027A | ANTI FREEZE RECIPROCATING INJECTION PUMP. | DHAFRA ANTI FREEZE INJECTION PUMP 410ME011. |  | PURE | M410ME011 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269389 | M410P027B | ANTI FREEZE RECIPROCATING INJECTION PUMP. | ANTI FREEZE INJECTION PUMP 410ME011. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269390 | M410MP028A | ANTI FREEZE ADDITIVE (DILUTED CHEMICAL) INJECTION PUMPS MOTOR | MOTOR OF ANTI FREEZE ADDITIVE (DILUTED CHEMICAL) INJECTION PUMP. |  | MOTOR | M410P028A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP028A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269391 | M410MP028B | ANTI FREEZE ADDITIVE (DILUTED CHEMICAL) INJECTION PUMPS MOTOR | MOTOR OF ANTI FREEZE ADDITIVE (DILUTED CHEMICAL) INJECTION PUMP. |  | MOTOR | M410P028B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP028B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269392 | M410MP027A | ANTI FREEZE ADDITIVE (NEAT CHEMICAL) INJECTION PUMPS MOTOR | MOTOR OF DHAFRA ANTI FREEZE ADDITIVE INJECTION PUMP. |  | MOTOR | M410P027A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP027A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269393 | M410MP027B | ANTI FREEZE ADDITIVE (NEAT CHEMICAL) INJECTION PUMPS MOTOR | MOTOR OF DHAFRA ANTI FREEZE ADDITIVE INJECTION PUMP. |  | MOTOR | M410P027B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP027B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269394 | M410MP040A | Electric Motor LV Cage-Induction - Hazardous Area | ANTI FREEZE CHEMICAL OFFLOADING PUMP-A |  | MOTOR | M410P040A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP040A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269395 | M410MP040B | Electric Motor LV Cage-Induction - Hazardous Area | ANTI FREEZE CHEMICAL OFFLOADING PUMP-B |  | MOTOR | M410P040B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP040B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269396 | M410T030 | ANTI FREEZE CHEMICAL STORAGE TANK | ANTI FREEZE CHEMICAL STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269397 | M410T031 | ANTI FREEZE CHEMICAL STORAGE TANK | ANTI FREEZE CHEMICAL STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269398 | M410FT751 | FLOW TRANSMITTER FOR ANTI-FREEZE INJECTION PACKAGE 410-ME-011 FOR JET A1 / JP-8 | FLOW TRANSMITTER FOR ANTI-FREEZE INJECTION PACKAGE 410-ME-011 FOR JET A1 / JP-8 |  | PACKAGE | M410ME011 | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269399 | M410PSV752 | ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) | ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) |  | PSV | M410ME011 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269400 | M410PSV753 | ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) | ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) |  | PSV | M410ME011 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269401 | M410PSV754 | ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) | ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) |  | PSV | M410ME011 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269402 | M410XV752 | PNEUMATIC VAVLE FOR ANTI-FREEZE INJECTION PACKGAE 410-ME-011 FOR JET A1 / JP-8 | PNEUMATIC VAVLE FOR ANTI-FREEZE INJECTION PACKGAE 410-ME-011 FOR JET A1 / JP-8 |  | SOL_VLV | M410ME011 | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269403 | M410PSV761 | ANTI STATIC CHEMICAL INJECTION PACKAGE | ANTI STATIC CHEMICAL INJECTION PACKAGE |  | PSV | M410ME201 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269404 | M410PSV762 | ANTI STATIC CHEMICAL INJECTION PACKAGE | ANTI STATIC CHEMICAL INJECTION PACKAGE |  | PSV | M410ME201 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269405 | M410TSV761 | THERMAL SAFETY VALVE FOR ANTI STATIC CHEMICAL INJECTION PACKAGE | THERMAL SAFETY VALVE FOR ANTI STATIC CHEMICAL INJECTION PACKAGE |  | PSV | M410ME201 | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 50 | 10 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269406 | M410ME201 | ANTI STATIC INJECTION PACKGE FOR GAS OIL | ANTI STATIC INJECTION PACKGE FOR GAS OIL |  | PACKAGE | M410PKG | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269407 | M410T020 | ANTI-STATIC CHEMICAL SRORAGE TANK | ANTI-STATIC CHEMICAL SRORAGE TANK |  | VESSEL | M410ME002 | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269408 | M410T201 | ANTI-STATIC CHEMICAL STORAGE TANK | ANTI-STATIC CHEMICAL STORAGE TANK |  | VESSEL | M410ME201 | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269409 | M410MP020A | ANTI-STATIC DILUTED CHEMICAL INJECTION PUMPS MOTOR | MOTOR OF ANTI-STATIC DILUTED CHEMICAL INJECTION PUMP. |  | MOTOR | M410P020A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP020A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269410 | M410MP020B | ANTI-STATIC DILUTED CHEMICAL INJECTION PUMPS MOTOR | MOTOR OF ANTI-STATIC DILUTED CHEMICAL INJECTION PUMP. |  | MOTOR | M410P020B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP020B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269411 | M410LT731 | LEVEL TRANSMITTER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | LEVEL TRANSMITTER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269412 | M410PSV731 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269413 | M410PSV732 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269414 | M410PSV733 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269415 | M410PSV734 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269416 | M410PSV735 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269417 | M410PSV736 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269418 | M410PSV737 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269419 | M410PSV738 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269420 | M410PSV751 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PRESSURE SAFETY VALVE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME011 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269421 | M410XV731 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 1 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269422 | M410XV732 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269423 | M410XV733 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269424 | M410XV734 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269425 | M410XV751 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | PNEUMATIC VAVLE FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME011 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269426 | M410FT731 | FLOW TRANSMITTER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | FLOW TRANSMITTER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269427 | M410FT732 | FLOW TRANSMITTER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 | FLOW TRANSMITTER FOR ANTI-STATIC INJECTION PACKAGE 410-ME-002 FOR JET A1 / JP-8 |  | PACKAGE | M410ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269428 | M410P201A | GAS OIL ANTI-STATIC INJECTION PUMPS | GAS OIL ANTI-STATIC INJECTION PUMPS |  | PURE | M410ME201 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269429 | M410P201B | GAS OIL ANTI-STATIC INJECTION PUMPS | GAS OIL ANTI-STATIC INJECTION PUMPS |  | PURE | M410ME201 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269430 | M410MP017A | ANTI-STATIC CHEMICAL INJECTION PUMPS MOTOR | ANTI-STATIC NEAT CHEMICAL INJECTION PUMPS MOTOR |  | MOTOR | M410P017A | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP017A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269431 | M410MP017B | ANTI-STATIC NEAT CHEMICAL INJECTION PUMPS MOTOR | ANTI-STATIC NEAT CHEMICAL INJECTION PUMPS MOTOR |  | MOTOR | M410P017B | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP017B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269432 | M410MP201A | ANTI-STATIC NEAT CHEMICAL INJECTION PUMPS MOTOR | ANTI-STATIC NEAT CHEMICAL INJECTION PUMPS MOTOR |  | MOTOR | M410P201A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP201A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269433 | M410MP201B | ANTI-STATIC NEAT CHEMICAL INJECTION PUMPS MOTOR | ANTI-STATIC NEAT CHEMICAL INJECTION PUMPS MOTOR |  | MOTOR | M410P201B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP201B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269434 | M410P017A | ANTI-STATIC NEAT CHEMICAL LNJECTION PUMPS | ADIA NORTH ANTI-STATIC CHEMICAL INJECTION PUMP 410ME002. |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269435 | M410P017B | ANTI-STATIC NEAT CHEMICAL LNJECTION PUMPS | ADIA NORTH ANTI-STATIC CHEMICAL INJECTION PUMP 410ME002. |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132691 | M400MAG001 | MOTOR,ELECTRIC, AGITATOR MOTOR, 1.10 KW, 50 HZ, 415 V, 1500 RPM, 3, 2.90 AMP, LCP-2 | MOTOR FOR AGITATOR MIXER INTERMEDIATE BUFFER TANK - CHAIN 1 |  | MOTOR | M400AG001 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MAG001-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 17/01/19 | ME-PM-014-M6
969132692 | M400MAG002 | MOTOR,ELECTRIC, VERTICAL MIXER, 1.10 KW, 50 HZ, 415 V, 3, LCP-4 | MOTOR FOR POLY ELECTROLYTE MAKE UP TANK MIXER |  | MOTOR | M400AG002 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MAG002-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 18/01/19 | ME-PM-014-M6
969132693 | M400MK001A | MOTOR,ELECTRIC, COMPRESSOR MOTOR, 1.70 KW, 50 HZ, 415 V, 1500 RPM, 3, 4.0 AMP, 400MCC001 (LCP-4) | MOTOR FOR AIR COMPRESSOR-A |  | MOTOR | M400K001A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MK001A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 22/11/18 | ME-PM-014-M6
969132694 | M400MK001B | MOTOR,ELECTRIC, AIR COMPRESSOR MOTOR, IP 54, 1.70 KW, 50 HZ, 415 V, 1500 RPM, 3, 4.00 AMP, M400MCC001 LCP-4 | MOTOR FOR AIR COMPRESSOR - B |  | MOTOR | M400K001B | 2 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MK001B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 23/11/18 | ME-PM-014-M6
969132696 | M400MK002A | MOTOR,ELECTRIC, AIR BLOWER MOTOR, 3.00 KW, VARIABLE HZ, 415 V, 3, 7.70 AMP | MOTOR FOR AIR BLOWER - A |  | MOTOR | M400K002A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MK002A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 19/12/18 | ME-PM-014-M6
939705 | M400LI303 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for ULG95 Tank 400-T-112 |  | TANKGAUG | M400T112 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | Non Critical | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI303-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/08/18 | MC-PM067.M6
939706 | M400LI312 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION GAS OIL TANK 400-T-116 |  | TANKGAUG | M400T116 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939707 | M400LI313 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for Jet A1 Tank 400-T-117 |  | TANKGAUG | M400T117 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI313-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/10/18 | MC-PM067.M6
939708 | M400LI314 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION JET A1 TANK 400-T-117 |  | TANKGAUG | M400T117 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939709 | M400LI315 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for Jet A1 Tank 400-T-118 |  | TANKGAUG | M400T118 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI315-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/10/18 | MC-PM067.M6
939710 | M400LI316 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION JET A1 TANK 400-T-118 |  | TANKGAUG | M400T118 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939711 | M400LI317 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for Jet A1 Tank 400-T-119 |  | TANKGAUG | M400T119 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI317-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 24/08/18 | MC-PM067.M6
939712 | M400LI318 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION JET A1 TANK 400-T-119 |  | TANKGAUG | M400T119 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939713 | M400LI319 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for Jet A1 Tank 400-T-120 |  | TANKGAUG | M400T120 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI319-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/11/18 | MC-PM067.M6
939714 | M400LI320 | RADAR TRANSMITTER,LIQUID LEVEL, GUIDED WAVE RADAR, 240VAC, DIE-CAST ALUMINIUM, INTRINSICALLY SAFE | RADAR LEVEL INDICATION JET A1 TANK 400-T-120 |  | TANKGAUG | M400T120 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939715 | M400LI532 | LOOP, LEVEL INDICATOR INSTRUMENT, FOXBORO , 244LD+104FK+104DC+104DE , 0-654MM | FILTER COALESCER 400L003A, DISPLACER LEVEL | 932609 | DIS_TXTR | M400L003A | 3 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI532-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/08/18 | MC-PM-004-Y1
939716 | M400LI534 | LOOP, LEVEL INDICATOR INSTRUMENT, FOXBORO , 244LD+104FK+104DC+104DE , 0-654MM | FILTER COALESCER 400L003A, DISPLACER LEVEL | 932609 | DIS_TXTR | M400L003A | 3 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI534-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/08/18 | MC-PM-004-Y1
939717 | M400LI576 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , FMP40-5LL2APJB21CB , 0-2180 | SUMP TANK SRR P/L 400V175, WAVE RADAR LEVEL | 937629 | RDR_TXTR | M400V175 | 3 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI576-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/05/19 | MC-PM-004-Y1
939718 | M400LI577 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , FMP40-5LL2APJB21CB , 0-2180 | SUMP TANK SRR P/L 400V175, WAVE RADAR LEVEL | 937629 | RDR_TXTR | M400V175 | 3 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI577-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/05/19 | MC-PM-004-Y1
939719 | M400LI578 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , FMP40-5LL2APJB21CB , 0-2180 | SUMP TANK SRR P/L 400V176, WAVE RADAR LEVEL | 937630 | RDR_TXTR | M400V176 | 3 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI578-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/05/19 | MC-PM-004-Y1
939720 | M400LI579 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , FMP40-5LL2APJB21CB , 0-2180 | SUMP TANK SRR P/L 400V176, WAVE RADAR LEVEL | 937630 | RDR_TXTR | M400V176 | 3 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 3 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI579-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/05/19 | MC-PM-004-Y1
939721 | M400LI752 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , 244LD+104FK+104DC+104DE , 0 | FILTER COALESCER 400L004A, DISPLACER LEVEL | 932611 | DIS_TXTR | M400L004A | 3 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI752-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/08/18 | MC-PM-004-Y1
939722 | M400LI754 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , 244LD+104FK+104DC+104DE , 0 | FILTER COALESCER 400L004B, DISPLACER LEVEL | 932612 | DIS_TXTR | M400L004B | 3 | DIS_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI754-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/08/18 | MC-PM-004-Y1
939723 | M400LI930 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , FMP40-5LL2APJB21CB , 0-3080 | POTABLE WATER VESSEL GUIDED WAVE RADAR LEVEL | 938645 | RDR_TXTR | M400V117 | 3 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI930-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/05/19 | MC-PM-004-Y1
939724 | M400LI931 | LOOP, LEVEL INDICATOR INSTRUMENT, SAAB , RTG39AB0SA0R20C0100S5013A30004 , 0-12 | Gas Oil Storage Tank 400-V-179 | 939598 | OPENLOOP | M400LEVEL | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI931-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/08/18 | MC-PM-004-Y1
939725 | M400LI926 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , FMD77-1BC7FB1DYABA , 0-1835 | LEVEL CORROSION INHIBITOR DOSING TANK 400-T-08 |  | OPENLOOP | M400LEVEL | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI926-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/08/18 | MC-PM-004-Y1
939726 | M400LI928 | LOOP, LEVEL INDICATOR INSTRUMENT, ENDRESS HAUSER , LT11-1007500420 , 0-17800 M | FIRE WATER TANK 400T201, FLOAT LEVEL | 939482 | OPENLOOP | M400T201 | 1 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 10 | 50 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI928-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/05/19 | MC-PM-004-Y1
939727 | M400PDI001 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR.TR. PUMP 400-P-021A STRAINER | 934051 | OPENLOOP | M400P021A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI001-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/01/19 | MC-PM-007-Y1
939728 | M400PDI002 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR. TRANSFER PUMP 400-P-021B STRAINER | 934052 | OPENLOOP | M400P021B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI002-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/01/19 | MC-PM-007-Y1
939729 | M400PDI003 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR. TRANSFER PUMP 400-P-021C STRAINER | 934053 | OPENLOOP | M400P021C | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI003-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/01/19 | MC-PM-007-Y1
939730 | M400PDI004 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR. TRANSFER PUMP 400-P-022A STRAINER | 934054 | OPENLOOP | M400P022A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI004-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/02/19 | MC-PM-007-Y1
939731 | M400PDI005 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR. TRANSFER PUMP 400-P-022B STRAINER | 934055 | OPENLOOP | M400P022B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI005-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/02/19 | MC-PM-007-Y1
939732 | M400PDI008 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR. TRANSFER PUMP 400-P-024A STRAINER | 934056 | OPENLOOP | M400P024A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI008-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/02/19 | MC-PM-007-Y1
939733 | M400PDI009 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR.TRANSFER PUMP 400-P-024B STRAINER | 934057 | OPENLOOP | M400P024B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI009-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/02/19 | MC-PM-007-Y1
939734 | M400PDI531 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR. COALESCER SEPARATR 400L003A FILTR | 932609 | OPENLOOP | M400L003A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI531-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/08/18 | MC-PM-007-Y1
939735 | M400PDI532 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR.FILTR COALESCR SEPARATR 400L003B FILTR | 932610 | OPENLOOP | M400L003B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI532-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/08/18 | MC-PM-007-Y1
939736 | M400PDI541A | LOOP, PRESSURE INDICATOR INSTRUMEN | D.P. NEPTHA/REFORM P/L, JET A1,CUSTODY METERIN | 938681 | OPENLOOP | M400FC541A | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI541A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/06/19 | MC-PM-007-Y1
939737 | M400PDI541B | LOOP, PRESSURE INDICATOR INSTRUMEN | D.P. NEPTHA/REFORM P/L, JET A1,CUSTODY METERIN | 938682 | OPENLOOP | M400FC541B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI541B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/06/19 | MC-PM-007-Y1
939738 | M400PDI546 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR. BOOSTER PUMP 400-P-020 STRAINER | 933878 | OPENLOOP | M400P020 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI546-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
939739 | M400PDI551 | LOOP, PRESSURE INDICATOR INSTRUMEN | DIFF.PR.TR. MAINLINE PUMP 400-P-019 STRAINER | 935830 | OPENLOOP | M400P019 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI551-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
939740 | M400PDI620A | LOOP, PRESSURE INDICATOR INSTRUMEN, ROSEMOUNT , 3051CD3A02A1BH2BAK8M5T1P1Q4Q8 | D.P. RUW-MUS, CUSTODY METERING SYSTEM. | 938683 | OPENLOOP | M400FC620A | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI620A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/06/19 | MC-PM-007-Y1
939741 | M400PDI620B | LOOP, PRESSURE INDICATOR INSTRUMEN, ROSEMOUNT , 3051CD3A02A1BH2BAK8M5T1P1Q4Q8 | Diff. Pr. RUW-MUS, Metering Skid 400FT620B. | 938684 | OPENLOOP | M400FC620B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI620B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/06/19 | MC-PM-007-Y1
939742 | M400PDI620C | LOOP, PRESSURE INDICATOR INSTRUMEN, ROSEMOUNT , 3051CD3A02A1BH2BAK8M5T1P1Q4Q8 | Diff. Pr. RUW-MUS, Metering Skid 400-FT-620C | 938685 | OPENLOOP | M400FC620C | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI620C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/06/19 | MC-PM-007-Y1
939743 | M400PDI751 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7CB1DABU , 0-2 K | DIFF.PR. BOOSTER PUMP 400-P-017A STRAINER | 933876 | OPENLOOP | M400P017A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI751-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/11/18 | MC-PM-007-Y1
939744 | M400PDI752 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7HB1DABU , 0-2 K | DIFF.PR. BOOSTER PUMP 400-P-017B STRAINER | 933877 | OPENLOOP | M400P017B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI752-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/11/18 | MC-PM-007-Y1
939745 | M400PDI753 | LOOP, PRESSURE INDICATOR INSTRUMEN, ROSEMOUNT , 3051CD3A02A1BH2BAK8M5T1P1Q4Q8 | DIFF.PR.FILTR COALESCR SEPARATR 400L004A FILTR | 932611 | OPENLOOP | M400L004A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI753-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/08/18 | MC-PM-007-Y1
939746 | M400PDI754 | LOOP, PRESSURE INDICATOR INSTRUMEN, ROSEMOUNT , 3051CD3A02A1BH2BAK8M5T1P1Q4Q8 | DIFF.PR.FILTR COALESCR SEPARATR 400L004B FILTR | 932612 | OPENLOOP | M400L004B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI754-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/08/18 | MC-PM-007-Y1
939747 | M400PDI771A | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7CB1DABU , 0-2 K | Diff. Pressure at 400-FT-771A | 938686 | OPENLOOP | M400FC771A | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI771A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/06/19 | MC-PM-007-Y1
939748 | M400PDI771B | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7CB1DABU , 0-2 K | Diff. Pressure at 400-FT-771B | 938687 | OPENLOOP | M400FC771B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI771B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/06/19 | MC-PM-007-Y1
939749 | M400PDI772 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7CB1DABU , 0-2 K | Flow metering skid 400-FT-772 | 938688 | OPENLOOP | M400FC772 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI772-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/06/19 | MC-PM-007-Y1
939750 | M400PDI801 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7HB1DABU , 0-1 K | DIFF.PR. MAINLINE PUMP 400-P-018A STRAINER | 935828 | OPENLOOP | M400P018A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI801-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/11/18 | MC-PM-007-Y1
939751 | M400PDI802 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7HB1DABU , 0-1 K | DIFF.PR.TR. MAINLINE PUMP 400-P-018B STRAINER | 935829 | OPENLOOP | M400P018B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI802-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/12/18 | MC-PM-007-Y1
939752 | M400PDI861A | LOOP, PRESSURE INDICATOR INSTRUMEN, ROSEMOUNT , 3051CD3A02A1BH2BAK8M5T1P1Q4Q8 | Flow metering skid 400-FT-861A | 938689 | OPENLOOP | M400FC861A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI861A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/08/18 | MC-PM-007-Y1
939753 | M400PDI861B | LOOP, PRESSURE INDICATOR INSTRUMEN, ROSEMOUNT , 3051CD3A02A1BH2BAK8M5T1P1Q4Q8 | Flow metering skid 400-FT-861B | 938690 | OPENLOOP | M400FC861B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI861B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/08/18 | MC-PM-007-Y1
939754 | M400PDI863 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDREE HAUSER , PMD75-1BC7CB1DABU , 0-03 K | DIFF.PR.TR. BOOSTER PUMP 400-P-015A STRAINER | 933874 | OPENLOOP | M400P015A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI863-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/09/18 | MC-PM-007-Y1
939755 | M400PDI864 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC7CB1DABU , 0-03 | DIFF.PR.TR. BOOSTER PUMP 400-P-015B STRAINER | 933875 | OPENLOOP | M400P015B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI864-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/09/18 | MC-PM-007-Y1
939757 | M400PDI881 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC8HB1DABU , 0-1 K | DIFF.PR.TR. MAINLINE PUMP 400-P-016A STRAINER | 935826 | OPENLOOP | M400P016A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI881-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/09/18 | MC-PM-007-Y1
939758 | M400PDI882 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMD75-1BC8HB1DABU , 0-1 K | DIFF.PR.TR. MAINLINE PUMP 400-P-016B STRAINER | 935827 | OPENLOOP | M400P016B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI882-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/10/18 | MC-PM-007-Y1
939759 | M400PI011 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | PRESS. AT SUCTION LINE 400-P-021A | 934051 |  | M400P021A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI011-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/01/19 | MC-PM-007-Y1
939760 | M400PI012 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | PRESS. AT SUCTION LINE 20-P-021B | 934052 |  | M400P021B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI012-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/01/19 | MC-PM-007-Y1
939761 | M400PI013 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | PRESS. SUCTION LINE PRESS. AT 400-P-021C | 934053 |  | M400P021C | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI013-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/01/19 | MC-PM-007-Y1
939762 | M400PI014 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | PRESS. SUCTION LINE PRESSURE AT 20-P-022A | 934054 |  | M400P022A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI014-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/02/19 | MC-PM-007-Y1
939763 | M400PI015 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | PRESS. SUCTION LINE PRESS.AT 400-P-022B | 934055 |  | M400P022B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI015-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/02/19 | MC-PM-007-Y1
939764 | M400PI018 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | SUCTION PRESS. ON SLOP TRANSFER PUMP 400P024A. | 934056 |  | M400P024A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI018-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/02/19 | MC-PM-007-Y1
939765 | M400PI019 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | PRESS. SUCTION SLOP TRANSFER PUMP 400P024B | 934057 |  | M400P024B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI019-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/02/19 | MC-PM-007-Y1
939766 | M400PI021A | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-25 | ULG 95/98 transfer pump 400-P-021ASeal Pr. | 934051 |  | M400P021A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI021A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/01/19 | MC-PM-007-Y1
939767 | M400PI021B | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-25 | ULG 95/98 transfer pump 400-P-021BSeal Pr. | 934052 |  | M400P021B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI021B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/01/19 | MC-PM-007-Y1
939768 | M400PI021C | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-25 | ULG 95/98 transfer pump 400-P-021CSeal Pr. | 934053 | OPENLOOP | M400P021C | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI021C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 31/01/19 | MC-PM-007-Y1
939769 | M400PI022A | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , 0-25 | Seal System Pressure-DE (M400P022A) | 934054 |  | M400P022A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI022A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/02/19 | MC-PM-007-Y1
939603 | M400T211 | RECEIVING SUMP PIT FOR WWTP (CHAIN I) | RECEIVING SUMP PIT FOR WWTP (CHAIN I) |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939604 | M400T218 | SUMP PIT FOR WWTP (CHAIN II) | RECEIVING SUMP PIT FOR WWTP (CHAIN II) |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939605 | M400T080 | CORROSION INHIBITOR DOSING TANK | CORROSION INHIBITOR DOSING TANK |  | TK |  | 3 | TK | 616101-610412 | IRPMTERMINAL | OPERATING | 10 | 1 | 50 | 5 | 5 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939606 | M400T114 | TANK | ULG-91 TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939607 | M400T115 | ULG-91 TANK IRP MUSSAFFAH TERMINAL. | ULG-91 TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939608 | M400T116 | GAS OIL TANK IRP MUSSAFFAH TERMINAL. | GAS OIL TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939609 | M400T116 | TANK, STORAGE | GAS OIL TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939610 | M400T117 | JET A1 TANK IRP MUSSAFFAH TERMINAL. | JET A1 TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939611 | M400T118 | JET A1 TANK IRP MUSSAFFAH TERMINAL | JET A1 TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939612 | M400T119 | JET A1 TANK IRP MUSSAFFAH TERMINAL. | JET A1 TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939613 | M400T120 | JET A1 TANK IRP MUSSAFFAH TERMINAL | JET A1 TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939630 | M400CONS1 | COMPUTER, DCS SYSTEM | WORKSTATION (CPU( (WP) |  | DCS_PNL | M400SYS | 2 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939631 | M400CONS2 | COMPUTER, DCS SYSTEM | WORKSTATION (CPU( (WP) |  | DCS_PNL | M400SYS | 2 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939632 | M400CONS3 | MONITOR, LCD | I/A SERIES MONITOR (LCD) |  | DCS_PNL | M400SYS | 2 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939633 | M400PT021C | TRANSMITTER, PRESSURE, SMART, 4-20MA, 24V DC, 2 WIRE , 1/ | ULG 95/98 transfer pump 400-P-021CSeal Pr. tx. | 939768 | PRES_TX | M400PI021C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939634 | M400PG21A | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | ULG 95/98 transfer pump 400-P-021ASeal Pr. GAUGE | 934051 |  | M400P021A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939635 | M400PG21B | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | ULG 95/98 transfer pump 400-P-021BSeal Pr. GAUGE | 934052 |  | M400P021B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939636 | M400PG21C | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | ULG 95/98 transfer pump 400-P-021CSeal Pr. GAUGE | 934053 | INDICATR | M400P021C | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939637 | M400PG24A | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | SLOP TRANSFER PUMPS 400-P-024A Seal Pr. GAUGE | 934056 |  | M400P024A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939638 | M400PG24B | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | SLOP TRANSFER PUMPS 400-P-024B Seal Pr. GAUGE | 934057 |  | M400P024B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939639 | M400PG017 | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Discharge Pressure at 400-P-024A | 934056 |  | M400P024A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939640 | M400PT20 | TRANSMITTER, PRESSURE, SMART, 4-20MA , 24V DC, 2 WIRE , 1/ | SEAL OIL PRESSURE FOR M400P015B | 933875 | PRES_TX | M400P015B | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT20-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/09/18 | MC-PM-007-Y1
939641 | M400LT555 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 4-20mA + HART , 24 V DC, 2 WIRE , | SAAB RADAR TRANSMITTER FOR M400T301 | 937600 | RDR_TXTR | M400T301 | 2 | RDR_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400LT555-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/05/19 | MC-PM-004-Y1
939642 | M400LT556 | TRANSMITTER, LIQUID LEVEL, ELECTRONIC , 4-20mA + HART , 24 V DC, 2 WIRE , 1/2" N | LEVEL TRANSMITTER FOR M400T301 | 937600 | LVL_TX | M400T301 | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939643 | M400PI001 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , 0-8 | Pr. transfer pump P-021A discharge line | 934051 |  | M400P021A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939644 | M400PI002 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , 0-8 | Pr. transfer pump P-021B discharge line | 934052 |  | M400P021B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI002-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/01/19 | MC-PM-007-Y1
939645 | M400PI003 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , 0-8 | Pr. transfer pump P-021C discharge line | 934053 |  | M400P021C | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI003-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/01/19 | MC-PM-007-Y1
939646 | M400PI004 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , 0-8 | Pressure 400-P-022A discharge line | 934054 |  | M400P022A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI004-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/02/19 | MC-PM-007-Y1
939647 | M400PI005 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , 0-8 | Pressure 400-P-022A discharge line | 934054 |  | M400P022A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI005-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/02/19 | MC-PM-007-Y1
939648 | M400PI008 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-20 | Pressure at 400-P-024A discharge line | 934056 |  | M400P024A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI008-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/02/19 | MC-PM-007-Y1
939649 | M400PI009 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-20 | Pressure at 400-P-024B discharge line | 934057 |  | M400P024B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI009-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/02/19 | MC-PM-007-Y1
939650 | M10FI301 | LOOP, FLOW INDICATOR INSTRUMENT, MULTI PRODUCT , 170 M3/H , 45 DEGC, CMF300M42 | Flow metering skid 10-FT-301 |  | FL_MTR | M10COMMON | 3 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939651 | M10FI302 | LOOP, FLOW INDICATOR INSTRUMENT, MULTI PRODUCT , 170 M3/H , 45 DEGC, CMF300M42 | Flow metering skid 10-FT-302 |  | FL_MTR | M10COMMON | 3 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939652 | M20TI161 | LOOP, TEMPERATURE INDICATOR INSTRU, PT 100 3 WIRES , PT100 , ENDRESS HAUSER | 20-P-227A Discharge Temp. | 934049 |  | M20P227A | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939653 | M20TI162 | LOOP, TEMPERATURE INDICATOR INSTRU, THERMORESISTANCE , PT100 , ENDRESS HAUSER | 20-P-227B Discharge Temp. | 934050 |  | M20P227B | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939654 | M20TE161 | ELEMENT, TEMPERATURE, THERMORESISTANCE, 3-WIRE, PT100 OHM @ 0 DEG C, PLATINUM. | 20-P-227A Discharge Temp. | 939652 | TEMP_ELE | M20TI161 | 1 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 1 | 5 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939655 | M20TE162 | ELEMENT, TEMPERATURE, THERMORESISTANCE , 3-WIRE , PT100 OHM @ 0 DEG C , PLATINUM | 20-P-227B Discharge Temp. | 939653 | TEMP_ELE | M20TI162 | 1 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 1 | 5 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939656 | M30DPI361 | LOOP, PRESSURE INDICATOR INSTRUMEN | Filter Coal. Sep. 30-L-006 Filter DP | 932607 | FL_TX | M30L006 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939657 | M30DPI362 | LOOP, PRESSURE INDICATOR INSTRUMEN | Filter Coal. Sep. 30-L-007 Filter DP | 932608 | FL_TX | M30L007 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939658 | M20PI262B | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , 0-8 | Discharge Pressure at 20-P-227B | 934050 | PRES_TX | M20P227B | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939659 | M20PI262A | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | SUCTION Pressure at 20-P-227B | 934050 | PRES_TX | M20P227B | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939660 | M20PI261B | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , 0-8 | Discharge Pressure at 20-P-227A | 934049 | PRES_TX | M20P227A | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939661 | M20PI261A | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1PB1RHABU , -1 T | Suction Pressure at 20-P-227A | 934049 | PRES_TX | M20P227A | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939662 | M20PT227A | TRANSMITTER, PRESSURE, SMART , 24V DC, 2 WIRE, 1/2" NPT(F) | PRESS.TRANSMITTER-Seal System Pressure FOR P227A | 934049 | PRES_TX | M20P227A | 2 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939663 | M20PT227B | TRANSMITTER, PRESSURE, SMART, 24V DC, 2 WIRE, 1/2" NPT(F) | PRESS.TRANSMITTER-Seal System Pressure FOR P227B | 934050 | PRES_TX | M20P227B | 2 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939679 | M400FI001 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 8" , 136.1MM , 6MM , 316 SS , 300 LB , | 400-P-021A Discharge Flow | 934051 | OPENLOOP | M400P021A | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FI001-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/01/19 | MC-PM-001-Y1
939680 | M400FI002 | LOOP, FLOW INDICATOR INSTRUMENT | 400-P-021B Discharge Flow | 934052 | OPENLOOP | M400P021B | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FI002-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/01/19 | MC-PM-001-Y1
939681 | M400FI003 | LOOP, FLOW INDICATOR INSTRUMENT | 400-P-021C Discharge Flow | 934053 | OPENLOOP | M400P021C | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FI003-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/01/19 | MC-PM-001-Y1
939682 | M400FI004 | LOOP, FLOW INDICATOR INSTRUMENT | Disch. Flow at 400-P-022A/B to 10-T-101/102/103/10 |  | OPENLOOP | M400SYS | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FI004-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/04/19 | MC-PM-001-Y1
939683 | M400FI008 | LOOP, FLOW INDICATOR INSTRUMENT | Slop Pump 400-P-024A Disch. | 934056 | OPENLOOP | M400P024A | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FI008-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/02/19 | MC-PM-001-Y1
939684 | M400FI009 | LOOP, FLOW INDICATOR INSTRUMENT | Slop Pump 400-P-024B Disch. Flow | 934057 | OPENLOOP | M400P024B | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FI009-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/02/19 | MC-PM-001-Y1
939685 | M400FQ541A | INDICATOR, FLOW , DIGITAL | mass flow indication for Metering Skid 400-FT-541A | 938681 | FL_MTR | M400FC541A | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ541A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/06/19 | MC-PM-002-Y1
939686 | M400FQ541B | INDICATOR, FLOW , DIGITAL | mass flow indicatio for Metering Skid 400-FT-541B | 938682 | FL_MTR | M400FC541B | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ541B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/06/19 | MC-PM-002-Y1
939687 | M400FQ620A | INDICATOR, FLOW , DIGITAL | Mass Flow Indication RUW-MUS, Metering Skid 400FT620A. | 938683 | FL_MTR | M400FC620A | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ620A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/06/19 | MC-PM-002-Y1
939688 | M400FQ620B | INDICATOR, FLOW , DIGITAL | Mass Flow Indication RUW-MUS, Metering Skid 400-FT-620B | 938684 | FL_MTR | M400FC620B | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ620B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/06/19 | MC-PM-002-Y1
939689 | M400FQ620C | INDICATOR, FLOW , DIGITAL | Mass Flow Indication RUW-MUS Metering Skid 400-FT-620C | 938685 | FL_MTR | M400FC620C | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ620C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/06/19 | MC-PM-002-Y1
939690 | M400FQ771A | INDICATOR, FLOW , DIGITAL | mass flow indication for Metering Skid 400-FT-771A | 938686 | FL_MTR | M400FC771A | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ771A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/06/19 | MC-PM-002-Y1
939691 | M400FQ771B | INDICATOR, FLOW , DIGITAL | mass flow indication for Metering Skid 400-FT-771B | 938687 | FL_MTR | M400FC771B | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ771B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/06/19 | MC-PM-002-Y1
939692 | M400FQ772 | INDICATOR, FLOW , DIGITAL | mass flow indication for Metering Skid 400-FT-772 | 938688 | FL_MTR | M400FC772 | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ772-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/06/19 | MC-PM-002-Y1
939693 | M400FQ861A | INDICATOR, FLOW , DIGITAL | mass flow indication for Metering Skid 400-FT-861A | 938689 | FL_MTR | M400FC861A | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ861A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/08/18 | MC-PM-002-Y1
939694 | M400FQ861B | INDICATOR, FLOW , DIGITAL | mass flow indication forMetering Skid 400-FT-861B | 938690 | FL_MTR | M400FC861B | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FQ861B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/08/18 | MC-PM-002-Y1
939695 | M400LI301 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for ULG95 Tank 400T111 |  | TANKGAUG | M400T111 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI301-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/08/18 | MC-PM067.M6
939696 | M400LI302 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION ULG95 TANK 400-T-111 |  | TANKGAUG | M400T111 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939697 | M400LI304 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION ULG95 TANK 400-T-112 |  | TANKGAUG | M400T112 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939698 | M400LI305 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for ULG95 Tank 400-T-113 |  | TANKGAUG | M400T113 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI305-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/08/18 | MC-PM067.M6
939699 | M400LI306 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION ULG95 TANK 400-T-113 |  | TANKGAUG | M400T113 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939700 | M400LI307 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION ON ULG91 Tank 400-T-114 |  | TANKGAUG | M400T114 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI307-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/08/18 | MC-PM067.M6
939701 | M400LI308 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION ULG95 TANK 400-T-114 |  | TANKGAUG | M400T114 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939702 | M400LI309 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for ULG91 Tank 400-T-115 |  | TANKGAUG | M400T115 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI309-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/08/18 | MC-PM067.M6
939703 | M400LI310 | RADAR LOOP, LEVEL INDICATOR INSTRUMENT | RADAR LEVEL INDICATION ULG95 TANK 400-T-115 |  | TANKGAUG | M400T115 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939704 | M400LI311 | ENRAF LOOP, LEVEL INDICATOR INSTRUMENT | ENRAF LEVEL INDICATION for GASOIL Tank 400-T-116 |  | TANKGAUG | M400T116 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | High | CRITICAL | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400LI311-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/08/18 | MC-PM067.M6
969130788 | M400PP002 | DISTRIBUTION BOARD,LIGHTING, FIRE STATION, S/S-400 | 415V A.C. POWER PANEL AT FIRE STATION |  | LIGHT | M400SCB | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130789 | M400PP011 | DISTRIBUTION BOARD,LIGHTING, WAREHOUSE, 400-MCC-001 | 415V A.C.POWER PANEL AT WAREHOUSE |  | LIGHT | M400SCB | 3 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130790 | M400PP012 | DISTRIBUTION BOARD,LIGHTING, FIRE STATION, 400-MCC-001 | 415V A.C.POWER PANEL AT FIRE STATION |  | LIGHT | M400SCB | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130796 | M400MVP024 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-105 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP024-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
969130797 | M400MVP036 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD AT WWTP AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP036-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
XXX935445 | SALAINCP1IJ3 |  | INSULATION JOINT 3 AT KM 0.76(C.P.S.# 1 AT KM3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935461 | SALAINTP16 |  | TEST POINT # 16 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935477 | SALAINTP29 |  | TEST POINT # 30 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935492 | SALAINTP44 |  | TEST POINT # 44 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935510 | SALAINTP56 |  | TEST POINT # 56 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935526 | SALAINTP71 |  | TEST POINT # 71 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132754 | M400LSLL727 | SWITCH,LEVEL | LEVEL SWITCH EFFLUENT STORAGE TANK 1 |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132755 | M400LSLL731 | SWITCH,LEVEL | LEVEL SWITCH EFFLUENT STORAGE TANK - 2 |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132756 | M400LSLL734 | SWITCH,LEVEL | LEVEL SWITCH -EFFLUENT STORAGE TANK 3 |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132757 | M400LSLL737 | SWITCH,LEVEL | LEVEL SWITCH-INTERMEDIATE BUFFER TANK CHAIN - II |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132758 | M400LSLL745 | SWITCH,LEVEL | LEVEL SWITCH-INTERMEDIATE BUFFER TANK EFFLUENT POLISHING |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132759 | M400LT251 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL-CLEAR WATER TANK |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132760 | M400LT258 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL - OIL COLLECTING TANK |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132761 | M400LT261 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL- CHEMICAL SLUDGE TANK |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132762 | M400LT264 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL - OILY SLUDGE TANK |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132763 | M400LT701 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL - RECEIVING SUMP CHAIN I |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132764 | M400LT705 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL- INTERMEDIATE BUFFER TANK CHAIN-I |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132765 | M400LT717 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC | LEVEL CONTROL - POLYELECTROLYTE MAKE-UP UNIT |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132766 | M400LT721 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL-RECEIVING SUMP CHAIN-II |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132767 | M400LT725 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL-EFFLUENT STORAGE TANK-1 |  | LVL_TX | M400T210A | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132768 | M400LT729 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL- EFFLUENT STORAGE TANK-2 |  | LVL_TX | M400T210B | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132769 | M400LT732 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL-EFFLUENT STORAGE TANK-3 |  | LVL_TX | M400T210C | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132778 | M400PSLL719 | SWITCH,PRESSURE | PROCESS CONTROL AIR SUPPLY |  | PRES_SWT | M400WWTP | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132770 | M400LT735 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL-INTERMEDIATE BUFFER TANK CHAIN II |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132771 | M400LT743 | TRANSMITTER,LIQUID LEVEL, 4-20MA, 24VDC, YES | LEVEL CONTROL-INTERMEDIATE BUFFER TANK EFFLUENT POLISHING |  | LVL_TX | M400WWTPLEVEL | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132772 | M400PDT720 | TRANSMITTER,DIFFERENTIAL PRESSURE, 4-20MA, 24VDC, YES | DIFFERENTIAL PRESSURE CONTROL - SAFETY FILTER |  | PRES_TX | M400WWTP | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132773 | M400PDT747 | TRANSMITTER,DIFFERENTIAL PRESSURE, 4-20MA, 24VDC, YES | DIFFERENTIAL PRESSURE CONTROL-AC FILTER A |  | PRES_TX | M400WWTP | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132774 | M400PDT748 | TRANSMITTER,DIFFERENTIAL PRESSURE, 4-20MA, 24VDC, YES | DIFFERENTIAL PRESSURE CONTROL-AC FILTER B |  | PRES_TX | M400WWTP | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132775 | M400FSLL267 | TRANSMITTER,DIFFERENTIAL PRESSURE | FLOW CONTROL-OIL COLLECTING PUMPS |  | FL_SWT | M400WWTPFLOW | 1 | FL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132776 | M400FSLL297 | SWITCH,FLOW | FLOW CONTROLLER - AIR FLOW STRIPPER |  | FL_SWT | M400WWTPFLOW | 1 | FL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132777 | M400PSLL718 | SWITCH,PRESSURE | PRESSURE CONTROL-PROCESS WATER |  | PRES_SWT | M400WWTP | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132779 | M400TT740 | TRANSMITTER,TEMPERATURE | TEMPERATURE METER-EXHAUST AIR FROM STRIPPER |  | TEMP_TX | M400WWTP | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936495 | U29PT668 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 24V | PR.TRASMTR. 29-EOV-507 OUTLET | 939408 | PRES_TX | U29PI668 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936496 | U29PT669 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 24V | PR.TRASMTR. 29-EOV-507 OUTLET | 939409 | PRES_TX | U29PI669 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936497 | M400PT670 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 24V | PRESS. TRANSMTR. AT OUTLET LINE 400-PV-670 | 938870 | PRES_TX | M400PIC670 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936498 | U29PT671 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 24V | SRR Main Pumps 2937-JA/B/C to 2903-L/302-PL-002 Pr | 939412 | PRES_TX | U29PI671 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936594 | PL300TT30305B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L UPSTREAM 303-EOV-05 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30305B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-017-M2
936595 | PL300TT30306A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L DOWNSTREAM 303-EOV-06 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30306A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-017-M2
936596 | PL300TT30306B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L UPSTREAM 303-EOV-06 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30306B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-017-M2
936597 | M400FT001 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0-2 | FLOW TRANSMTR. 400-P-021A DISCHARGE | 939679 | DP_TXTR | M400FI001 | 2 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936598 | M400FT002 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0-2 | FLOW TRANSMTR. 400-P-021B DISCHARGE | 939680 | DP_TXTR | M400FI002 | 2 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936599 | M400FT003 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0-2 | FLOW TRANSMTR. 400-P-021C DISCHARGE | 939681 | DP_TXTR | M400FI003 | 2 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936600 | M400FT004 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0-2 | FLOW TRANSMTR. AT 400P022A/B TO 10T101/102/103 | 939682 | DP_TXTR | M400FI004 | 2 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936601 | M400FT008 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0-2 | 400-P-024A Disch. Flow transmittr to Gas Oil Tanks | 939683 | DP_TXTR | M400FI008 | 2 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936602 | M400FT009 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0-2 | DISCHARGE FLOW TX. OF 400P024B TO GAS OIL TANKS. | 939684 | DP_TXTR | M400FI009 | 2 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936603 | M400FT866 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0-2 | FLOW TRANSMTR.INLET LINE FIRE WATER TANK 400-T-201 |  | DP_TXTR | M400SYS | 2 | DP_TXTR | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FT866-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/04/19 | MC-PM-002-Y1
936604 | M400LT926 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-LEVEL , 0 | LEVEL TR. CORROSION INHIBITOR DOSING TANK 400-T-08 | 939725 | DP_TXTR | M400LI926 | 2 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400LT926-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/08/18 | MC-PM-004-Y1
936605 | M400PDT001 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. TRANSFER PUMP 400-P-021A STRAINER | 939727 | DP_TXTR | M400PDI001 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936606 | M400PDT002 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. TRANSFER PUMP 400-P-021B STRAINER | 939728 | DP_TXTR | M400PDI002 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936607 | M400PDT003 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. TRANSFER PUMP 400-P-021C STRAINER | 939729 | DP_TXTR | M400PDI003 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936608 | M400PDT004 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. TRANSFER PUMP 400-P-022A STRAINER | 939730 | DP_TXTR | M400PDI004 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936609 | M400PDT005 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. TRANSFER PUMP 400-P-022B STRAINER | 939731 | DP_TXTR | M400PDI005 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936610 | M400PDT008 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. TRANSFER PUMP 400-P-024A STRAINER | 939732 | DP_TXTR | M400PDI008 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936611 | M400PDT009 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. TRANSFER PUMP 400-P-024B STRAINER | 939733 | DP_TXTR | M400PDI009 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936612 | M400PDT531 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. COALESCER SEPARATR 400L003A FILTR | 939734 | DP_TXTR | M400PDI531 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDT531-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/02/19 | MC-PM-007-Y1
936613 | M400PDT532 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR.FILTR COALESCR SEPARATR 400L003B FILTR | 939735 | DP_TXTR | M400PDI532 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936614 | M400PDT546 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. BOOSTER PUMP 400-P-020 STRAINER | 939738 | DP_TXTR | M400PDI546 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936615 | M400PDT551 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. MAINLINE PUMP 400-P-019 STRAINER | 939739 | DP_TXTR | M400PDI551 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936616 | M400PDT751 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. BOOSTER PUMP 400-P-017A STRAINER | 939743 | DP_TXTR | M400PDI751 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936617 | M400PDT752 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. BOOSTER PUMP 400-P-017B STRAINER | 939744 | DP_TXTR | M400PDI752 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936618 | M400PDT753 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0- | DIFF.PR.TR.FILTR COALESCR SEPARATR 400L004A FILTR | 939745 | DP_TXTR | M400PDI753 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936619 | M400PDT754 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0- | DIFF.PR.TR.FILTR COALESCR SEPARATR 400L004B FILTR | 939746 | DP_TXTR | M400PDI754 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936620 | M400PDT801 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. MAINLINE PUMP 400-P-018A STRAINER | 939750 | DP_TXTR | M400PDI801 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936621 | M400PDT802 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0- | DIFF.PR.TR. MAINLINE PUMP 400-P-018B STRAINER | 939751 | DP_TXTR | M400PDI802 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936622 | M400PDT863 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. BOOSTER PUMP 400-P-015A STRAINER | 939754 | DP_TXTR | M400PDI863 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936623 | M400PDT864 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. BOOSTER PUMP 400-P-015B STRAINER |  | DP_TXTR | M400PDI864 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936624 | M400PDT881 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. MAINLINE PUMP 400-P-016A STRAINER |  | DP_TXTR | M400PDI881 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936625 | M400PDT882 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PR.TR. MAINLINE PUMP 400-P-016B STRAINER | 939758 | DP_TXTR | M400PDI882 | 2 | DP_TXTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936626 | M400PT001 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 8 , 4-20mA , 24V DC, 2 W | PRESS.TRANSMTR. TRANSFER PUMP P021A DISCHARGE LINE | 939643 | PRES_TX | M400PI001 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936627 | M400PT002 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 8 , 4-20mA , 24V DC, 2 W | PRESS.TRANSMTR. TRANSFER PUMP P021B DISCHARGE LINE | 939644 | PRES_TX | M400PI002 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936628 | M400PT003 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 8 , 4-20mA , 24V DC, 2 W | PRESS.TRANSMTR. TRANSFER PUMP P021C DISCHARGE LINE | 939645 | PRES_TX | M400PI003 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936629 | M400PT004 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 8 , 4-20mA , 24V DC, 2 W | PRESS.TRANSMTR. 400-P-022A DISCHARGE LINE | 939646 | PRES_TX | M400PI004 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936630 | M400PT005 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 8 , 4-20mA , 24V DC, 2 W | PRESS.TRANSMTR. 400-P-022B DISCHARGE LINE | 939647 | PRES_TX | M400PI005 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936631 | M400PT008 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-20 KG/CM2 , 4-20mA , 24V D | PRESS.TRANSMTR. AT 400-P-024A DISCHARGE LINE | 939648 | PRES_TX | M400PI008 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936632 | M400PT009 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-20 KG/CM2 , 4-20mA , 24V D | PRESS.TRANSMTR. AT 400-P-024B DISCHARGE LINE | 939649 | PRES_TX | M400PI009 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936633 | M400PT011 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PRESS.TRANSMTR. AT SUCTION LINE 400-P-021A | 939759 | PRES_TX | M400PI011 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936634 | M400PT012 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PRESS.TRANSMTR. AT SUCTION LINE 20-P-021B | 939760 | PRES_TX | M400PI012 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936635 | M400PT013 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PRESS.TRANSMTR. SUCTION LINE PRESS. AT 400-P-021C | 939761 | PRES_TX | M400PI013 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936636 | M400PT014 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PRESS.TRANSMTR. SUCTION LINE PRESSURE AT 20-P-022A | 939762 | PRES_TX | M400PI014 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936637 | M400PT015 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PRESS.TRANSMTR. SUCTION LINE PRESS.AT 400-P-022B | 939763 | PRES_TX | M400PI015 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936638 | M400PT018 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | SUCTION PRESS.TR. ON SLOP TRANSFER PUMP 400P024A. | 939764 | PRES_TX | M400PI018 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936639 | M400PT019 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PRESS. TR. SUCTION SLOP TRANSFER PUMP 400P024B | 939765 | PRES_TX | M400PI019 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936640 | M400PT203A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 25 , 4-20mA , 24V DC, 2 | PRESS.TRANSMTR. FIRE WATER(M400P203A) | 936409 | PRES_TX | M400P203A | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT203A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/02/19 | MC-PM-007-Y1
936641 | M400PT203B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 25 , 4-20mA , 24V DC, 2 | PRESS.TRANSMTR. FIRE WATER M400P203B) | 936410 | PRES_TX | M400P203B | 1 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT203B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 22/01/19 | MC-PM-007-Y1
936642 | M400PT501 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | Pressure transm. for ADR 10" Naphtha Reformate P/L | 939786 | PRES_TX | M400PI501 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936643 | M400PT504 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | Pr. tx. Between ADR 10" & Ruwais 10" Naphtha P/L | 939787 | PRES_TX | M400PI504 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936644 | M400PT505 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | Pr. tx. Between ADR 10" & Ruwais 10" Naphtha P/L | 939788 | PRES_TX | M400PI505 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936645 | M400PT508 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | Pr. transmittr for To/From Ruwais 10" Naphtha P/L | 939789 | PRES_TX | M400PI508 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936646 | M400PT531 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 50 , 4-20mA , 24V DC, 2 | PR.TR. JET A1 RECEIVING END NAPHTHA REFORMATE P/L | 938968 | PRES_TX | M400PIC531 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936647 | M400PT532 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 20 , 4-20mA , 24V DC, 2 | PRESS. TR. INLET TO FLOW METERING SKID 400-FT-541 | 939791 | PRES_TX | M400PI532 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936648 | M400PT533 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 20 , 4-20mA , 24V DC, 2 | PRESS. TR. INLET TO FLOW METERING SKID 400-FT-541 | 939792 | PRES_TX | M400PI533 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936649 | M400PT534 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 20 , 4-20mA , 24V DC, 2 | PRESS. TR. INLET TO FLOW METERING SKID 400-FT-541 | 939793 | PRES_TX | M400PI534 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936650 | M400PT536 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PR.TR. JET A1 RECEIVING END NAPHTHA REFORMATE P/L | 938868 | PRES_TX | M400PIC536 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936651 | M400PT545 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 4-20MA , | PR.TR. JET A1 FROM STORAGE TANK TO BOOSTER PUMP | 939797 | PRES_TX | M400PI545 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936652 | M400PT547 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , (-1)-(+3) KG/CM2 , 24V DC, 2 | PR.TR. SUCTION LINE BOOSTER PUMP 400-P-020 | 939798 | PRES_TX | M400PI547 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936653 | M400PT550 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-12 KG/CM2, 0-70.3 KG/CM2 , | PR.TR. DISCHARGE LINE BOOSTER PUMP 400-P-020 | 939800 | PRES_TX | M400PI550 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939063 | M400TE425A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Casing For Pump 400-P-016B | 939167 | TEMP_ELE | M400TI425A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939064 | M400TE426A | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Pump Radial Bearing N.D.E. For Pump 400-P-016B | 939168 | TEMP_ELE | M400TI426A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939065 | M400TE426B | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | TEMP. ELEMENT. AT NON DRIVE END OF 400P16B. | 939169 | TEMP_ELE | M400TI426B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939066 | M400TE427A | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Thrust Bearing D.E. For Pump 400-P-016B | 939170 | TEMP_ELE | M400TI427A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939067 | M400TE427B | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Thrust Bearing D.E. For Pump 400-P-016B | 939171 | TEMP_ELE | M400TI427B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939068 | M400TE428A | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C | Thrust Bearing N.D.E. For Pump 400-P-016B | 939172 | TEMP_ELE | M400TI428A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939069 | M400TE428B | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C | Thrust Bearing N.D.E. For Pump 400-P-016B | 939173 | TEMP_ELE | M400TI428B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939070 | M400TE429C | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Lube Oil Header Temp. For Pump 400-P-016B | 939174 | TEMP_ELE | M400TI429C | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939071 | M400TE461 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'U' Winding For Pump 400-P-019 | 939175 | TEMP_ELE | M400TI461 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939072 | M400TE462 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'U' Winding For Pump 400-P-019 | 939176 | TEMP_ELE | M400TI462 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939073 | M400TE463 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'V' Winding For Pump 400-P-019 | 939177 | TEMP_ELE | M400TI463 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939074 | M400TE463C | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Lube Oil Heater Tripped for 400-P-019 | 939178 | TEMP_ELE | M400TI463C | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939075 | M400TE464 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'V' Winding For Pump 400-P-019 | 939179 | TEMP_ELE | M400TI464 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939076 | M400TE465 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'W' Winding For Pump 400-P-019 | 939180 | TEMP_ELE | M400TI465 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939077 | M400TE466 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'W' Winding For Pump 400-P-019 | 939181 | TEMP_ELE | M400TI466 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939078 | M400TE467A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing NCE For Pump 400-P-019 | 939182 | TEMP_ELE | M400TI467A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939079 | M400TE467B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing NCE For Pump 400-P-019 | 939183 | TEMP_ELE | M400TI467B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939080 | M400TE468A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing CE For Pump 400-P-019 | 939184 | TEMP_ELE | M400TI468A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939081 | M400TE468B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing CE For Pump 400-P-019 | 939185 | TEMP_ELE | M400TI468B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939082 | M400TE469A | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Pump Radial Bearingd D.E. For Pump 400-P-019 | 939186 | TEMP_ELE | M400TI469A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939084 | M400TE470A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , DOUBLE RTD, 3-WIRE , 100 OHM @ | Casing For Pump 400-P-019 | 939189 | TEMP_ELE | M400TI470A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939085 | M400TE471A | ELEMENT, TEMPERATURE, THERMOSTATIC , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG C , | Pump Radial Bearing N.D.E. For Pump 400-P-019 | 939190 | TEMP_ELE | M400TI471A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939086 | M400TE471B | ELEMENT, TEMPERATURE, THERMOSTATIC , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG C , | Pump Radial Bearing N.D.E. For Pump 400-P-019 | 939191 | TEMP_ELE | M400TI471B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939087 | M400TE472A | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Thrust Bearing D.E. For Pump 400-P-019 | 939192 | TEMP_ELE | M400TI472A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939088 | M400TE472B | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Thrust Bearing D.E. For Pump 400-P-019 | 939193 | TEMP_ELE | M400TI472B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939089 | M400TE473A | ELEMENT, TEMPERATURE, THERMOSTATIC , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C , P | Thrust Bearing N.D.E. For Pump 400-P-019 | 939194 | TEMP_ELE | M400TI473A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939090 | M400TE473B | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C | Thrust Bearing N.D.E. For Pump 400-P-019 | 939195 | TEMP_ELE | M400TI473B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939092 | M400TE301 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. for ULG 95 Tank 400-T-111 | 939123 | TANKGAUG | M400TI301 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939093 | M400TE303 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp. for ULG 95 Tank 400-T-112 | 939124 | TANKGAUG | M400TI303 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939094 | M400TE305 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp for ULG 95 Tank 400-T-113 | 939125 | TANKGAUG | M400TI305 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939095 | M400TE307 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp for ULG 95 Tank 400-T-114 | 939126 | TANKGAUG | M400TI307 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939096 | M400TE309 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Temp for ULG 95 Tank 400-T-115 | 939127 | TANKGAUG | M400TI309 | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37096 | UNISSAN27534 | 10-27534 NISSAN PATROL. | NISSAN PATROL 10-27534. |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UNISSAN27534-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 01/08/18 | MM-PM-029-M1
937812 | M400RO032 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937813 | M400RO033 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937814 | M400RO034 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937815 | M400RO035 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937816 | M400RO036 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937817 | M400RO037 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937818 | M400RO038 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937819 | M400RO039 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937820 | M400RO040 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937821 | M400RO051 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937822 | M400RO052 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937823 | M400RO053 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937824 | M400RO290 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937825 | M400RO291 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937826 | M400RO292 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131422 | M400FACP003 | PANEL,FIRE ALARM, MINERVA | FIRE ALARM CONTROL PANEL AT FIRE STATION P&TD. |  | F&G_PNL | MFIRE | 1 | F&G_PNL | 617101-310510 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FACP003-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/09/18 | MFPS-PM01.M3
969131424 | M400FACP005 | PANEL,FIRE ALARM, MINERVA | FIRE ALARM CONTROL PANEL AT WARE HOUSE P&TD. |  | F&G_PNL | MWH | 1 | F&G_PNL | 617101-310510 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FACP005-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 10/09/18 | MFPS-PM01.M3
939469 | M400T203 | O/H WATER STORAGE TANK ON CONTROL ROOM | O/H WATER STORAGE TANK ON CONTROL ROOM |  | TK |  | 3 | TK | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 1 | 1 | 1 | 5 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131426 | M400FSP002 | PANEL,FIRE ALARM, ANSUL, ANALOG ADDRESSABLE RELEASE & FIRE ALARM SYSTEM. | FIRE SUPPRESSION PANEL AT MTERMINAL SUB STATION BUILDING |  | F&G_PNL | M400FACP002 | 1 | F&G_PNL | 617101-310510 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FSP002-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 15/09/18 | MFPS-PM10.M3
939481 | M400T204 | O/H WATER STORAGE TANK ON FIRE STATION | O/H WATER STORAGE TANK ON FIRE STATION |  | TK |  | 3 | TK | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 1 | 1 | 1 | 5 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939482 | M400T201 | FIRE WATER STORAGE TANK | FIRE WATER STORAGE TANK |  | TK | M400TANKS | 1 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | High | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939483 | M400T205 | O/H WATER STORAGE ON WAREHOUSE | O/H WATER STORAGE ON WAREHOUSE |  | VESSEL |  | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 1 | 1 | 1.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939484 | M400T206 | O/H WATER STORAGE ON GATEHOUSE | O/H WATER STORAGE ON GATEHOUSE |  | VESSEL |  | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 1 | 1 | 1.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939487 | M400T207 | O/H WATER STORAGE ON SUBSTATION | O/H WATER STORAGE ON SUBSTATION |  | VESSEL |  | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 1 | 1 | 1.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939499 | M400T210A | EFFLUENT STORAGE TANKS | OILY WATER EFFLUENT TANK WWTP IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939500 | M400T210B | OILY WATER EFFLUENT TANK IRP MUSSAFFAH TERMINAL. | OILY WATER EFFLUENT TANK WWTP IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939501 | M400T210C | OILY WATER EFFLUENT TANK IRP MUSSAFFAH TERMINAL. | OILY WATER EFFLUENT TANK WWTP IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Very High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59172 | M50PI187W | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-107 | TNK56616 | INDICATR | M10T107 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59173 | M50PI203F | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-107 | TNK56616 | INDICATR | M10T107 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59174 | M50PI223F | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-107 | TNK56616 | INDICATR | M10T107 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59191 | M50PI178W | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-108 | TNK56634 | INDICATR | M10T108 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59192 | M50PI188W | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-108 | TNK56634 | INDICATR | M10T108 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59208 | M50PI179W | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-109 | TNK56645 | INDICATR | M10T109 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59209 | M50PI199W | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-109 | TNK56645 | INDICATR | M10T109 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59227 | M50PI180W | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-110 | TNK56656 | INDICATR | M10T110 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59228 | M50PI190W | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-110 | TNK56656 | INDICATR | M10T110 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59252 | M40PI076 | GAUGE, PRESSURE, 0-40 KG/CM2 , 150MM , 1/2" , 316 SS , COPPER ALLOY , 316 SS , B | PRESSURE INDICATOR FOR SLOPS LOADING PUMP 172 ADNOC DIST. | PMC56668 | INDICATR | M40P172 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59255 | M40PI077 | GAUGE, PRESSURE, 0-25 KG/CM2 , 150MM , 1/2" , 316 SS , COPPER ALLOY , 316 SS , B | PRESSURE INDICATOR FOR SLOPS LOADING PUMP 173 ADNOC DIST. | PMC56670 | INDICATR | M40P173 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59024 | M10TE302 | THERMOCOUPLE, RESISTANCE , 6MM OD , 316 SS , 1/2" MNPT | RTD FOR MULTI PRODUCT INLET METERING SKID | IIF59021 | TEMP_ELE | M10FQRAL302 | 2 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59038 | M10TE011 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-101 | IIT59039 | TANKGAUG | M10TT011 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59039 | M10TT011 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , INTRINSICALLY SAFE | TEMPERATURE TRANSMITTER FOR TANK T-101 | TNK56513 | TANKGAUG | M10T101 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59060 | M10TE021 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-102 | IIT59061 | TANKGAUG | M10TT021 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59061 | M10TT021 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , INTRINSICALLY SAFE | TEMPERATURE TRANSMITTER FOR TANK T-102 | TNK56531 | TANKGAUG | M10T102 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59082 | M10TE031 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-103 | IIT59083 | TANKGAUG | M10TT031 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59083 | M10TT031 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , INTRINSICALLY SAFE | TEMPERATURE TRANSMITTER FOR TANK T-103 | TNK56547 | TANKGAUG | M10T103 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59102 | M10TE041 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-104 | IIT59103 | TANKGAUG | M10TT041 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59103 | M10TT041 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , INTRINSICALLY SAFE | TEMPERATURE TRANSMITTER FOR TANK T-104 | TNK56565 | TANKGAUG | M10T104 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59122 | M10TE051 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-105 | IIT59123 | TANKGAUG | M10TT051 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59123 | M10TT051 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , INTRINSICALLY SAFE | TEMPERATURE TRANSMITTER FOR TANK T-105 | TNK56585 | TANKGAUG | M10T105 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59142 | M10TE061 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-106 | IIT59143 | TANKGAUG | M10TT061 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59143 | M10TT061 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , CENELEC ATEX FLAME-PRO | TEMPERATURE TRANSMITTER FOR TANK T-106 | TNK56600 | TANKGAUG | M10T106 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59162 | M10TE071 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-107 | IIT59163 | TANKGAUG | M10TT071 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59163 | M10TT071 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , CENELEC ATEX FLAME-PRO | TEMPERATURE TRANSMITTER FOR TANK T-107 | TNK56616 | TANKGAUG | M10T107 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59184 | M10TE081 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-108 | IIT59185 | TANKGAUG | M10TT081 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59185 | M10TT081 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , CENELEC ATEX FLAME-PRO | TEMPERATURE TRANSMITTER FOR TANK T-108 | TNK56634 | TANKGAUG | M10T108 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59201 | M10TE091 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-109 | IIT59202 | TANKGAUG | M10TT091 | 2 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 50 | 10 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59202 | M10TT091 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , CENELEC ATEX FLAME-PRO | TEMPERATURE TRANSMITTER FOR TANK T-109 | TNK56645 | TANKGAUG | M10T109 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59219 | M10TE101 | ELEMENT, TEMPERATURE, TANK GAUGING SYSTEM , SINGLE RTD , -20 TO 90 DEG C , COPPE | MULTI THERMO COUPLE ELEMENTS FOR TANK T-110 | IIT59220 | TEMP_ELE | M10TT101 | 2 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59220 | M10TT101 | TRANSMITTER, TEMPERATURE, RTD , 4-20MA , M20X1.5 , ALUM , CENELEC ATEX FLAME-PRO | TEMPERATURE TRANSMITTER FOR TANK T-110 | TNK56656 | TANKGAUG | M10T110 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59275 | M10TW301 | THERMOWELL, 1-1/2" 300 LB RF FLANGE , 316 SS | THERMOWELL FOR MULTI PRODUCT INLET METERING SKID. | IIT59020 | TERM_WEL | M10TE301 | 2 | TERM_WEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIT59277 | M10TW302 | THERMOWELL, 1-1/2" 300 LB RF FLANGE , 316 SS | THERMOWELL FOR MULTI PRODUCT INLET METERING SKID | IIT59024 | TERM_WEL | M10TE302 | 2 | TERM_WEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939231 | M400VE403Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing D.E. 400-P-016A |  | VIBRE_TX | M400VI403Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939232 | M400VE404X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing N.D.E. 400-P-016A |  | VIBRE_TX | M400VI404X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939233 | M400VE404Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing N.D.E. 400-P-016A |  | VIBRE_TX | M400VI404Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939234 | M400VT405 | PROBE, VIBRATION , 8MM , 0.5 M | Pump Housing For 400-P-016A |  | VIBRE_TX | M400VI405 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939235 | M400VE416X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing NCE for 400-P-016B | 939253 | VIBRE_TX | M400VI416X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939236 | M400VE416Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing NCE for 400-P-016B | 939254 | VIBRE_TX | M400VI416Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939237 | M400VE461X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing NCE for 400-P-019 | 939264 | VIBRE_TX | M400VI461X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939238 | M400VE461Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing NCE for 400-P-019 | 939265 | VIBRE_TX | M400VI461Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939239 | M400VE462X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing CE for 400-P-019 | 939266 | VIBRE_TX | M400VI462X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939240 | M400VE462Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing CE for 400-P-019 | 939267 | VIBRE_TX | M400VI462Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939241 | M400VE463X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing D.E. 400-P-019 | 939268 | VIBRE_TX | M400VI463X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939242 | M400VE463Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing D.E. 400-P-019 | 939269 | VIBRE_TX | M400VI463Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939243 | M400VE464X | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing N.D.E. 400-P-019 | 939270 | VIBRE_TX | M400VI464X | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939244 | M400VE464Y | PROBE, VIBRATION , 8MM , 0.5 M | Main E-MOTOR Radial Bearing N.D.E. 400-P-019 | 939271 | VIBRE_TX | M400VI464Y | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939245 | M400VI401X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing NCE for 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI401X-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/10/18 | MC-PM-012-M3
939246 | M400VI401Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing NCE for M400P016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI401Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/10/18 | MC-PM-012-M3
939247 | M400VI402X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing CE for 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI402X-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/10/18 | MC-PM-012-M3
939248 | M400VI402Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing CE for 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI402Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/10/18 | MC-PM-012-M3
939249 | M400VI403X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing D.E. 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI403X-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/10/18 | MC-PM-012-M3
939250 | M400VI403Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing D.E. 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI403Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/10/18 | MC-PM-012-M3
939251 | M400VI404X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing N.D.E. 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI404X-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/10/18 | MC-PM-012-M3
939252 | M400VI404Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing N.D.E. 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI404Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/10/18 | MC-PM-012-M3
939253 | M400VI416X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing NCE for 400-P-016B | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI416X-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/10/18 | MC-PM-012-M3
939254 | M400VI416Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing NCE for 400-P-016B | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI416Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/10/18 | MC-PM-012-M3
939255 | M400VI417X | INDICATOR, REMOTE VIBRATION | MAIN MOTOR RADIAL BEARING D.E (M400P016B) | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI417X-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/08/18 | MC-PM-012-M3
939256 | M400VI417Y | INDICATOR, REMOTE VIBRATION | (M400P016B) MAIN MOTOR RADIAL BEARING D.E | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI417Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/08/18 | MC-PM-012-M3
939257 | M400VI418X | INDICATOR, REMOTE VIBRATION | (M400P016B) MAIN MOTOR RADIAL BEARING D.E | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI418X-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/08/18 | MC-PM-012-M3
939258 | M400VI418Y | INDICATOR, REMOTE VIBRATION | (M400P016B) MAIN MOTOR RADIAL BEARING D.E | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI418Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/08/18 | MC-PM-012-M3
939259 | M400VI419X | INDICATOR, REMOTE VIBRATION | (M400P016B) MAIN MOTOR RADIAL BEARING N.D.E | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI419X-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939260 | M400VI419Y | INDICATOR, REMOTE VIBRATION | (M400P016B) MAIN MOTOR RADIAL BEARING N.D.E | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI419Y-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/08/18 | MC-PM-012-M3
939261 | M400VI405 | INDICATOR, REMOTE VIBRATION | Pump Housing REMOTE VIBRATION INDICATOR, FOR 400-P-016AFor 400-P-016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI405-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 15/10/18 | MC-PM-012-M3
939262 | M400VI420 | INDICATOR, REMOTE VIBRATION | COMPRESSOR CASING FOR M400P016B | 935827 | VIBRE_TX | M400P016B | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI420-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/08/18 | MC-PM-012-M3
939263 | M400VI465 | INDICATOR, REMOTE VIBRATION | COMPRESSOR CASING FOR M400P019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI465-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939264 | M400VI461X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing NCE for 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI461X-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939265 | M400VI461Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing NCE for 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI461Y-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939266 | M400VI462X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing CE for 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI462X-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939267 | M400VI462Y | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing CE for 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI462Y-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
939268 | M400VI463X | INDICATOR, REMOTE VIBRATION | Main E-MOTOR Radial Bearing D.E. 400-P-019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400VI463X-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
XXX935612 | SMTP13 |  | TEST POINT# 13 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935478 | SALAINTP30 |  | TEST POINT # 30 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935479 | SALAINTP31 |  | TEST POINT # 31 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131784 | M400XMC001 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-101 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC001-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131785 | M400XMC002 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-101 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC002-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131788 | M400XMC005 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-103 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC005-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131789 | M400XMC006 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-103 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC006-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131791 | M400XMC012 | DUPLICATE OF M50XMC-------CALL POINT, BREAK GLASS MANUAL, 15V MIN/30V MAX, RED, YES | MANUAL CALL POINT NEAR TANK T-104 |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XMC012-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131932 | MQ600XAC003 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT SCADA ROOM MAQTA TERMINAL |  | PB_HS-MC | MQ600FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XAC003-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131935 | MQ600XHD201A | DETECTOR,FIRE PROTECTION, RATE OF RISE HEAT, YES | LINEAR HEAT DETECTOR FOR SUMP TANK AT MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XHD201A-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM05.M3
969131936 | MQ600XHD201B | DETECTOR,FIRE PROTECTION, RATE OF RISE HEAT, YES | LINEAR HEAT DETECTOR FOR SUMP TANK AT MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XHD201B-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM05.M3
969131942 | MQ600XSP005 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131944 | MQ600XSP007 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131161 | M400LP006R603 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131170 | M400LP006B201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT CONTROL ROOM SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131202 | M400LP006Y401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT EAST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131203 | M400LP006Y402 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT EAST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131204 | M400LP006R401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SOUTH BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131205 | M400LP008R501 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SOUTH BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131206 | M400LP008Y501 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SOUTH BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131207 | M400LP008B501 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SOUTH BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131208 | M400LP008R502 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SOUTH BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNK56513 | M10T101 | TANK, GAS OIL , N/A , N/A , API 650 , API 650 , (VACUUM/MAX) MBAR G : -2.5 / 7. | GASOIL TANK - 30,000 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | M10T101-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/08/18 | ME-PM-003-Y1
TNK56531 | M10T102 | TANK, GAS OIL , N/A , N/A , API 650 , API 650 , (VACUUM/MAX) -2.5 / 7.5 MBAR G | GASOIL TANK - 30,000 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T102-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 23/09/18 | ME-PM-003-Y1
TNK56547 | M10T103 | TANK, GAS OIL , N/A , N/A , API 650 , API 650 , (VACUUM/MAX ) -2.5 / 7.5 MBAR | GASOIL TANK - 30,000 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T103-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/08/18 | ME-PM-003-Y1
TNK56565 | M10T104 | TANK, GAS OIL , N/A , N/A , API 650 , API 650 , ATMOSPHERIC KG/CM2 | GAS OIL TANK -15000 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T104-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/08/18 | ME-PM-003-Y1
TNK56585 | M10T105 | TANK, GAS OIL 97 (OCTANE) , N/A , N/A , API 650 , API 650 , ATMOSPHERIC KG/CM2 | ULG 95 OCTANE TANK -15000 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T105-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/08/18 | ME-PM-003-Y1
TNK56600 | M10T106 | TANK, GAS OIL 90 , N/A , N/A , API 650 , API 650 , NA -ATMOSPHERIC KG/CM2, 10/85 | ULG 91 OCTANE TANK -10,000 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T106-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 05/09/18 | ME-PM-003-Y1
TNK56616 | M10T107 | TANK, GAS OLINE 90 (OCTANE) , N/A , N/A , API 650 , API 650 , NA-ATMOSPHERIC PRE | 98-OCTANE TANK -10,000 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T107-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 06/09/18 | ME-PM-003-Y1
TNK56634 | M10T108 | TANK, KEROSENE / SLOPS STORAGE , N/A , N/A , API 650 , API 650 , (VACUUM / MAX | KEROSENE TANK - 750 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T108-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 07/09/18 | ME-PM-003-Y1
TNK56645 | M10T109 | TANK, KEROSENE / SLOPS STORAGE TANK , N/A , N/A , API 650 , API 650 , (VACUUM / | KEROSENE TANK - 750 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T109-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 08/09/18 | ME-PM-003-Y1
TNK56656 | M10T110 | TANK, KEROSENE / SIOPS STORAGE TANK , N/A , N/A , API 650 , API 650 , VACUUM / M | SLOPS TANK - 750 M3 |  | TK | M10TANKS | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | M10T110-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 09/09/18 | ME-PM-003-Y1
VVS935269 | M10OGV-102 | OUTLET GATE VALVE - 16" | OUTLET GATE VALVE - 16" FOR TANK T - 102 |  | VALVE | M10T102 | 3 | VALVE | 617101-310600 | MTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935457 | SALAINTP12 |  | TEST POINT # 12 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935473 | SALAINTP25 |  | TEST POINT # 25 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935488 | SALAINTP40 |  | TEST POINT # 40 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935506 | SALAINTP52 |  | TEST POINT # 52 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935522 | SALAINTP67 |  | TEST POINT # 67 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935539 | SALAINTP82 |  | TEST POINT # 82 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935556 | SALAINTP96 |  | TEST POINT # 96 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935573 | SADIATP4 |  | TEST POINT# 4 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935589 | SADIATP20 |  | TEST POINT# 20 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935605 | SMTP6 |  | TEST POINT# 6 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935621 | SMTP22 |  | TEST POINT# 22 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935635 | SMTP37 |  | TEST POINT# 37 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935651 | SMLPGTP6 | CP TEST POINT | TEST POINT # 6 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935666 | SMLPGTP21 | CP TEST POINT | TEST POINT # 21 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935681 | SMLPGTP36 | CP TEST POINT | TEST POINT # 36 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935466 | SALAINTP18 |  | TEST POINT # 18 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935628 | SMTP29 |  | TEST POINT# 29 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935643 | SMTP45 | ???????????????? | TEST POINT# 45 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935658 | SMLPGTP13 | CP TEST POINT | TEST POINT # 13 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935674 | SMLPGTP29 | CP TEST POINT | TEST POINT # 29 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935689 | SMLPGTP44 | CP TEST POINT | TEST POINT # 44 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131801 | M400XAC208 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC208-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 04/10/18 | MFPS-PM07.M3
969131805 | M400XAC212 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC212-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 09/10/18 | MFPS-PM07.M3
969131806 | M400XAC213 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC213-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 11/10/18 | MFPS-PM07.M3
969131802 | M400XAC209 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC209-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 04/10/18 | MFPS-PM07.M3
969131803 | M400XAC210 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC210-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 09/10/18 | MFPS-PM07.M3
969131804 | M400XAC211 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT TANK FARM AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC211-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 26/07/18 | MFPS-PM07.M3
969131807 | M400XAC216 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT SCRAPPER AREA |  | PB_HS-MC | M400TMR001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC216-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 11/10/18 | MFPS-PM07.M3
SSV935314 | M10NRVI104 | INLET NON-RETURN VALVE - 10" | INLET NON-RETURN VALVE- 10" FOR TANK T-104 |  | VALCH | M10NRVI-104 | 3 | VALCH | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SSV935257 | M10NRVO102 | OUTLET NON-RETURN VALVE -16" | OUTLET NON-RETURN VALVE -16" FOR TANK T - 102 |  | VALCH | M10TANKS | 3 | VALCH | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969165718 | M410MP007A | ULG 91/95 INTER-TANK TRANSFER PUMP MOTOR | MOTOR FOR ULG 91/95 INTER-TANK TRANSFER PUMP 7-A |  | MOTOR | M410P007A | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP007A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 27/11/18 | ME-PM-HT1-6M
969165719 | M410MP007B | ULG 91/96 INTER-TANK TRANSFER PUMP MOTOR | MOTOR FOR ULG 91/95 INTER-TANK TRANSFER PUMP 7-B |  | MOTOR | M410P007B | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP007B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 28/11/18 | ME-PM-HT1-6M
969269341 | M410BAV21243037 | 8" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 8" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269342 | M410BAV21243046 | 8" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 8" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269343 | M410BAV21243050 | 8" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 8" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269344 | M410FFE2101309 | 9 kg BC DCP Fire Extinguisher (Indoor) | 9 kg BC DCP Fire Extinguisher (Indoor) |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269345 | M410PG763A | A/B TOWER & PURGE PRESSURE GAUGE | A/B TOWER & PURGE PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269346 | M410PG763B | A/B TOWER & PURGE PRESSURE GAUGE | A/B TOWER & PURGE PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969257164 | M410P007B | SEAL FLUSH SYSTEM FOR ULG 91/95 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP | 969147447 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 11/11/18 | MM-PM-7-Y1
969257166 | M410P008A | SEAL FLUSH SYSTEM FOR GAS OIL INTER-TANK TRANSFER PUMP | GAS OIL INTER-TANK TRANSFER PUMP | 969147449 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-4-Y1
969257167 | M410P008B | SEAL FLUSH SYSTEM FOR GAS OIL INTER-TANK TRANSFER PUMP | GAS OIL INTER-TANK TRANSFER PUMP | 969147450 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 11/11/18 | MM-PM-4-Y1
VVS56536 | M10PSV025 | VALVE SAFETY RELIEF | PRESSURE RELIEF VALVE FOR OUTLET TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56548 | M10PSV031 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 KG/CM2 , N | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-103 |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56549 | M10PSV032 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 KG/CM2 , N | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-103 |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56550 | M10PSV033 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-103 |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56551 | M10PSV034 | VALVE SAFETY RELIEF | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-103 |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56552 | M10PSV035 | VALVE SAFETY RELIEF | PRESSURE RELIEF VALVE FOR OUTLET TANK T-103 |  | PSV | M10T103 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56566 | M10PSV041 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-104 |  | PSV | M10T104 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56567 | M10PSV042 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/CM | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-104 |  | PSV | M10T104 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56568 | M10PSV043 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-104 |  | PSV | M10T104 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56569 | M10PSV044 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/CM | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-104 |  | PSV | M10T104 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56570 | M10PRV041A | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-104 |  | PSV | M10T104 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56571 | M10PRV041B | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-104 |  | PSV | M10T104 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56572 | M10PRV041C | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-104 |  | PSV | M10T104 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56573 | M10PSV052 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/CM | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-105 |  | PSV | M10T105 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56574 | M10PSV054 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/CM | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-105 |  | PSV | M10T105 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56575 | M10PSV051 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-105 |  | PSV | M10T105 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56576 | M10PSV053 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/CM | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-105 |  | PSV | M10T105 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56586 | M10PRV051A | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-105 |  | PSV | M10T105 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56587 | M10PRV051B | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-105 |  | PSV | M10T105 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56588 | M10PRV051C | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-105 |  | PSV | M10T105 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56601 | M10PSV061 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 90 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-106 |  | PSV | M10T106 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56602 | M10PSV062 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-106 |  | PSV | M10T106 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56603 | M10PSV064 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 90 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/CM | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-106 |  | PSV | M10T106 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56603_1 | M10PSV063 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 90 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-106 |  | PSV | M10T106 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56604 | M10PRV061A | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-106 |  | PSV | M10T106 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56605 | M10PRV061B | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-106 |  | PSV | M10T106 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56606 | M10PRV061C | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-106 |  | PSV | M10T106 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56617 | M10PSV071 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 90 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-107 |  | PSV | M10T107 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56618 | M10PSV072 | VALVE, SAFETY RELIEF, THERMAL , 90 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/CM2 , N/ | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-107 |  | PSV | M10T107 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56619 | M10PSV073 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 90 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-107 |  | PSV | M10T107 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56620 | M10PSV074 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 90 OCTANE , 1" X 1" , 150 LB , 5.0 KGF/C | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-107 |  | PSV | M10T107 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56621 | M10PRV071A | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-107 |  | PSV | M10T107 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56622 | M10PRV071B | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-107 |  | PSV | M10T107 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56623 | M10PRV071C | VALVE SAFETY RELIEF | PRESSURE/VACUUM RELIEF VALVE FOR TANK T-107 |  | PSV | M10T107 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56635 | M10PSV081 | VALVE, SAFETY RELIEF, THERMAL RELIEF , KEROSENE , 1" X 1" , 300 LB , 30 KG/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-108 |  | PSV | M10T108 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56636 | M10PSV082 | VALVE, SAFETY RELIEF, THERMAL RELIEF , KEROSENE , 1" X 1" , 150 LB , 5.0 KGF/CM2 | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-108 |  | PSV | M10T108 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56637 | M10PSV083 | VALVE, SAFETY RELIEF, THERMAL RELIEF , KEROSENE , 1" X 1" , 300 LB , 30 KG/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-108 |  | PSV | M10T108 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56638 | M10PSV084 | VALVE SAFETY RELIEF | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-108 |  | PSV | M10T108 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56639 | M10PRV085 | VALVE SAFETY RELIEF | PRESSURE RELIEF VALVE FOR OUTLET TANK T-108 |  | PSV | M10T108 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56640 | M10PVRV081A | VALVE, SAFETY RELIEF, FIG 700 : 6" , KEROSENE , 6" , FLANGED , SS AISI 316 , PL | VACUUM RELIEF VALVE FOR TANK T-108 |  | PSV | M10T108 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56641 | M10PVRV081B | VALVE, SAFETY RELIEF, FIG 700 , KEROSENE , 6" , FLANGED , SS AISI 316 , PLAIN LI | VACUUM RELIEF VALVE FOR TANK T-108 |  | PSV | M10T108 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56646 | M10PSV091 | VALVE, SAFETY RELIEF, THERMAL RELIEF , SLOPS , 1" X 1" , 300 LB , 30 KG/CM2 , N/ | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-109 |  | PSV | M10T109 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56647 | M10PSV092 | VALVE, SAFETY RELIEF, THERMAL RELIEF , SLOPS , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-109 |  | PSV | M10T109 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56648 | M10PSV093 | VALVE, SAFETY RELIEF, THERMAL RELIEF , SLOPS , 1" X 1" , 300 LB , 30 KG/CM2 , N/ | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-109 |  | PSV | M10T109 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56649 | M10PSV094 | VALVE, SAFETY RELIEF, THERMAL RELIEF , SLOPS , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-109 |  | PSV | M10T109 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56650 | M10PRV095 | VALVE SAFETY RELIEF | PRESSURE RELIEF VALVE FOR OUTLET TANK T-109 |  | PSV | M10T109 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56651 | M10PVRV091A | VALVE, SAFETY RELIEF, FIG 700 , KEROSENE , 6" , FLANGED , SS AISI 316 , PLAIN LI | VACUUM RELIEF VALVE FOR TANK T-109 |  | PSV | M10T109 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56652 | M10PVRV091B | VALVE, SAFETY RELIEF, FIG 700 , KEROSENE/SLOPS , 6" , FLANGED , SS AISI 316 , PL | VACUUM RELIEF VALVE FOR TANK T-109 |  | PSV | M10T109 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56657 | M10PSV101 | VALVE, SAFETY RELIEF, THERMAL RELIEF , SLOPS , 1" X 1" , 300 LB , 30 KG/CM2 , N/ | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-110 |  | PSV | M10T110 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56658 | M10PSV102 | VALVE, SAFETY RELIEF, THERMAL RELIEF , SLOPS , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-110 |  | PSV | M10T110 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56659 | M10PSV103 | VALVE, SAFETY RELIEF, THERMAL RELIEF , SLOPS , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-110 |  | PSV | M10T110 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56660 | M10PSV104 | VALVE, SAFETY RELIEF | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-110 |  | PSV | M10T110 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56661 | M10PRV105 | VALVE SAFETY RELIEF | PRESSURE RELIEF VALVE FOR OUTLET TANK T-110 |  | PSV | M10T110 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56662 | M10PVRV101A | VALVE, SAFETY RELIEF, FIG 700 , KEROSEN /SLOPS , 6" , FLANGED , SS AISI 316 , PL | VACUUM RELIEF VALVE FOR TANK T-110 |  | PSV | M10T110 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIS59231 | M10TB227 | TELEPHONE, Ex. PROOF , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Very High | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIS59232 | M10TB228 | TELEPHONE, Ex. PROOF , BUTTON , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIS59233 | M10TB229 | TELEPHONE, Ex. PROOF , BUTTON , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIS59234 | M10TB230 | TELEPHONE, Ex. PROOF , BUTTON , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIS59235 | M10TB231 | TELEPHONE, Ex. PROOF , BUTTON , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIS59236 | M10TB232 | TELEPHONE, Ex. PROOF , BUTTON , TONE/PULSE , BLACK | TELEPHONE BOOTH SYSTEM FOR PRODUCT TANKS AREA |  | TELEPHON | M10TELEPHONE | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132031 | PL300BATT001A | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-A =38 Nos FOR SV-1. |  | BATTERY | PL300BAT001 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132032 | PL300BATT001B | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V | BATTERY BANK-B =38 Nos FOR SV-1. |  | BATTERY | PL300BAT001 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132033 | PL300BATT002A | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V | BATTERY BANK-A =38 Nos FOR SV-2. |  | BATTERY | PL300BAT002 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FTP56669 | M40FLT002 | FILTER FOR SLOPS LOADING PUMP 172 | FILTER FOR SLOPS LOADING PUMP 172 ADNOC DIST. |  | CLN_FLTR | M40P172 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FTP56671 | M40FLT001 | FILTER FOR SLOPS LOADING PUMP 172 | FILTER FOR SLOPS LOADING PUMP 172 ADNOC DIST. |  | CLN_FLTR | M40P173 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935586 | SADIATP17 |  | TEST POINT# 17 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935587 | SADIATP18 |  | TEST POINT# 18 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935588 | SADIATP19 |  | TEST POINT# 19 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271731 | M410STR004A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271732 | M410STR004B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271733 | M410STR005A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271741 | M410STR023C | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271730 | M410STR003B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184930 | M410AHU101B | HVAC SYSTEM | HVAC SYSTEM |  | HVAC_FLT | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184931 | M410AHU201A | HVAC SYSTEM | HVAC SYSTEM |  | HVAC_FLT | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184932 | M410AHU201B | HVAC SYSTEM | HVAC SYSTEM |  | HVAC_FLT | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184933 | M410AHU301A | HVAC SYSTEM | HVAC SYSTEM |  | HVAC_FLT | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184934 | M410AHU301B | HVAC SYSTEM | HVAC SYSTEM |  | HVAC_FLT | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184935 | M410FT150A | 410-P-009 DISCHARGE | FLOW TX ULG/GAS OIL SUMP PUMP 410-P-009 DISCHARGE |  | FL_MTR | M410P009 | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184936 | M410FT150B | 410-P-009 DISCHARGE | FLOW TX ULG/GAS OIL SUMP PUMP 410-P-009 DISCHARGE |  | FL_MTR | M410P009 | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184937 | M410FT151A | 410-P-010 DISCHARGE | FLOW TX JET A1 SUMP PUMP 410-P-010 DISCHARGE |  | FL_MTR | M410P010 | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184938 | M410FT151B | 410-P-010 DISCHARGE | FLOW TX JET A1 SUMP PUMP 410-P-010 DISCHARGE |  | FL_MTR | M410P010 | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184939 | M410FT201A | 410-P-008A DISCHARGE | FLOW TX GAS OIL 410-P-008A DISCHARGE |  | FL_MTR | M410P008A | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184940 | M410FT201B | 410-P-008B DISCHARGE | FLOW TX GAS OIL 410-P-008B DISCHARGE |  | FL_MTR | M410P008B | 3 | FL_MTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184941 | M410FT250A | 410-P-014A DISCHARGE | JET A1 ITT LINE 410-P-014A DISCHARGE. |  | FL_MTR | M410P014A | 3 | FL_MTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184942 | M410FT250B | 410-P-014B DISCHARGE | JET A1 ITT LINE 410-P-014B DISCHARGE. |  | FL_MTR | M410P014B | 3 | FL_MTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184943 | M410FT251A | JET A1 FROM MPH2 PUMPS DISCH | JET A1 FROM MPH2 PUMPS DISCH |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184944 | M410FT251B | JET A1 FROM MPH2 PUMPS DISCH | JET A1 FROM MPH2 PUMPS DISCH |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184945 | M410FT701B | 410-P-007A DISCHARGE | FLOW TX ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A DISCHARGE |  | FL_MTR | M410P007A | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184946 | M410FT702A | 410-P-007B DISCHARGE | FLOW TX ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B DISCHARGE |  | FL_MTR | M410P007B | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184947 | M410FT703A | 410-P-007C DISCHARGE | FLOW TX ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C DISCHARGE |  | FL_MTR | M410P007C | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184948 | M410FT703B | 410-P-007C DISCHARGE | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C DISCHARGE |  | FL_MTR | M410P007C | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184949 | M410MCM001 | MCM SYSTEM | MCM SYSTEM |  |  | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184950 | M410MCM002 | MCM NETWORK SERVER | MCM NETWORK SERVER |  | TELECOM | M410PCH | 3 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184951 | M410PFI001A1A | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001A1A-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 23/10/18 | ME-PM-005-Y1
969184952 | M410PFI001A2A | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001A2A-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 24/10/18 | ME-PM-005-Y1
969184953 | M410PFI001A3A | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001A3A-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 25/10/18 | ME-PM-005-Y1
969184954 | M410PFI001A4A | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001A4A-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 26/10/18 | ME-PM-005-Y1
969184955 | M410PFI001B1B | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001B1B-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 28/10/18 | ME-PM-005-Y1
969184956 | M410PFI001B2B | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001B2B-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 29/10/18 | ME-PM-005-Y1
969184957 | M410PFI001B3B | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001B3B-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 30/10/18 | ME-PM-005-Y1
969184958 | M410PFI001B4B | Power Capacitor Bank | Power Capacitor Bank |  | BATTERY | M410BATT | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001B4B-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 31/10/18 | ME-PM-005-Y1
969195499 | M410FU404 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195500 | M410FU405 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195501 | M410FU406 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195502 | M410FU407 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195503 | M410FU408 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195504 | M410FU409 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195505 | M410FU410 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195506 | M410FU411 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR 410T015 AREA. |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932798 | M400BD11311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932799 | M400BD13511051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932800 | M400BD13611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932801 | M400BD13711051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932802 | M400BD13811051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932803 | M400BD17411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932804 | M400BD17511051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932805 | M400BD18911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932806 | M400BD19011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932807 | M400BD20911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932808 | M400BD21011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932809 | M400BD22911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932810 | M400BD23011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , FLANGED , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932811 | M400BD26111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932812 | M400BD26211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932813 | M400BD26311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932814 | M400BD26411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932815 | M400BD28311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932816 | M400BD28411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932817 | M400BD28511051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932818 | M400BD28611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932819 | M400BD31411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932820 | M400BD31511051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932821 | M400BD32911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932822 | M400BD34911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932823 | M400BD35011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932824 | M400BD37111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932825 | M400BD37211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932826 | M400BD37311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932827 | M400BD37411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932828 | M400BD39311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932829 | M400BD39411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932830 | M400BD39511051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932831 | M400BD39611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933846 | PL300VA10BV900 | VALVE BALL | M/P, BALL VALVE, 10" 900 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933847 | PL300VA10CH1500 | VALVE CHECK | STOP CHECK VALVE, 10" 1500 LB(Y-GLOBE VALVE) |  | VALCH | PL300VALVE | 3 | VALCH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933848 | PL300VA12BV600 | VALVE BALL | SRR, BALL VALVE, 12" 600 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933849 | PL300VA2BV300 | VALVE BALL | JET A1, BALL VALVE, 2" 300 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933850 | PL300VA2BV600 | VALVE BALL | JET A1, BALL VALVE, 2" 600 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933851 | PL300VA2BV900 | VALVE BALL | M/P, BALL VALVE, 2" 900 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933852 | PL300VA4BV600 | VALVE BALL | N/R, BALL VALVE, 4" 600 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933853 | PL300VA4BV900 | VALVE BALL | M/P, BALL VALVE, 4"X3" 900 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933854 | PL300VA8BV600 | VALVE BALL | SRR, BALL VALVE, 8"X6" 600 LB |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933855 | M400VA4BV300 | VALVE BALL | JET A1, BALL VALVE, 4"X3" 300 LB |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933856 | M400VA4BV600 | VALVE BALL | N/R, BALL VALVE, 4"X3" 600 LB |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933857 | M400VA4BV900 | VALVE BALL | M/P, BALL VALVE, 4"X3" 900 LB |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933858 | M400VA8BV600 | VALVE BALL | SRR, BALL VALVE, 8"X6" 600 LB |  | VALVE | M400VALVE | 3 | VALVE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933859 | MQ600VA4BV900 | VALVE BALL | M/P, BALL VALVE, 4"X3" 900 LB |  | VALVE | MQ600VALVE | 3 | VALVE | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933863 | AT800VA4BV300 | VALVE BALL | JET A1 PIPE LINE,BALL VALVE, 4"X3" 300 LB |  | VALVE | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 5 | 5 | 5 | 1 | 50 | 50 | 5.4949 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933867 | M400UPSDC001 | DC POWER SUPPLY UNINTERRUPTED | POWER SUPPLY |  | INVRT_UP | M400BATT | 1 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400UPSDC001-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 09/12/18 | ME-PM-017-M6
933868 | MQ600UPSDC001 | POWER SUPPLY, SUPPLY-SWITCHGEAR CONTROL AND INSTRM.SYSTEM, 4.8KVA, 65 dBA, ********, 48V, N/A, 4.8KW, 100, =< 2%, 61 VDCV, 42.6 VDCV, N/AV, ********, 415V, 3, 10AMP, 28%, ********, N/AV, N/A, N/AAMP, ********, 48V, 100AMP, 8HOUR, 54V, 55.1V, N/AV, 42.6 VDCV, 36V | SUPPLY TO SWITCHGEAR CONTROL AND INSTRUMENT.SYSTEM |  | INVRT_UP | MQ600BATT | 2 | INVRT_UP | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600UPSDC001-ME1 | INACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-017-M6
933874 | M400P015A | PUMP, CENTRIFUGAL, VERTICAL, VS 6 , ULG95/ULG98/GAS OIL/JET A1/KEROSENE , SEPARA | ULG95/GAS OIL/JET A1/KEROSENE BOOSTER PUMP- AL AIN |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P015A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/10/18 | MM-PM-007-M6
933875 | M400P015B | PUMP, CENTRIFUGAL, VERTICAL, VS 6 , ULG95/ULG98/GAS OIL/JET A1/KEROSENE , SEPARA | ULG95/ULG98/GAS OIL/JET A1/KEROSENE BOOSTER PUMPS |  | PUCE | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | m | 0 | N | N | 0 | 0 | 0 | M400P015B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/11/18 | MM-PM-007-M6
933876 | M400P017A | PUMP, CENTRIFUGAL, HOR OH2 , JET A1 , CENTERLINE , 1 , INDUCTION MOTOR , 1484 RP | JET A1 BOOSTER PUMP-A TO ADIA. |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P017AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/10/18 | MM-PM-004-M6
933877 | M400P017B | PUMP, CENTRIFUGAL, HOR OH2 , JET A1 , CENTERLINE , 1 , INDUCTION MOTOR , 1484 RP | JET A1 BOOSTER PUMP-B TO ADIA. |  | PUCE | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P017BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/11/18 | MM-PM-004-M6
933878 | M400P020 | PUMP, CENTRIFUGAL, HOR OH2 , OFF SPEC JET A1 , CENTERLINE , INDUCTION MOTOR , 14 | OFF SPEC JET A1 BOOSTER PUMP TO RUWAIS. |  | PUCE | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P020MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/12/18 | MM-PM-001-M6
933883 | AA13VA1GA091 | GATE VALVE | GATE VALVE, 1" 800 LB SW |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933884 | AA13VA112GA091 | GATE VALVE | GATE VALVE, 1-1/2" 800 LB SW |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933885 | AA13VA34GA091 | GATE VALVE, 3/4" 800 LB, SW | GATE VALVE, 3/4" 800 LB, SW |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933886 | AA13VA34GA092 | GATE VALVE, 3/4" 800 LB, SW+NPT | GATE VALVE,3/4" 800 LB, SW+NPT |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933887 | AA13VA34GL091 | GLOBE VALVE, 3/4" 800 LB, SW | GLOBE VALVE, 3/4" 800 LB, SW |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933914 | PL300VA12GA092 | GATE VALVE | GATE VALVE, 1/2" 800 LB, SW+NPT |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933915 | PL300VA12GA191 | GATE VALVE | GATE VALVE, 1/2" 1500LB, SW |  | VALVE | PL300VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933916 | M400VA1CH091 | VALVE CHECK | CHECK VALVE, 1" 800 LB, SW |  | VALCH | M400VALVE | 3 | VALCH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933917 | M400VA1CH093 | VALVE CHECK | CHECK VALVE, 1" 800 LB,SW |  | VALCH | M400VALVE | 3 | VALCH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933918 | M400VA1GA091 | GATE VALVE | GATE VALVE, 1" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933919 | M400VA1GA095 | GATE VALVE | GATE VALVE, 1" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933920 | M400VA1GA191 | GATE VALVE | GATE VALVE, 1" 1500 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933921 | M400VA1GA192 | GATE VALVE | GATE VALVE, 1" 1500 LB, BW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933922 | M400VA112GA091 | GATE VALVE | GATE VALVE, 1-1/2" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933923 | M400VA112GA095 | GATE VALVE | GATE VALVE, 1-1/2" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933924 | M400VA12GA091 | GATE VALVE | GATE VALVE, 1/2" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933925 | M400VA12GA092 | GATE VALVE | GATE VALVE, 1/2" 800 LB, SW+NPT |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933926 | M400VA12GA096 | GATE VALVE | GATE VALVE, 1/2" 800 LB, SW+NPT |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933927 | M400VA12GA097 | GATE VALVE | GATE VALVE, 1/2" 800 LB, SW+NPT |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933928 | M400VA12GA191 | GATE VALVE | GATE VALVE, 1/2"1500 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935489 | SALAINTP41 |  | TEST POINT # 41 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935490 | SALAINTP42 |  | TEST POINT # 42 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935491 | SALAINTP43 |  | TEST POINT # 43 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935622 | SMTP23 |  | TEST POINT# 23 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935623 | SMTP24 |  | TEST POINT# 24 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935507 | SALAINTP53 |  | TEST POINT # 53 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935508 | SALAINTP54 |  | TEST POINT # 54 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935509 | SALAINTP55 |  | TEST POINT # 55 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935523 | SALAINTP68 |  | TEST POINT # 68 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935524 | SALAINTP69 |  | TEST POINT # 69 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935525 | SALAINTP70 |  | TEST POINT # 70 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935540 | SALAINTP83 |  | TEST POINT # 83 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935541 | SALAINTP84 |  | TEST POINT # 84 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935542 | SALAINTP85 |  | TEST POINT # 85 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131691 | M400XLF202 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE FOR TRANSFER PUMP AREA |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131698 | M400XHD201B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-015A |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD201B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/08/18 | MFPS-PM05.M3
969131699 | M400XHD202A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-015B |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD202A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/08/18 | MFPS-PM05.M3
969131701 | M400XHD203A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-016A |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD203A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM05.M3
969131702 | M400XHD203B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-016A |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD203B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM05.M3
969265862 | PL100ACBATT001B | Battery for 100-UPS-AC-001B | Battery for 100-UPS-AC-001B |  | BATTERY | PL100BATT | 3 | BATTERY | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265864 | PL100AE001A | Air Eliminator for Custody Transfer Metering System (Flow Meter) | Air Eliminator for Custody Transfer Metering System (Flow Meter) |  | VESSEL | PL100VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 50 | 5 | 5 | 1 | 1 | 3.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265865 | PL100AE001B | Air Eliminator for Custody Transfer Metering System (Flow Meter) | Air Eliminator for Custody Transfer Metering System (Flow Meter) |  | VESSEL | PL100VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 50 | 5 | 5 | 1 | 1 | 3.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278943 | PL318CCTV152 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278944 | PL318CCTV153 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278945 | PL318CCTV154 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278946 | PL318CCTV155 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278947 | PL318CCTV156 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278948 | PL318CCTV157 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278949 | PL318CCTV158 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278950 | PL318CCTV159 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278951 | PL318CCTV160 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278952 | PL318CCTV161 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278953 | PL318CCTV162 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278959 | PL318TEL002 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278960 | PL318TEL003 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278961 | PL318TEL004 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278962 | PL318TEL005 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278963 | PL321CCTV001 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278964 | PL321CCTV002 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278965 | PL321CCTV003 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278966 | PL321CCTV004 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278967 | PL321CCTV005 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278968 | PL321CCTV006 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278969 | PL321CCTV007 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278970 | PL321CCTV008 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278971 | PL321CCTV009 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278972 | PL321CCTV010 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278973 | PL321CCTV011 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278974 | PL321CCTV012 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278975 | PL321CCTV013 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278976 | PL321CCTV014 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278977 | PL321CCTV015 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278978 | PL321CCTV016 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278979 | PL321CCTV017 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278980 | PL321CCTV018 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278981 | PL321CCTV019 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278982 | PL321CCTV020 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278983 | PL321CCTV021 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278984 | PL321CCTV022 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278985 | PL321CCTV023 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278986 | PL321CCTV024 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278987 | PL321CCTV025 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278988 | PL321CCTV026 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278989 | PL321CCTV027 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL321TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278990 | PL324CCTV001 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278991 | PL324CCTV002 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278992 | PL324CCTV003 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278993 | PL324CCTV004 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278994 | PL324CCTV005 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278995 | PL324CCTV006 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278996 | PL324CCTV007 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278997 | PL324CCTV008 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278998 | PL324CCTV009 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL324TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278999 | PL325CCTV001 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279000 | PL325CCTV002 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279001 | PL325CCTV003 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279002 | PL325CCTV004 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279003 | PL325CCTV005 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279004 | PL325CCTV006 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279005 | PL325CCTV007 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279006 | PL325CCTV008 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279007 | PL325CCTV009 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279008 | PL325CCTV010 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279009 | PL325CCTV011 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279010 | PL325CCTV012 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279011 | PL325CCTV013 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279012 | PL325CCTV014 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279013 | PL325CCTV015 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279014 | PL325CCTV016 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279015 | PL325CCTV017 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279016 | PL325CCTV018 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279017 | PL325CCTV019 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279018 | PL325CCTV020 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279019 | PL325CCTV021 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL325TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279021 | PL325TEL001 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL325MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936334 | M400LMK016A3 | MOTOR, ELECTRIC, - , II 3 G Eex Na II T3 , 0.55KW , 50HZ , 415V , S1 , IP55 , IM | MOTOR FOR SEAL OIL COOLER FAN 'A' FOR 400MP016A |  | MOTOR | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016A3-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/10/18 | ME-PM-014-M6
936335 | M400LMK016A4 | MOTOR, ELECTRIC, - , II 3 G Eex Na II T3 , 0.55KW , 50HZ , 415V , S1 , IP55 , IM | MOTOR FOR SEAL OIL COOLER FAN 'B' FOR 400MP016A |  | MOTOR | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016A4-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/10/18 | ME-PM-014-M6
936336 | M400LMK016B3 | MOTOR,ELECTRIC, DE SIDE COOLER FAN MOTOR, II 3 G Eex Na II T3, 0.55KW, 50HZ, 415V, S1, IP55, AMGK 090LB 5A, IM B3, 945RPM, 3, STAR, OHM, F, 18KG, SAE, ****, V, AMP | MOTOR FOR SEAL OIL COLLER FAN 'A' FOR 400MP016B |  | MOTOR | M400P016B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016B3-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/11/18 | ME-PM-014-M6
936337 | M400LMK016B4 | MOTOR,ELECTRIC, NDE SIDE COOLER FAN MOTOR, II 3 G Eex Na II T3, 0.55KW, 50HZ, 415V, S1, IP55, 090LB-06A, IM B3, 945RPM, 3, STAR, AMP, OHM, F, 18KG, SAE, ****, V, AMP | MOTOR FOR SEAL OIL COOLER FAN 'B' FOR 400MP016B |  | MOTOR | M400P016B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016B4-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/11/18 | ME-PM-014-M6
936338 | M400LMK018A3 | MOTOR,ELECTRIC, SEAL OIL COOLER FAN 'A' FOR M400MP018A, II 3 G Eex Na II T3, 0.55KW, 50HZ, 415V, S1, IP55, AMGK-090LB-06A, 6205-2ZC3, IM B3, 945RPM, 3, OHM, F, 18KG, SAE, ****, V, M400-PC-001, AMP | MOTTOR FOR SEAL OIL COOLER FAN 'A' FOR 400MP018A |  | MOTOR | M400P018A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M400LMK018A3-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/10/18 | ME-PM-014-M6
936339 | M400LMK018A4 | MOTOR,ELECTRIC, SEAL OIL COOLER FAN 'B' FOR M400MP018A, II 3 G Eex Na II T3, 0.55KW, 50HZ, 415V, S1, IP55, AMGK 090LB-06A, 6205-2Z C3, IM B3, 945RPM, 3, OHM, F, 18KG, SAE, ****, V, M400-PC-001, AMP | MOTOR FOR SEAL OIL COOLER FAN 'B' FOR 400MP016A |  | MOTOR | M400P018A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M400LMK018A4-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/10/18 | ME-PM-014-M6
936499 | U29PT672 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-150 KG/CM2 , 4-20mA , 10-3 | PR.TRANSM.SCRAPER LAUNCHER 2903L- SV STATN-7 SRR | 939413 | PRES_TX | U29PI672 | 2 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937022 | M400MCM001 | MACHINE MONITORING SYSTEM | MACHINE MONITORING SYSTEM |  | MCM_PNL | M400MOTOR | 1 | MCM_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937027 | M400MCMRACK1 | SYSTEM, MACHINE CONDITION MONITORING | VIBRATION AND TEMP. OF 400-P-016 A |  | MCM_PNL | M400MCM001 | 1 | MCM_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937028 | M400MCMRACK2 | SYSTEM, MACHINE CONDITION MONITORING | VIBRATION AND TEMP. OF 400-P-016 B |  | MCM_PNL | M400MCM001 | 1 | MCM_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937029 | M400MCMRACK3 | SYSTEM, MACHINE CONDITION MONITORING | VIBRATION AND TEMP. OF 400-P-019 |  | MCM_PNL | M400MCM001 | 1 | MCM_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56546 | M50SPR102 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-102 |  | F_N_S | M10T102 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56564 | M50SPR103 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-103 |  | F_N_S | M10T103 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56584 | M50SPR104 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-104 |  | F_N_S | M10T104 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56599 | M50SPR105 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-105 |  | F_N_S | M10T105 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56615 | M60SPR106 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-106 |  |  | M10T106 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56633 | M50SPR107 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-107 |  | F_N_S | M10T107 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56643 | M50SPR108 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-108 |  | F_N_S | M10T108 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56654 | M50SPR109 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-109 |  | F_N_S | M10T109 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFS56665 | M50SPR110 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-110 |  | F_N_S | M10T110 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMC56138 | SALAIN12DTP101 | Circulation Pump | CIRCULATION PUMP (DENSITY MEASURING STN AT 147 KM) |  | PUCE | SALAINDMS1 | 3 | PUCE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PMC56668 | M40P172 | PUMP, CENTRIFUGAL, ECP J 32-160 , SLOPS PUMP , SLOP , 0.7-1 , CL , SIZE & TYPE:E | SLOPS TRANSFER PUMP AT ADNOC DIST. |  | PUCE | M40UTILITY | 2 | PUCE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M40P172-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/08/18 | MM-PM-037-M6
PMC56670 | M40P173 | PUMP, CENTRIFUGAL, ECP J 32-160 , SL0PS PUMP , SLPO , 0.7-1 , CL , SIZE & TYPE : | SLOPS TRANSFER PUMP AT ADNOC DIST. |  | PUCE | M40UTILITY | 2 | PUCE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M40P173-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 18/09/18 | MM-PM-037-M6
932934 | M400ME003 | PACKAGE | TANK FOR RED DYE INJECTION IN ULG-91. |  | PACKAGE | M400CINJ | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932935 | M400ME001BV001 | VALVE BALL | BALL VALVE, 2X1-1/2" 300#RF, RB |  | VALVE | M400ME001 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932936 | M400ME001BV002 | VALVE BALL | BALL VALVE, 2X1-1/2" 150#RF, RB |  | VALVE | M400ME001 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932937 | M400ME001BV003 | VALVE BALL | BALL VALVE, 1X3/4" 150#RF, RB |  | VALVE | M400ME001 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932938 | M400ME001BV004 | VALVE BALL | BALL VALVE, 1/2X3/8" 150 # RF, RB |  | VALVE | M400ME001 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932939 | M400ME001BV005 | VALVE BALL | BALL VALVE, 1/2X3/8" 400#NPTF, RB |  | VALVE | M400ME001 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932940 | M400ME002BV001 | VALVE BALL | BALL VALVE, 2X1-1/2" 300#RF, RB |  | VALVE | M400ME002 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932941 | M400ME002BV002 | VALVE BALL | BALL VALVE, 2X1-1/2" 150#RF, RB |  | VALVE | M400ME002 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932942 | M400LG754 | GAUGE, LEVEL, MAGNETIC , 1200MM , 2" X 300LB RF FLANGED , 3.5 BAR G @ 87 DEG C , | MAGNETIC LEVEL GAUGE FOR BLUE DYE TANK | 932934 | INDICATR | M400ME003 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932943 | M400LG755 | GAUGE, LEVEL, MAGNETIC , 1400MM , 2" X 300LB RF FLANGED , 3.5 BAR G @ 87 DEG C , | MAGNETIC LEVEL GAUGE FOR GREEN DYE TANK | 932933 | INDICATR | M400ME002 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932944 | M400FT012 | METER, FLOW | FLOW TRANSMETER FOR ANTISTATIC CHEMICAL DOSING PKG |  | FL_TX | M400ME001 | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FT012-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/08/18 | MC-PM-001-Y1
932945 | M400FT013 | FLOW METER, MICRO MOTION | FLOW METER FOR RED DYE INJECTION PKG ULG-91 | 932934 | FL_TX | M400ME003 | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | M400FT013-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 31/08/18 | MC-PM-001-Y1
932946 | M400FT014 | METER, FLOW | FLOW METER FOR GREEN DYE INJECTION PKG ULG-95 |  | FL_TX | M400ME002 | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | M400FT014-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/08/18 | MC-PM-001-Y1
932947 | M400LG753 | GAUGE, LEVEL, MAGNETIC , 1200MM , 2" X 300LB RF FLANGED , 3.5 BAR G @ 87 DEG C , | MAGNETIC LEVEL GAUGE FOR ANTISTATIC TANK | 932932 | INDICATR | M400ME001 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932948 | M400ME002BV003 | VALVE BALL | BALL VALVE, 1X3/4" 150#RF, RB |  | VALVE | M400ME002 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932949 | M400ME002BV004 | VALVE BALL | BALL VALVE, 1/2X3/8" 150#RF, RB |  | VALVE | M400ME002 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932950 | M400ME002BV005 | VALVE BALL | BALL VALVE, 1/2X3/8" 400#NPTF, RB |  | VALVE | M400ME002 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932951 | M400ME003BV001 | VALVE BALL | BALL VALVE, 2X1-1/2" 300#RF, RB |  | VALVE | M400ME003 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932952 | M400ME003BV002 | VALVE BALL | BALL VALVE, 2X1-1/2" 150#RF, RB |  | VALVE | M400ME003 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932953 | M400ME003BV003 | VALVE BALL | BALL VALVE, 1X3/4" 150#RF, RB |  | VALVE | M400ME003 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932954 | M400ME003BV004 | VALVE BALL | BALL VALVE, 1/2X3/8" 150#RF, RB |  | VALVE | M400ME003 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932955 | M400ME003BV005 | VALVE BALL | BALL VALVE, 1/2X3/8" 400#NPTF, RB |  | VALVE | M400ME003 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932956 | M400P081A | PUMP, METERING, 4.2 L/HR, 9 BAR, 415V 0.25KW MOTOR. | ANTISTATIC CHEMICAL DOSING PUMP A. |  | PURE | M400ME001 | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 3 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P081A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-009-M6
932957 | M400P081B | PUMP, METERING , 4.2 L/HR , 9 BAR , 415V 0.25KW MOTOR | ANTISTATIC CHEMICAL DOSING PUMP B. |  | PURE | M400ME001 | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P081B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/08/18 | MM-PM-009-M6
932958 | M400P082A | PUMP, METERING , 7.5 L/HR , 9 BAR , 415V 0.25KW MOTOR | GREEN DYE CHEMICAL DOSING PUMP A. |  | PURE | M400ME002 | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P082A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-009-M6
932959 | M400P082B | PUMP, METERING , 7.5 L/HR , 9 BAR , 415V 0.25KW MOTOR | GREEN DYE CHEMICAL DOSING PUMP B. |  | PURE | M400ME002 | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P082B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/08/18 | MM-PM-009-M6
932960 | M400P083A | PUMP, METERING , 7.5 L/HR , 9 BAR , 415V 0.25KW MOTOR | RED DYE CHEMICAL DOSING PUMP A. |  | PURE | M400ME003 | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P083A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-009-M6
932961 | M400P083B | PUMP, METERING , 7.5 L/HR , 9 BAR , 415V 0.25KW MOTOR | RED DYE CHEMICAL DOSING PUMP B. |  | PURE | M400ME003 | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P083B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 04/08/18 | MM-PM-009-M6
932962 | M400PDI950A | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , 1/2" FNPT , 304 SS , NiCrCo | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400ME001 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI950A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/08/18 | MC-PM-011-M3
932963 | M400PDI951 | GAUGE DIFFERENTIAL PRESSURE | DIFF PRESSURE GAUGE |  |  | M400ME001 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI951-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/09/18 | MC-PM-011-M3
932964 | M400PDI952 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , 1/2 NPTFIN , 304 SS , NiCrC | DIFF PRESSURE GAUGE |  |  | M400ME003 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI952-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/09/18 | MC-PM-011-M3
932965 | M400PDI953 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , 1/2" FNPTIN , 304 SS , NiCr | DIFF PRESSURE GAUGE | 932934 |  | M400ME003 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI953-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 23/09/18 | MC-PM-011-M3
932966 | M400PDI954 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , 1/2" FNPTIN , 304 SS , NiCr | DIFF PRESSURE GAUGE |  |  | M400ME002 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI954-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 15/09/18 | MC-PM-011-M3
932967 | M400PDI955 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , 1/2" FNPTIN , 304 SS , NiCr | DIFF PRESSURE GAUGE |  |  | M400ME002 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI955-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 21/09/18 | MC-PM-011-M3
932968 | M400PG601 | GAUGE, PRESSURE, 0-0.6 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L SS , 316L SS , | PRESSURE GAUGE (M400ME001) | 932932 |  | M400ME001 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932969 | M400PG602 | GAUGE, PRESSURE, DIRECT , 0-16 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L SS , 3 | PRESSURE GAUGE FOR ANTI STATIC PACKAGE (M400ME001) | 932932 |  | M400ME001 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932970 | M400PG603 | GAUGE, PRESSURE, DIRECT , 0-16 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L SS , 3 | PRESSURE GAUGE (M400ME002) | 932933 |  | M400ME002 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932971 | M400PG604 | GAUGE, PRESSURE, DIRECT , 0-0.6 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L SS , | PRESSURE GAUGE (M400ME002) | 932933 |  | M400ME002 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932972 | M400PG605 | GAUGE, PRESSURE, BOURDON TUBE , 0-16 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L | PRESSURE GAUGE (M400ME003) | 932934 |  | M400ME003 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932973 | M400PG606 | GAUGE, PRESSURE, BOURDON TUBE , 0-16 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L | PRESSURE GAUGE (M400ME003) | 932934 |  | M400ME003 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932974 | M400PG607 | GAUGE, PRESSURE, BOURDON TUBE , 0-16 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L | PRESSURE GAUGE (M400ME002) | 932933 |  | M400ME002 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932975 | M400PG608 | GAUGE, PRESSURE, BOURDON TUBE , 0-0.6 KG/CM2 , 100MM , 1/2" NPTM , 304 SS , 316L | PRESSURE GAUGE (M400ME002) | 932932 |  | M400ME002 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932976 | M400PG609 | GAUGE, PRESSURE, BOURDON TUBE , 0-16 KG/CM2 , 100MM , 1/2" MNPT , 304 SS , 316L | INJECT GREEN DYE IN :PRESSURE GAUGE (M400ME002) | 932933 |  | M400ME002 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932977 | M400PSV651 | VALVE RELIEF | PRESURE RELIEF VALVE |  | PSV | M400ME001 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932978 | M400PSV652 | VALVE RELIEF | PRESURE RELIEF VALVE |  | PSV | M400ME001 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932979 | M400PSV653 | VALVE RELIEF | PRESURE RELIEF VALVE FOR DISCHRGE LINE |  | PSV | M400ME003 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932980 | M400PSV654 | VALVE RELIEF | PRESURE RELIEF VALVE FOR DISCHRGE LINE |  | PSV | M400ME003 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932981 | M400PSV655 | VALVE RELIEF | PRESURE RELIEF VALVE FOR DISCHRGE LINE |  | PSV | M400ME002 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932982 | M400PSV656 | VALVE RELIEF | PRESURE RELIEF VALVE FOR DISCHRGE LINE |  | PSV | M400ME002 | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932988 | M400TG576 | THERMOMETER, DIAL, CAPILLARY , 0-100 DEG C , 455MM , 100MM , 1/2" NPT , BOTTOM , | SUMP TANK 400-V-175 LIQUID TEMPERATURE |  |  | M400TEMP | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932992 | AT800TG101 | THERMOMETER DIAL | MUSSAFAH ADIA JET A1 P/L TO STORAGE TANKS |  |  | AT800TEMP | 4 | PIPES | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 5 | 1 | 1.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932993 | M400ME351 | SHOWER, EYE WASH SAFETY | PERSONNEL PROTECTION-EYE WASH SHOWER |  |  | M400MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Non Critical | Low | Medium | Y | High Critical | Y | 0 | 6 | o | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932994 | M400ME352 | SHOWER, EYE WASH SAFETY | PERSONNEL PROTECTION-EYE WASH SHOWER |  |  | M400MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Non Critical | Low | Medium | Y | High Critical | Y | 0 | 6 | o | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933006 | M400P204A | Potable Water pump FOR PIT TANK 400V117. | Potable Water pump FOR PIT TANK 400V117. |  | PUCE | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P204A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/08/18 | MM-PM-035-M6
933007 | M400P204B | PUMP, CENTRIFUGAL | Potable Water pump FOR PIT TANK 400V117. |  | PUCE | M400PUMP | 2 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P204B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/09/18 | MM-PM-035-M6
933010 | M400P075 | PUMP, SUBMERSIBLE, 20 M3/HR , SINGLE , 17.7 M , 2980 RPM , 50-85 DEG C , 1.0 KG/ | Sump Pump SRR Pipeline |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P075-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 09/12/18 | MM-PM-034-M6
933011 | M400P076 | PUMP, SUBMERSIBLE, 20 M3/HR , 2 , 54.2 M , 2980 RPM , 13-45 DEG C , 1.0 KG/CM2 , | Sump Pump Multi Product Pipeline |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P076-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/01/19 | MM-PM-034-M6
933012 | MQ600G077 | PUMP, CENTRIFUGAL, Vertical Submersible , Sump Pump , Slops , 0.794 - 0.912 , Sp | Sump Pump Mussafah Alain Multi Product Pipeline |  | PUCE | MQ600PUMP | 3 | PUCE | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933015 | M20FV161 | VALVE, CONTROL, GLOBE RECIPROCATING , 3" , 300 LB , 87 , RF FLANGE , A216 GR WCC | JET A1 LOADING PUMPS DISCHARGE MIN FLOW | 938867 | CNTR_VLV | M20FIC161 | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933021 | M30LV161A | VALVE, CONTROL, GLOBE RECIPROCATING , 1/2" , 300 LB , 87 , A 105 , A564 GR630 , | CONTROL VALVE LEVEL FOR FILTER COALSECER 30-L-006 | 938875 | CNTR_VLV | M30LIC161A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933022 | M30LV162A | VALVE, CONTROL, GLOBE RECIPROCATING , 1/2" , 300 LB , 87 , A 105 , A564 GR630 , | CONTROL VALVE LEVEL FOR FILTER COALESCER 30-L-007 | 938876 | CNTR_VLV | M30LIC162A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933023 | M400LV541 | VALVE, CONTROL, GLOBE RECIPROCATING , 1/2" , 300 , 87 , A 105 , A564 GR630 , 416 | ON/OFF VALVE FILTER COALESCER 400-L-003B | 938743 | CNTR_VLV | M400LIC541 | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933024 | M400LV540 | VALVE, CONTROL, GLOBE RECIPROCATING , 1/2" , 300 LB , 87 , ASTM A105 , A564 GR63 | ON/OFF VALVE FILTER COALESCER 400-L-003A | 938742 | CNTR_VLV | M400LIC540 | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933025 | M400LV751 | VALVE, CONTROL, GLOBE RECIPROCATING , 1/2" , 300 LB , 87 , A 105 , A564 GR630 , | ON/OFF VALVE FILTER COALESCER 400-L-004A | 938744 | CNTR_VLV | M400LIC751 | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933026 | M400LV753 | VALVE, CONTROL, GLOBE RECIPROCATING , 1/2" , 300 LB , 87 , A 105 , A564 GR630 , | ON/OFF VALVE FILTER COALESCER 400-L-004B | 938874 | CNTR_VLV | M400LIC753 | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933027 | M400PV536 | VALVE, CONTROL, GLOBE RECIPROCATING , 6" , 600 LB , 87 , A216 GR WCC , A564 GR63 | JET A1 TO FILTER COALESCER SEPARATOR(400-L-003A/B) | 938868 | CNTR_VLV | M400PIC536 | 3 | CNTR_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933028 | M400PV561 | VALVE, CONTROL, GLOBE RECIPROCATING , 6" , 900 , 87 , A216 GR WCC , A564 GR630 , | OFF SPEC JET A1- MAINLINE PUMP DISCHARGE | 938869 | CNTR_VLV | M400PIC561 | 3 | CNTR_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935602 | SMTP3 |  | TEST POINT# 3 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935603 | SMTP4 |  | TEST POINT# 4 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935604 | SMTP5 |  | TEST POINT# 5 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130814 | M400LMK016A1 | MOTOR,ELECTRIC, LUBE COOLER FAN 'A' FOR M400MP016A, IP55, 3 KW, 50 HZ, 415 V, S1, EXn, 100 LB4, 6206/2ZC3, VERTICCAL SHAFT UP FOOT MOUNTED, 1431 RPM, 3, DELTA, 5.8 AMP, CCW, F, IIA ZONE 2, 60 KG, T3 | MOTOR FOR LUBE OIL COOLER FAN 'A' FOR M4000MP016A |  | MOTOR | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016A1-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/10/18 | ME-PM-014-M6
969130815 | M400LMK016A2 | MOTOR,ELECTRIC, LUBE OIL COOLER FAN 'B' FOR M400MP016A, IP55, 3 KW, 50 HZ, 415 V, S1, EXn, M3GP 100LB4, 6206 2Z/C3, VERTICAL ,SHAFT UP,FOOT MOUNTED, 1431 RPM, 3, DELTA, 5.8 AMP, CCW, F, IIA ZONE 2, 60 KG, 400-PC-001, T3 | MOTOR FOR LUBE OIL COOLER FAN 'B' FOR M400MP016A |  | MOTOR | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016A2-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/10/18 | ME-PM-014-M6
969130816 | M400LMK016B1 | MOTOR,ELECTRIC, LUBE OIL COOLER FAN FOR M400MP016B, IP55, 3 KW, 50 HZ, 415 V, S1, EXn IIA T3, M3GP 100LB4, 6206-2Z/C3, VERTICAL FOOT MOUNTED, 1431 RPM, 3, DELTA, 5.8 AMP, CCW, F, IIA ZONE 2, 60 KG, T3 | LUBE OIL COOLER FAN 'A' FOR M400MP016B |  | MOTOR | M400P016B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016B1-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/11/18 | ME-PM-014-M6
969130817 | M400LMK016B2 | MOTOR,ELECTRIC, LUBE COOLER FAN 'B' FOR M400MP016B, IP 55, 3 KW, 50 HZ, 415 V, S1, M3GP 100LB4, 6206-2Z/C3, 1431 RPM, 3, DELTA, 5.8 AMP, CCW, F, IIA ,ZONE - 2, 60 KG | LUBE OIL COOLER FAN 'B' FOR M400MP016B |  | MOTOR | M400P016B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK016B2-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/10/18 | ME-PM-014-M6
969130818 | M400LMK019A1 | MOTOR,ELECTRIC, LUBE OIL COOLER FANS, IP55, 1.5 KW, 50 HZ, 415 V, S1, EXn, 905L, HOIZONTAL ,FOOT MOUNTED,SHAFT UP, 1420 RPM, 3, DELTA, 3.1 AMP, CCW, F, IIA ZONE2, 44 KG, T3 | MOTOR FOR LUBE OIL COOLER FAN 'A' FOR M400MP019 |  | MOTOR | M400P019 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK019A1-ME1 | INACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-014-M6
969130826 | M400MP080A | MOTOR,ELECTRIC, CORROSION INHIBITOR INJECTION PUMP, EExnAIIT3, IP55, 0.37 KW, 50 HZ, 415 V, 1380 RPM, 3, STAR, 1.07 AMP, 11 KG | MOTOR FOR CORROSSION INHIBITOR INJECTION PUMP |  | MOTOR | M400P080A | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 5 | 1 | 1 | 5 | 2.7959 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N |  | 1 | 0 | M400MP080A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/12/18 | ME-PM-014-M6
969130827 | M400MP080B | MOTOR,ELECTRIC, CORROSSION INHIBITOR INJECTION PUMP, EExnAIIT3,,IP55, 0.37 KW, 50 HZ, 415 V, s1, 1380 RPM, 3, STAR, 1.07 AMP, F, T3 | MOTOR FOR CORROSSION INHIBITOR INJECTION PUMP |  | MOTOR | M400P080B | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP080B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
969130828 | M400MP081A | MOTOR,ELECTRIC, CHEMICAL DOSING PUMP(ANTI STATIC), IP55, 0.37 KW, 50 HZ, 415 V, S1, EExnAIIT3, M3GP 80MA, DE-6205-2Z/C3,NDE-6204-2Z/C3, 1421 RPM, 3, DELTA, 0.9 AMP, F, EExnAIIT3, 29 KG, 400-PC-001,11AF-2, T3 | MOTOR FOR CHEMICAL DOSING PUMP 'A' (ANTI STATIC) |  | MOTOR | M400P081A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP081A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
969130831 | M400MP082A | MOTOR,ELECTRIC, GREEN DYE INJECTION PUMP, 0.37 KW, 50 HZ, 415 V, S1, M3GP 80MA 4B5, 6205 2ZC3,,6204 2ZC3, 1421 RPM, 3, 0.9 AMP | MOTOR FOR CHEMICAL DOSING PUMP 'A'(DYE INJECTION GREEN) |  | MOTOR | M400P082A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP082A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
969130834 | M400MP083B | MOTOR,ELECTRIC, CHEMICAL DOSING PUMP, 0.37 KW, 50 HZ, 415 V, M3GP 80 MA 4B5, 6205 2ZC3/6204 2ZC3, 1421 RPM, 3, 0.9 AMP | CHEMICAL DOSING PUMP BLUE DYE INJECTION PUMP 'A' |  | MOTOR | M400P083B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP083B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 18/08/18 | ME-PM-014-M6
969130819 | M400LMK019A2 | MOTOR,ELECTRIC, LUBE OIL COOLER FAN 'B' FOR M400MP019, IP55, 2.2 KW, 50 HZ, 415 V, S1, EXn, M3GP 100LA 4B 35, 6206-2ZC3, 1466 RPM, 3, 4.3 AMP, CCW, F, T3, 44 KG, 400-PC-001, T3 | MOTOR FOR LUBE OIL COOLER FAN 'B' FOR M400MP019 |  | MOTOR | M400P019 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK019A2-ME1 | INACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-014-M6
969130821 | M400MOV423 | ACTUATOR,ELECTRIC MOTOR, BIFFI - TYCO, 1, 50 HZ | LUBE OIL FILTER MOV FOR M400MP016B |  | MOV | M400P016B | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV423-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/12/18 | ME-PM-002-M6
969130822 | M400MOV468 | ACTUATOR,ELECTRIC MOTOR, BIFFI - TYCO, 1, 50 HZ | LUBE OIL FILTER MOV FOR M400MP019 |  | MOV | M400P019 | 3 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV468-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969130843 | M400MP301A | MOTOR,ELECTRIC, PPD PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR PPD PUMP 'A' |  | MOTOR | M400P301A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP301A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/08/18 | ME-PM-014-M6
969130847 | M400MP301B | MOTOR,ELECTRIC, PPD PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR PPD PUMP 'B' |  | MOTOR | M400P301B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP301B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/09/18 | ME-PM-014-M6
969130858 | M400MP302A | MOTOR,ELECTRIC, PPD PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR PPD PUMP 'A' |  | MOTOR | M400P302A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP302A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 08/08/18 | ME-PM-014-M6
969130865 | M400MP302B | MOTOR,ELECTRIC, PPD PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR PPD PUMP 'B' |  | MOTOR | M400P302B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP302B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/09/18 | ME-PM-014-M6
969130866 | M400MP303A | MOTOR,ELECTRIC, LUBRICITY IMPROVER PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR LUBRICITY IMPROVER PUMP 'A' |  | MOTOR | M400P303A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP303A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 09/08/18 | ME-PM-014-M6
969130867 | M400MP303B | MOTOR,ELECTRIC, LUNBRICITY IMPROVER PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR LUBRICITY IMPROVER PUMP 'B' |  | MOTOR | M400P303B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP303B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/09/18 | ME-PM-014-M6
969130868 | M400MP304A | MOTOR,ELECTRIC, LUBRICITY IMPROVER PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR LUBRICITY IMPROVER PUMP 'A' |  | MOTOR | M400P304A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP304A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 10/08/18 | ME-PM-014-M6
969130869 | M400MP304B | MOTOR,ELECTRIC, LUBRICITY IMPROVER PUMP, 0.75 KW, 50 HZ, 415 V, 80MB 4B5, 1422 RPM, 3, 1.78 AMP | MOTOR FOR LUBRICITY IMPROVER PUMP 'B' |  | MOTOR | M400P304B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M400MP304B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 26/09/18 | ME-PM-014-M6
969130820 | M400MOV408 | ACTUATOR,ELECTRIC MOTOR, BIFFI - TYCO, 1, 50 HZ | LUBE OIL FILTER MOV FOR M400MP016A |  | MOV | M400P016A | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV408-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/12/18 | ME-PM-002-M6
969130829 | M400MP081B | MOTOR,ELECTRIC, CHEMICAL DOSING PUMP(ANTI STATIC), IP55, 0.37 KW, 50 HZ, 415 V, S1, M3GP 80MA 4B5, 6205 2ZC3/6204 2ZC3, 1421 RPM, 3, 0.9 AMP, F | MOTOR FOR CHEMICAL DOSING PUMP 'B'(ANTI STATIC) |  | MOTOR | M400P081B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP081B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 02/08/18 | ME-PM-014-M6
969130832 | M400MP082B | MOTOR,ELECTRIC, GREEN DYE INJECTION PUMP 'B', 0.37 KW, 50 HZ, 415 V, M3GP 80MA 4B5, 6205 2ZC3/6204 2ZC3, 1421 RPM, 3, 0.9 AMP, F | CHEMICAL DOSING PUMP 'B' (DYE INJECTION GREEN) |  | MOTOR | M400P082B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP082B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/08/18 | ME-PM-014-M6
969131572 | M400XSP162 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN ELECTRICAL REPAIR AREA-WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131573 | M400XSP163 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN INSTRUMENT REPAIR AREA-WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131574 | M400XSP164 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN TOILET-WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131589 | M400XHE004 | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT PANTRY ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131590 | M400XHE005 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT TR 400-TMM-001A |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131592 | M400XHE007 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT TR 400-TMM-001B IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131593 | M400XHE008 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR FOR 400-NER-001B IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131594 | M400XHE009 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT BATTREY ROOM IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131595 | M400XHE010 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT BATTREY ROOM IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131596 | M400XHE011 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT M400-VSD-16B-TR IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131597 | M400XHE012 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT M400-VSD-16B-TR IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131598 | M400XHE013 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT M400-VSD-16A-TR IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131599 | M400XHE014 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT M400-VSD-16A-TR IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131600 | M400XHE015 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT TR M400-TML001B IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131575 | M400XSP165 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN MAIN STORAGE -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131576 | M400XSP166 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN MAIN STORAGE -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131577 | M400XSP167 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN MAIN STORAGE -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131578 | M400XSP168 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN MAIN STORAGE -WAREHOUSE |  | FG_DET | M400FACP005 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253449 | M410TML001A | TRANSFORMER | Transformer and NER |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TML001A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 03/09/18 | ME-PM-009-M6
933929 | M400VA12GA192 | GATE VALVE | GATE VALVE,1/2" 1500 LB, BW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933930 | M400VA12GL091 | GLOBE VALVE | GLOBE VALVE, 1/2" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933931 | M400VA10CH392 | VALVE CHECK | CHECK VALVE, WAFER DOUBLE DISC, 10" 150 LB |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933932 | M400VA10CH491 | VALVE CHECK | CHECK VALVE, 10" 300 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933933 | M400VA10CH691 | VALVE, CHECK, SWING , 10" , 900 LB , RF FLANGE , ASTM A216 GR WCB , 838MM | CHECK VALVE, 10" 900 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933934 | M400VA10CH791 | VALVE CHECK | CHECK VALVE, 10" 1500 LB, BW |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933935 | M400VA12CH392 | VALVE CHECK | CHECK VALVE, WAFER DOUBLE DISC, 12" 150 LB |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933936 | M400VA12GL691 | GLOBE VALVE | GLOBE VALVE, 12" 900 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933937 | M400VA14CH392 | VALVE CHECK | CHECK VALVE, WAFER DOUBLE DISC, 14" 150 LB |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933938 | M400VA2CH391 | VALVE CHECK | CHECK VALVE, 2" 150 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933939 | M400VA2GA391 | GATE VALVE | GATE VALVE, 2" 150 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933940 | M400VA2GA491 | GATE VALVE | GATE VALVE, 2" 300 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933941 | M400VA2GA591 | GATE VALVE | GATE VALVE, 2" 600 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933942 | M400VA2GA691 | GATE VALVE | GATE VALVE, 2" 900 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933943 | M400VA2GL391 | GLOBE VALVE | GLOBE VALVE, 2" 150 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933944 | M400VA2GL491 | GLOBE VALVE | GLOBE VALVE, 2" 300 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933945 | M400VA2GL591 | VALVE, GLOBE, 2" , 600 LB , RF FLANGE , ASTM A216 GR WCB , HANDWHEEL , FULL , 29 | GLOBE VALVE, 2" 600 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933946 | M400VA2GL691 | GLOBE VALVE | GLOBE VALVE, 2" 900 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933947 | M400VA3CH391 | VALVE, CHECK, SWING , 3" , 150 LB , 425 DEG C MAX , RF FLANGE , ASTM A216 GR WCB | CHECK VALVE, 3" 150 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933948 | M400VA3CH396 | VALVE, CHECK, SWING , 3" , 150 LB , 425 DEG C MAX , RF FLANGE , ASTM A216 GR WCB | CHECK VALVE, 3" 150 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933949 | M400VA3CH491 | VALVE CHECK | CHECK VALVE, 3" 300 LB, RF FLG |  | VALCH | M400VALVE | 3 | VALCH | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933950 | M400VA3GL391 | GLOBE VALVE | GLOBE VALVE, 3" 150 LB, RF FLG |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933951 | M400VA34GA091 | GATE VALVE | GATE VALVE, 3/4" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933952 | M400VA34GA092 | GATE VALVE | GATE VALVE, 3/4" 800 LB, SW+NPT |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934675 | M400TSV347 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934676 | M400TSV348 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934677 | M400TSV349 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934678 | M400TSV350 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934679 | M400TSV351 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934680 | M400TSV352 | VALVE RELIEF | JET A1 FILLING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934681 | M400TSV353 | VALVE RELIEF | JET A1 FILLING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934682 | M400TSV354 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934683 | M400TSV355 | VALVE RELIEF | JET A1 LOWERING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934684 | M400TSV356 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934685 | M400TSV357 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934686 | M400TSV391 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934687 | M400TSV392 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934688 | M400TSV393 | VALVE RELIEF | ULG 98, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934689 | M400TSV394 | VALVE RELIEF | KEROSENE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934690 | M400TSV401 | VALVE RELIEF | ULG 98, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934691 | M400TSV402 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934692 | M400TSV403 | VALVE RELIEF | ULG 98, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934693 | M400TSV404 | VALVE RELIEF | ULG 98, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934694 | M400TSV405 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934695 | M400TSV406 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934696 | M400TSV409 | VALVE RELIEF | ULG 95 / 98, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934697 | M400TSV410 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934698 | M400TSV411 | VALVE RELIEF | SLOP, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934699 | M400TSV412 | VALVE RELIEF | SLOP, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934700 | M400TSV421 | VALVE RELIEF | SLOP, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934701 | M400TSV422 | VALVE RELIEF | SLOP, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934702 | M400TSV501 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934703 | M400TSV502 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934704 | M400TSV503 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934705 | M400TSV504 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934706 | M400TSV505 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934707 | M400TSV506 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934708 | M400TSV531 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934709 | M400TSV533 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934710 | M400TSV535 | VALVE RELIEF | IRP JET A1, THERMAL SAFETY VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934711 | M400TSV536 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934712 | M400TSV537 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934713 | M400TSV547 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934714 | M400TSV550 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934715 | M400TSV551 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934716 | M400TSV552 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934717 | M400TSV566 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934718 | M400TSV567 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934719 | M400TSV568 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934720 | M400TSV569 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934721 | M400TSV570 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934722 | M400TSV578 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934723 | M400TSV651 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934724 | M400TSV652 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934725 | M400TSV653 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934726 | M400TSV654 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934727 | M400TSV655 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934728 | M400TSV656 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934729 | M400TSV657 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934730 | M400TSV658 | THERMAL VALVE RELIEF | ULG 91 MANIFOLD, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934731 | M400TSV659 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934732 | M400TSV660 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934733 | M400TSV661 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934734 | M400TSV751 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934735 | M400TSV752 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934736 | M400TSV756 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934737 | M400TSV775 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934738 | M400TSV801 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934739 | M400TSV802 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934740 | M400TSV803 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934741 | M400TSV804 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934742 | M400TSV805 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934743 | M400TSV851 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934744 | M400TSV852 | VALVE RELIEF | ULG 98, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934745 | M400TSV853 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934746 | M400TSV854 | VALVE RELIEF | KEROSENE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934747 | M400TSV855 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934748 | M400TSV856 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934749 | M400TSV858 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934750 | M400TSV861 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934751 | M400TSV882 | VALVE RELIEF | 239 BAR ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934752 | M400TSV883 | VALVE RELIEF | 239 BAR ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934753 | M400TSV884 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934754 | M400TSV885 | VALVE RELIEF | ULG 95 / JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934755 | M400TSV886 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934756 | M400TSV887 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934757 | MQ600TSV001 | VALVE RELIEF | MULTI PRODUCT, M/T TO ALAIN, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934758 | MQ600TSV002 | VALVE RELIEF | MULTI PRODUCT TO ADIA, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934759 | MQ600TSV003 | VALVE RELIEF | MULTI PRODUCT, M/T TO ALAIN, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934760 | MQ600TSV004 | VALVE RELIEF | MULTI PRODUCT TO ADIA, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934761 | MQ600TSV005 | VALVE RELIEF | MULTI PRODUCT, M/T TO ALAIN, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934762 | MQ600TSV006 | VALVE RELIEF | MULTI PRODUCT, M/T TO ALAIN, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934763 | MQ600TSV007 | VALVE RELIEF | MULTI PRODUCT TO ADIA, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934764 | MQ600TSV008 | VALVE RELIEF | MULTI PRODUCT, THERMAL RELIEF VALVE |  | PSV | MQ600VALVE | 1 | PSV | 616101-310600 | IRPMAQTA | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932749 | M400MVH001 | EOT Crane | ELECTRICAL OVERHEAD TRAVELING CRANE. |  | CRANE | MPH1 | 4 | CRANE | 616101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 1 | 1 | 10 | 2.699 | Low | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400MVH001-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 17/08/18 | ME-PM-007-M6
932751 | M30Z326H | LOADING ARM, MARINE, Metallic Swivel , Loading-Road Tanker , 154 , 13.5 , API Dr | Loading Arm |  |  | M30MISC | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932752 | M30Z326J | LOADING ARM, MARINE, Metallic Swivel , Loading-Road Tanker , 154 , 13.5 , API Dr | Loading Arm |  |  | M30MISC | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932755 | M400PFI001A | CAPACITOR BANK | CAPACITOR,BANK |  | SWBOARD | M400SCB | 3 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PFI001A-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 11/10/18 | ME-PM-005-Y1
932756 | M400PFI001B | CAPACITOR BANK | CAPACITOR,BANK |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PFI001B-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 12/10/18 | ME-PM-005-Y1
932759 | AA13BD1151105X | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-2" |  |  | AA13FLOW | 3 | SIGHT_GL | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932760 | AA13BD1241105XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  |  | AA13FLOW | 3 | SIGHT_GL | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932779 | M400BD6011051XV | GLASS, SIGHT, TOUGHENED BOROSILICATE , 25 BAR , CLEAR | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932780 | M400BD6111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932781 | M400BD6311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932782 | M400BD01011051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932783 | M400BD01211051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932784 | M400BD01311051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932785 | M400BD01411051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932786 | M400BD03511051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932787 | M400BD03611051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932788 | M400BD03711051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932789 | M400BD03811051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932790 | M400BD06211051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934083 | U29PG577 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Scraper Launcher 2902-L Pressure | 933173 | INDICATR | U2902L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934084 | U29PG578 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Naphtha Reformate/HSGO Line To SV Station-7 Pressu |  | INDICATR | U2902L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934085 | U29PG579 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Scraper Launcher 2902-L Pressure | 933173 | INDICATR | U2902L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934086 | U29PG580 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Scraper Launcher 2902-L Pressure GAUGE | 933173 | INDICATR | U2902L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934106 | U29PG600 | GAUGE, PRESSURE, BOURDON TUBE , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , | Pumps 2937-JA/JB/JC to 2903L/302-PL-002 |  | INDICATR | U2903L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934107 | U29PG601 | GAUGE, PRESSURE, INDICATION , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Scraper Launcher 2903-L Pressure |  | INDICATR | U2903L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934108 | U29PG602 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L | Scraper Launcher 2903-L Pressure | 933174 | INDICATR | U2903L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934109 | U29PG603 | GAUGE, PRESSURE, BOURDON TUBE , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , | Scraper Launcher 2903-L Line Pressure |  | INDICATR | U2903L | 4 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934120 | M30PI261 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | 30-ESD-706 Inlet PRESSURE GAUGE |  |  | M30PRESS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934121 | M30PI262 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | 400-L-006 Outlet Pressure GAUGE |  |  | M30PRESS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934122 | M30PI263 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | 400-L-007 Outlet Pressure GAUGE |  |  | M30PRESS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934123 | PL300PG30101A | GAUGE PRESSURE | Naph/Ref P/L Upstream Press.-301-EOV-01 |  |  | PL300SVS1 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934124 | PL300PG30101B | GAUGE PRESSURE | SRR P/L Downstream Press.-302-EOV-01 |  |  | PL300SVS1 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934125 | PL300PG30102A | GAUGE PRESSURE | Naph/Ref. P/L Upstream Press-301-EOV-02 |  |  | PL300SVS2 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934126 | PL300PG30102B | GAUGE PRESSURE | SRR P/L Downstream Press.-302-EOV-02 |  |  | PL300SVS2 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934127 | PL300PG30103A | GAUGE PRESSURE | Naph/Ref. P/L SRR P/L Downstream Press.-302-EOV-02 |  |  | PL300SVS3 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934128 | PL300PG30103B | GAUGE PRESSURE | Naph/Ref. P/L Downstream Press.-301-EOV-03 |  |  | PL300SVS3 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934129 | PL300PG30104A | GAUGE PRESSURE | Naph./Ref. P/L Upstream Press. 301-EOV-04 |  |  | PL300SVS4 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934130 | PL300PG30104B | GAUGE PRESSURE | Naph/Ref. P/L Downstream Press.-301-EOV-04 |  |  | PL300SVS4 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934131 | PL300PG30105A | GAUGE PRESSURE | Naph/Ref. P/L Upstream Press.-301-EOV-05 |  |  | PL300SVS5 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934132 | PL300PG30105B | GAUGE PRESSURE | Naph/Ref. P/L Downstream Press.-301-EOV-05 |  |  | PL300SVS5 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934133 | PL300PG30106A | GAUGE PRESSURE | Naph/Ref. P/L Upstream Press.-301-EOV-06 |  |  | PL300SVS6 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934134 | PL300PG30106B | GAUGE PRESSURE | Naph/Ref. P/L Downstream Press.-301-EOV-06 |  |  | PL300SVS6 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934135 | PL300PG30107A | GAUGE, PRESSURE, INDICATION , 0 TO 160 , 100MM , ½" NPTM , SS 316L , SS 316 , BO | Naph/Ref. P/L Upstream Press.-301-EOV-07 |  |  | PL300SVS7 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934136 | PL300PG30107B | GAUGE, PRESSURE, INDICATION , 0 TO 160 , 100MM , ½" NPTM , SS 316L , SS 316 , BO | Naph/Ref. P/L Downstream Press.-EOV-301-07 |  |  | PL300SVS7 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934137 | PL300PG30201A | GAUGE PRESSURE | SRR P/L Upstream Press.-302-EOV-01 |  |  | PL300SVS1 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934138 | PL300PG30201B | GAUGE PRESSURE | SRR P/L Downstream Press.-302-EOV-01 |  |  | PL300SVS1 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934139 | PL300PG30202A | GAUGE PRESSURE | SRR P/L Upstream Press.-302-EOV-02 |  |  | PL300SVS2 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934140 | PL300PG30202B | GAUGE PRESSURE | SRR P/L Downstream Press.-302-EOV-02 |  |  | PL300SVS2 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934141 | PL300PG30203A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #3 |  |  | PL300SVS3 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934142 | PL300PG30203B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #3 |  |  | PL300SVS3 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934143 | PL300PG30204A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #4 |  |  | PL300SVS4 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934144 | PL300PG30204B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #4 |  |  | PL300SVS4 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934145 | PL300PG30205A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #5 |  |  | PL300SVS5 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934146 | PL300PG30205B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #5 |  |  | PL300SVS5 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934147 | PL300PG30206A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #6 |  |  | PL300SVS6 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934148 | PL300PG30206B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #6 |  |  | PL300SVS6 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934149 | PL300PG30207A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #7 |  |  | PL300SVS7 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934150 | PL300PG30207B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #7 |  |  | PL300SVS7 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934151 | PL300PG30301A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #1 |  |  | PL300SVS1 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934152 | PL300PG30301B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #1 |  |  | PL300SVS1 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934153 | PL300PG30302A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #2 |  |  | PL300SVS2 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934358 | AT800PG106 | GAUGE PRESSURE | PRESSURE GAUGE |  |  | AT800PRESS | 4 | PRES GAUG | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934359 | AT800PG107 | GAUGE, PRESSURE, INDICATION , 0 TO 10 , 100MM , ½" NPTM , SS 316L , SS 316 , BOT | Pr. at Jet A1 P/L from Mussafah to ADIA St. Tanks |  |  | AT800PRESS | 4 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934360 | AT800PG108 | GAUGE PRESSURE | PRESSURE GAUGE |  |  | AT800PRESS | 3 | PRES GAUG | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934361 | AT800PG109 | GAUGE PRESSURE | PRESSURE GAUGE |  |  | AT800PRESS | 3 | PRES GAUG | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934363 | PL300MUX001 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | PL300SVS1 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934364 | PL300MUX002 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | PL300SVS2 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934365 | PL300MUX003 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | PL300SVS3 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934366 | PL300MUX004 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | PL300SVS4 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934367 | PL300MUX005 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | PL300SVS5 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934368 | PL300MUX006 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | PL300SVS6 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934369 | PL300MUX007 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | PL300SVS7 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934370 | M400IPX001 | SYSTEM | EPABX SYSTEM |  | TELECOM | M400TEL | 1 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934371 | M400MUX001 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | M400TEL | 1 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934372 | MQ600MUX001 | SYSTEM | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | MQ600 | 1 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934374 | AT800MUX001 | SYSTEM - FIBER TO COPPER MULTIPLEXER | FIBER TO COPPER MULTIPLEXER (TN1Ue SDH). |  |  | AT800 | 3 | TELECOM | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934375 | AT800ODF001 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 24 PORT |  |  | AT800MUX001 | 2 | TELECOM | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934378 | MQ600TEL001 | CABINET | TELECOM CABINET |  |  | MQ600MUX001 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934379 | MQ600ODF001 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | MQ600MUX001 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934380 | MQ600ODF002 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 24 PORT |  |  | MQ600MUX001 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934381 | AT800TEL001 | TELECOM CABINET | TELECOM CABINET |  |  | AT800MUX001 | 3 | TELECOM | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265922 | PL100PDT400A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935640 | SMTP42 |  | TEST POINT# 42 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935641 | SMTP43 |  | TEST POINT# 43 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935642 | SMTP44 | ???????????????? | TEST POINT# 44 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132834 | M400K002A | BLOWER | PROCESS AIR STRIPPER BLOWER OF WASTE WATER TREATMENT PLANT AT MS&P TERMINAL. |  | FAN | M400WWTP | 3 | FAN | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 1 | 5 | 2.7959 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | M400K002A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 19/12/18 | MM-PM-022-M6
XXX935650 | SMLPGTP5 | CP TEST POINT | TEST POINT # 5 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59040 | M10MLG101 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-101 | TNK56513 | TANKGAUG | M10T101 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59062 | M10MLG102 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-102 | TNK56531 | TANKGAUG | M10T102 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59084 | M10MLG103 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-103 | TNK56547 | TANKGAUG | M10T103 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59104 | M10MLG104 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-104 | TNK56565 | TANKGAUG | M10T104 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59124 | M10MLG105 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-105 | TNK56585 | TANKGAUG | M10T105 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59144 | M10MLG106 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-106 | TNK56600 | TANKGAUG | M10T106 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59164 | M10MLG107 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-107 | TNK56616 | TANKGAUG | M10T107 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59186 | M10MLG108 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-108 | TNK56634 | TANKGAUG | M10T108 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59203 | M10MLG109 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-109 | TNK56645 | TANKGAUG | M10T109 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGL59221 | M10MLG110 | INDICATOR, LEVEL, TANK , -40 C TO +70 C | MECHANICAL LEVEL GAUGE FOR TANK T-110 | TNK56656 | TANKGAUG | M10T110 | 3 | TANKGAUG | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969133169 | M10LZHH053 | SWITCH,LEVEL FLOAT, 2", 316 SS, BASEEFA EXD IIC T6, IP66, SIDE/SIDE | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-105 | TNK56585 | LVL_SWT | M10T105 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZHH053-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/09/18 | MC-PM-025-M6
969131420 | M400FACP001 | PANEL,FIRE ALARM, MINERVA | FIRE ALARM CONTROL PANEL AT MCR RACK ROOM-PLCR P&TD. |  | F&G_PNL | MMCR | 1 | F&G_PNL | 617101-310510 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FACP001-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 06/09/18 | MFPS-PM01.M3
935216 | M400F14 | TRUCK, FIRE, MULTIPURPOSE, 3341 AK , FOAM CONCENTRATE(4000L) , 300KW (408HP), 18 | F-14 FIRE TRUCK 79046 (M400ME004). |  |  | M400FIRE | 1 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935217 | M400F23 | TRUCK, FIRE, FOAM TRANSPORT, 3341 AK , FOAM CONCENTRATE(9000L) , 300KW (408HP), | FIRE Vehicle GR25759, Heavy equipment, M400 |  |  | M400FIRE | 1 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935218 | M400ME005B | FOAM MONITOR, SERIES 377, INLET DN150,PN16 X OUTLET FOAMPIPE SW 100 WITH DEFLECT | FOAM MONITOR & AUXILLIARIES-F/FIGHT. VEHICLE | 935217 |  | M400F23 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | f | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935219 | M400ME004A | PANEL CONTROL | F/FIGHT. VEHICLE-CONTROL PANEL | 935216 |  | M400F14 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | f | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935220 | M400ME004B | FOAM MONITOR, SERIES 377, INLET DN150,PN16 X OUTLET FOAMPIPE SW 100 WITH DEFLECT | FOAM MONITOR & AUXILLIARIES-F/FIGHT. VEHICLE | 935216 |  | M400F14 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | f | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935221 | M400MEG004 | PUMP,CENTRIFUGAL, WATER, 10000 L/MIN@ 12BARG WITH HYDRANT SUPPLY @ 6 BARG, PH. BRONZE, PH. BRONZE, PH. BRONZE, PH. BRONZE, SINGLE, MONOCELLULAR, BY TRUCK N56 PTO | FIRE PUMP-F/FIGHT. VEHICLE | 935216 | PUCE | M400F14 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | f | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935866 | M400LP016AA | PUMP, SCREW, GEAR | LUBE OIL PUMP FOR M400P016A. |  | PUSC | M400P016A | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935867 | M400LP016AB | PUMP, SCREW, GEAR | LUBE OIL PUMP FOR M400P016B. |  | PUSC | M400P016B | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935868 | M400LP016BA | PUMP, SCREW, GEAR | LUBE OIL PUMP FOR M400P016A. |  | PUSC | M400P016A | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935869 | M400LP016BB | PUMP, SCREW, GEAR | LUBE OIL PUMP FOR M400P016B. |  | PUSC | M400P016B | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935870 | M400LP019A | PUMP, SCREW, GEAR | LUBE OIL PUMP-A FOR 400P019 & 400MP019 |  | PUSC | M400P019 | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935871 | M400LP019B | PUMP, SCREW, GEAR | LUBE OIL PUMP-B FOR 400P019 & 400MP019 |  | PUSC | M400P019 | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936738 | MQ600TT002 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 60 , 4-20mA WITH H | TEMP.TR. MULTIPRODUCT TIE-IN P/L I/L TO 600PLR015 |  |  | MQ600TEMP | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600TT002-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-010-M6
936739 | MQ600TT003 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 60 , 4-20mA WITH H | TEMP.TR. ADR-ALAIN MULTIPRODUCT TIE-IN P/L 600PL |  |  | MQ600TEMP | 2 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | MQ600TT003-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-010-M6
FFF56544 | M50J102A | FIRE FIGHTING FOAM GENERATOR FOR T-102 | FIRE FIGHTING FOAM GENERATOR FOR T-102 |  | F_MIXR | M10T102 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56545 | M50J102B | FIRE FIGHTING FOAM GENERATOR FOR T-102 | FIRE FIGHTING FOAM GENERATOR FOR T-102 |  | F_MIXR | M10T102 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56562 | M50J103A | FIRE FIGHTING FOAM GENERATOR FOR T-103 | FIRE FIGHTING FOAM GENERATOR FOR T-103 |  | F_MIXR | M10T103 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56563 | M50J103B | FIRE FIGHTING FOAM GENERATOR FOR T-103 | FIRE FIGHTING FOAM GENERATOR FOR T-103 |  | F_MIXR | M10T103 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56578 | M50J104A | FIRE FIGHTING FOAM GENERATOR FOR T-104 | FIRE FIGHTING FOAM GENERATOR FOR T-104 |  | F_MIXR | M10T104 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56579 | M50J104B | FIRE FIGHTING FOAM GENERATOR FOR T-104 | FIRE FIGHTING FOAM GENERATOR FOR T-104 |  | F_MIXR | M10T104 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56580 | M50J104C | FIRE FIGHTING FOAM GENERATOR FOR T-104 | FIRE FIGHTING FOAM GENERATOR FOR T-104 |  | F_MIXR | M10T104 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56581 | M50J104D | FIRE FIGHTING FOAM GENERATOR FOR T-104 | FIRE FIGHTING FOAM GENERATOR FOR T-104 |  | F_MIXR | M10T104 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56582 | M50J104E | FIRE FIGHTING FOAM GENERATOR FOR T-104 | FIRE FIGHTING FOAM GENERATOR FOR T-104 |  | F_MIXR | M10T104 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132453 | M400MPWP1CR | MOTOR,ELECTRIC, PORTABLE WATER PUMP, 50 HZ | MOTOR FOR PORTABLE WATER PUMP N0.1 AT CONTROL ROOM |  | MOTOR | MMCR | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132454 | M400MPWP2CR | MOTOR,ELECTRIC, PORTABLE WATER PUMP, 50 HZ | MOTOR FOR PORTABLE PUMP NO.2 AT CONTROL ROOM MUSAFFAH |  | MOTOR | MMCR | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132455 | M400MPWP1SS | MOTOR,ELECTRIC, PORTABLE WATER PUMP, 50 HZ, S1 | MOTOR FOR PORTABLE WATER PUMP NO.1 AT MUSAFFAH S/S-400 |  | MOTOR | M400SUBSTN | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132456 | M400MPWP2SS | MOTOR,ELECTRIC | MOTOR FOR PORTABLE WATER PUMP NO.2 AT MUSAFFAH S/S 400 |  | MOTOR | M400SUBSTN | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132459 | PL300XSP001/01 | DETECTOR,FIRE PROTECTION, PHOTOELECTRONIC, 70 DEG C, 24VDC, IN-DOOR, YES | SMOKE DETECTOR AT PASSIVE SHELTER SV STATION -1 |  | FG_DET | PL300SVS1 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XSP001/01-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 25/10/18 | MFPS-PM08.M3
969132460 | PL300XSP001/02 | DETECTOR,FIRE PROTECTION, PHOTOELECTRONIC, 70 DEG C, 24VDC, IN-DOOR, YES | SMOKE DETECTOR AT PASSIVE SHELTER SV STATION - 2 |  | FG_DET | PL300SVS2 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XSP001/02-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/10/18 | MFPS-PM08.M3
969132461 | PL300XSP001/03 | DETECTOR,FIRE PROTECTION, PHOTOELECTRONIC, 70 DEG C, 24VDC, IN-DOOR, YES | SMOKE DETECTOR AT PASSIVE SHELTER SV STATION - 3 |  | FG_DET | PL300SVS3 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XSP001/03-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM08.M3
969132462 | PL300XSP001/04 | DETECTOR,FIRE PROTECTION, PHOTOELECTRONIC, 70 DEG C, 24VDC, IN-DOOR, YES | SMOKE DETECTOR AT PASSIVE SHELTER SV STATION - 4 |  | FG_DET | PL300SVS4 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XSP001/04-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM08.M3
969132464 | PL300XSP001/06 | DETECTOR,FIRE PROTECTION, PHOTOELECTRONIC, 70 DEG C, 24VDC, IN-DOOR, YES | SMOKE DETECTOR AT PASSIVE SHELTER SV STATION - 6 |  | FG_DET | PL300SVS6 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XSP001/06-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM08.M3
969132465 | PL300XSP001/07 | DETECTOR,FIRE PROTECTION, PHOTOELECTRONIC, 70 DEG C, 24VDC, IN-DOOR, YES | SMOKE DETECTOR AT PASSIVE SHELTER SV STATION - 7 |  | FG_DET | PL300SVS7 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XSP001/07-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM08.M3
969132466 | PL300XAC001/01 | CALL POINT, FIRE ALARM PUSH BUTTON, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, RED, YES | MANUAL CALL POINT AT MAIN GATE SV STATION - 1 |  | PB_HS-MC | PL300SVS1 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC001/01-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/10/18 | MFPS-PM07.M3
969132467 | PL300XAC002/01 | CALL POINT, EEx emd IIT4 or EEx ed IIT6, RED, FIRE ALARM PUSH BUTTON, IP66 & IP 67, YES | MANUAL CALL POINT AT EMERGENCY GATE SV STATION - 1 |  | PB_HS-MC | PL300SVS1 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC002/01-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/10/18 | MFPS-PM07.M3
969132463 | PL300XSP001/05 | DETECTOR,FIRE PROTECTION, PHOTOELECTRONIC, 70 DEG C, 24VDC, IN-DOOR, YES | SMOKE DETECTOR AT PASSIVE SHELTER SV STATION - 5 |  | FG_DET | PL300SVS5 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XSP001/05-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM08.M3
969132487 | MBS1 | BATTERY,BANK, ni-cd, XHP, 20, E4, 1.4V/CELL V, YES | BATTERY SET "A" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201A AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MBS1-ME1 | DRAFT | ELEC | PM | EDS | 3 | MONTHS |  | ME-PM-001-M3
969132488 | MBS2 | BATTERY,BANK, ni-cd, 20, E4 | BATTERY SET "B" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201A AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132489 | MBS3 | BATTERY,BANK, ni-cd, 20, E4 | BATTERY SET "A" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201B AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132490 | MBS4 | BATTERY,BANK, ni-cd, 20, E4 | BATTERY SET "B" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201B AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132491 | MBS5 | BATTERY,BANK, ni-cd, 20, E4 | BATTERY SET "A" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201C AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132492 | MBS6 | BATTERY,BANK, ni-cd, 20, E4 | BATTERY SET "B" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201C AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132493 | MBS7 | BATTERY,BANK, ni-cd, 20, E4 | BATTERY SET "A" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201D AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132494 | MBS8 | BATTERY,BANK, ni-cd, 20, E4 | BATTERY SET "B" FOR DIESEL DRIVEN ENGINE FIRE WATER PUMP M400MP201D AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132495 | MBS9 | BATTERY,BANK, ni-cd, SBH 118-2, 20, YES | BATTERY SET "A" FOR EMERGENCY DIESEL GENERATOR SET M400EPB001 AT MTERMINAL IRP-1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132496 | MBS10 | BATTERY,BANK, ni-cd, SBH 118-2, 10, YES | BATTERY SET "B" FOR EMERGENCY DIESEL GENERATOR SET M400EPB001 AT MTERMINAL IRP - 1 |  | BATTERY | M400BATT | 1 | BATTERY | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969166707 | M410P014A | MECHANICAL SEAL(DE) FOR JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP | 969147451 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-4-Y1
969166708 | M410P014B | MECHANICAL SEAL (DE) FOR JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP | 969147452 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-4-Y1
969166709 | M410P009 | MECHANICAL SEAL FOR ULG/GAS OIL SUMP PUMP | ULG/GAS OIL SUMP PUMP ON 410V003. | 969147453 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P009-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-7-Y1
969166710 | M410P010 | MECHANICAL SEAL FOR JET A1 SUMP PUMP | JET A1 SUMP PUMP ON 410V004. | 969147454 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P010-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-7-Y1
969259606 | M410PKG2306002 | GENERATOR, FOAM | Foam Mobile |  | VESSEL | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936537 | PL300PT30204A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. SRR P/L UPSTREAM PRESSURE-302-EOV-04 |  | TRANS | PL300SVS4 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30204A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-021-M2
936538 | PL300PT30204B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR.SRR P/L DOWNSTREAM PRESSURE-302-EOV-04 |  | TRANS | PL300SVS4 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30204B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-021-M2
936539 | PL300PT30205A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. SRR P/L UPSTREAM PRESSURE-302-EOV-05 |  | TRANS | PL300SVS5 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30205A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-021-M2
936540 | PL300PT30205B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR.SRR P/L DOWNSTREAM PRESSURE-302-EOV-05 |  | TRANS | PL300SVS5 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30205B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-021-M2
936541 | PL300PT30206A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. SRR P/L UPSTREAM PRESSURE-302-EOV-06 |  | TRANS | PL300SVS6 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30206A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-021-M2
936542 | PL300PT30206B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR.SRR P/L DOWNSTREAM PRESSURE-302-EOV-06 |  | TRANS | PL300SVS6 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30206B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-021-M2
936543 | PL300PT30207A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. SRR P/L UPSTREAM PRESSURE-302-EOV-07 |  | TRANS | PL300SVS7 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30207A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-021-M2
936544 | PL300PT30207B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR.SRR P/L DOWNSTREAM PRESSURE-302-EOV-07 |  | TRANS | PL300SVS7 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30207B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-021-M2
936545 | PL300PT30301A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20mA , 24V DC, 2 | PR.TRANSMTR.M/P P/L DOWNSTREAM PRESSURE-303-EOV-01 |  | TRANS | PL300SVS1 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30301A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-021-M2
936546 | PL300PT30301B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20mA , 24V DC, 2 | PR.TRANSMTR. M/P P/L UPSTREAM PRESSURE-303-EOV-01 |  | TRANS | PL300SVS1 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30301B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-021-M2
936547 | PL300PT30302A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20mA , 24V DC, 2 | PR.TRANSMTR.M/P P/L DOWNSTREAM PRESSURE-303-EOV-02 |  | TRANS | PL300SVS2 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30302A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-021-M2
936548 | PL300PT30302B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR. M/P P/L UPSTREAM PRESSURE-303-EOV-02 |  | TRANS | PL300SVS2 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30302B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-021-M2
936549 | PL300PT30303A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR.M/P P/L DOWNSTREAM PRESSURE-303-EOV-03 |  | TRANS | PL300SVS3 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30303A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-021-M2
936550 | PL300PT30303B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR. M/P P/L UPSTREAM PRESSURE-303-EOV-03 |  | TRANS | PL300SVS3 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30303B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-021-M2
936551 | PL300PT30304A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR.M/P P/L DOWNSTREAM PRESSURE-303-EOV-04 |  | TRANS | PL300SVS4 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30304A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-021-M2
936552 | PL300PT30304B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR. M/P P/L UPSTREAM PRESSURE-303-EOV-04 |  | TRANS | PL300SVS4 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30304B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-021-M2
936553 | PL300PT30305A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR.M/P P/L DOWNSTREAM PRESSURE-303-EOV-05 |  | TRANS | PL300SVS5 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30305A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-021-M2
936554 | PL300PT30305B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR. M/P P/L UPSTREAM PRESSURE-303-EOV-05 |  | PRES_TX | PL300SVS5 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30305B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-021-M2
936555 | PL300PT30306A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR.M/P P/L DOWNSTREAM PRESSURE-303-EOV-06 |  | TRANS | PL300SVS6 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30306A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-021-M2
936556 | PL300PT30306B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 110 , 4-20MA , 24V DC, 2 | PR.TRANSMTR. M/P P/L UPSTREAM PRESSURE-303-EOV-06 |  | PRES_TX | PL300SVS6 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30306B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-021-M2
936557 | PL300TT30101A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L UPSTREAM 301EOV01 |  | TEMP_TX | PL300SVS1 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30101A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-017-M2
936558 | PL300TT30101B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM 301EOV01 |  | TEMP_TX | PL300SVS1 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30101B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-017-M2
936559 | PL300TT30102A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L UPSTREAM 301EOV02 |  | TEMP_TX | PL300SVS2 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30102A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-017-M2
936560 | PL300TT30102B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L DOWNSTREAM 301EOV02 |  | TEMP_TX | PL300SVS2 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30102B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-017-M2
936561 | PL300TT30103A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L UPSTREAM 301EOV03 |  | TEMP_TX | PL300SVS3 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30103A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-017-M2
936562 | PL300TT30103B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM 301EOV03 |  | TEMP_TX | PL300SVS3 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30103B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-017-M2
936563 | PL300TT30104A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L UPSTREAM 301EOV04 |  | TEMP_TX | PL300SVS4 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30104A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-017-M2
936564 | PL300TT30104B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L DOWNSTREAM 301EOV04 |  | TEMP_TX | PL300SVS4 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30104B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-017-M2
936565 | PL300TT30105A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L UPSTREAM 301EOV05 |  | TEMP_TX | PL300SVS5 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30105A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-017-M2
936566 | PL300TT30105B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L DOWNSTREAM 301EOV05 |  | TEMP_TX | PL300SVS5 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30105B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-017-M2
936567 | PL300TT30106A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L UPSTREAM 301EOV06 |  | TEMP_TX | PL300SVS6 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30106A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-017-M2
936568 | PL300TT30106B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L DOWNSTREAM 301EOV06 |  | TEMP_TX | PL300SVS6 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30106B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-017-M2
936569 | PL300TT30107A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L UPSTREAM 301EOV07 |  | TEMP_TX | PL300SVS7 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30107A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-017-M2
936570 | PL300TT30107B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TR. NAPHTHA/REFORMATE P/L DOWNSTREAM 301EOV07 |  | TEMP_TX | PL300SVS7 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30107B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-017-M2
936571 | PL300TT30201A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L UPSTREAM 302-EOV-01 |  | TEMP_TX | PL300SVS1 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30201A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-017-M2
936572 | PL300TT30201B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L DOWNSTREAM 302-EOV-01 |  | TEMP_TX | PL300SVS1 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30201B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-017-M2
936573 | PL300TT30202A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L UPSTREAM 302-EOV-02 |  | TEMP_TX | PL300SVS2 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30202A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-017-M2
936574 | PL300TT30202B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L DOWNSTREAM 302-EOV-02 |  | TEMP_TX | PL300SVS2 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30202B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-017-M2
936575 | PL300TT30203A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L UPSTREAM 302-EOV-03 |  | TEMP_TX | PL300SVS3 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30203A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-017-M2
936576 | PL300TT30203B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 4-20MA+HART PROTOCOL , | TEMP.TRANSMTR. SRR P/L DOWNSTREAM 302-EOV-03 |  | TEMP_TX | PL300SVS3 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30203B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-017-M2
936577 | PL300TT30204A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 4-20MA+HART PROTOCOL , | TEMP.TRANSMTR. SRR P/L UPSTREAM TEMP. 302-EOV-04 |  | TEMP_TX | PL300SVS4 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30204A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-017-M2
936578 | PL300TT30204B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L DOWNSTREAM 302-EOV-04 |  | TEMP_TX | PL300SVS4 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30204B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-017-M2
936579 | PL300TT30205A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L UPSTREAM 302-EOV-05 |  | TEMP_TX | PL300SVS5 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30205A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-017-M2
936580 | PL300TT30205B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L DOWNSTREAM 302-EOV-05 |  | TEMP_TX | PL300SVS5 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30205B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-017-M2
936581 | PL300TT30206A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L UPSTREAM 302-EOV-06 |  | TEMP_TX | PL300SVS6 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30206A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-017-M2
936582 | PL300TT30206B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L DOWNSTREAM 302-EOV-06 |  | TEMP_TX | PL300SVS6 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30206B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-017-M2
936583 | PL300TT30207A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L UPSTREAM 302-EOV-07 |  | TEMP_TX | PL300SVS7 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30207A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-017-M2
936584 | PL300TT30207B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR P/L DOWNSTREAM 302-EOV-07 |  | TEMP_TX | PL300SVS7 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30207B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-017-M2
936585 | PL300TT30301A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L DOWNSTREAM 303-EOV-01 |  | TEMP_TX | PL300SVS1 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30301A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-017-M2
936586 | PL300TT30301B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L UPSTREAM 303-EOV-01 |  | TEMP_TX | PL300SVS1 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30301B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-017-M2
936587 | PL300TT30302A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L DOWNSTREAM 303-EOV-02 |  | TEMP_TX | PL300SVS2 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30302A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-017-M2
936588 | PL300TT30302B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L UPSTREAM 303-EOV-02 |  | TEMP_TX | PL300SVS2 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30302B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-017-M2
936589 | PL300TT30303A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L DOWNSTREAM 303-EOV-03 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30303A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-017-M2
936590 | PL300TT30303B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L UPSTREAM 303-EOV-03 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30303B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-017-M2
936591 | PL300TT30304A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L DOWNSTREAM 303-EOV-04 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30304A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-017-M2
936592 | PL300TT30304B | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L UPSTREAM 303-EOV-04 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30304B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-017-M2
936593 | PL300TT30305A | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 100 , 4-20mA WITH | TEMP.TRANSMTR. M/P P/L DOWNSTREAM 303-EOV-05 |  | TEMP_TX | PL300TEMP | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | PL300TT30305A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-017-M2
936819 | AT800PT101B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 20 , 4-20mA , 24V DC, 2 | PRESS.TRANSMTR. FLOW METERING SKID |  | TRANS | AT800PRESS | 3 | PRES_TX | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936820 | AT800PT102 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 20 , 4-20mA , 24V DC, 2 | PRESS.TRANSMTR. EOV-405 INLET |  | TRANS | AT800PRESS | 3 | PRES_TX | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936821 | AT800PT103 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 20 , 4-20mA , 24V DC, 2 | PRESS.TRANSMTR. PV-105 INLET |  | TRANS | AT800PRESS | 3 | PRES_TX | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936822 | AT800PT104 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 15 , 4-20mA , 24V DC, 2 | PRESS.TR. JET A1 P/L FROM MUSSAFAH TO ADIA STORA |  | TRANS | AT800PRESS | 3 | PRES_TX | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936823 | AT800PT105 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 10 , 4-20mA , 24V DC, 2 | PRESS.TRANSMTR. PV-105 OUTLET | 938873 | TRANS | AT800PIC105 | 2 | PRES_TX | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936824 | AT800TT102 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP.TR. JET A1 INLET LINE TEMPERATURE TO PLR-101 |  |  | AT800TEMP | 3 | TEMP_TX | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936825 | AT800TT103 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMP.TR. JET A1 TEMPERATURE AT O/L OF PV-105 |  |  | AT800TEMP | 3 | TEMP_TX | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933390 | M400MOV065 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 OUTLET HEADER (GAS OIL, 16" X 14" CL 150 WITH EXTN LG 1740MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV065-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/01/19 | ME-PM-002-M6
933391 | M400MOV066 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-101 OUTLET ISOLATION (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV066-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/10/18 | ME-PM-002-M6
933392 | M400MOV067 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR GAS OIL FROM T-101 TO LOADING PUMP 221B,C,& D.(GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV067-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/10/18 | ME-PM-002-M6
933393 | M400MOV068 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-102 INLET ISOLATION.(FILLING OF T102, GAS OIL, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV068-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/10/18 | ME-PM-002-M6
933394 | M400MOV069 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-102 INLET HEADER (GAS OIL, 10" X 8" CL 300 WITH EXTN LG 1830MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV069-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/10/18 | ME-PM-002-M6
933395 | M400MOV070 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-102 INLET HEADER.(GAS OIL, 10" X 8" CL 300 WITH EXTN LG 1830MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV070-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/01/19 | ME-PM-002-M6
933396 | M400MOV071 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-102 OUTLET HEADER.(GAS OIL, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV071-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/10/18 | ME-PM-002-M6
933397 | M400MOV072 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-102 OUTLET HEADER (GAS OIL, 16" X 14" CL 150 WITH EXTN LG 1740MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV072-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/02/19 | ME-PM-002-M6
933398 | M400MOV073 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-102 OUTLET ISOLATION (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV073-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/10/18 | ME-PM-002-M6
933399 | M400MOV074 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR GAS OIL FROM T-102 TO LOADING PUMP 221B,C & D.(GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV074-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/10/18 | ME-PM-002-M6
933400 | M400MOV075 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-103 INLET ISOLATION (GAS OIL, 10" X 8" CL 300 WITH EXTN LG 2590MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV075-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/10/18 | ME-PM-002-M6
933401 | M400MOV076 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, F14, SAE 80 EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-103 INLET HEADER (GAS OIL, 10" X 8" CL 300 WITH EXTN LG 1830MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV076-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/10/18 | ME-PM-002-M6
933402 | M400MOV077 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-103 INLET HEADER (GAS OIL, 10" X 8" CL 300 WITH EXTN LG 1830MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV077-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/02/19 | ME-PM-002-M6
933403 | M400MOV078 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, F14, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-103 OUTLET HEADER (GAS OIL, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV078-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/10/18 | ME-PM-002-M6
933404 | M400MOV079 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-103 OUTLET HEADER (GAS OIL, 16" X 14" CL 150 WITH EXTN LG 1740MM) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV079-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/02/19 | ME-PM-002-M6
933405 | M400MOV080 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-103 OUTLET ISOLATION VALVE (GAS OIL, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV080-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/10/18 | ME-PM-002-M6
933406 | M400MOV081 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE 80 EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-103 GAS OIL TO LOADING PUMP P-221B,C,& D (GAS OIL, 16" X 14" CL 150)_ |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV081-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/10/18 | ME-PM-002-M6
933407 | M400MOV082 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR T-104 COMMON FILLING HEADER. |  | MOV | M400MOV | 2 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV082-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933408 | M400MOV083 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T- 104 INLET HEADER (GAS OIL, 10" X 8" CL 300 WITH EXTN LG 2000MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV083-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/01/19 | ME-PM-002-M6
933409 | M400MOV084 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-104 INLET HEADER (GAS OIL, 10" X 8" CL 300 WITH EXTN LG 2000MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV084-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/02/19 | ME-PM-002-M6
938417 | M30DT261H | TRANSMITTER | Density at Loading Bay H |  | ANALYSER | M30SYS | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938418 | M30DT261J | TRANSMITTER | Density at Loading Bay J |  | ANALYSER | M30SYS | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938419 | M30EOY706A | VALVE, SOLENOID | ESD Valve for JET A1 Loading |  | SOL_VLV | M30SYS | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938420 | M30EOY706B | VALVE, SOLENOID | ESD Valve for JET A1 Loading |  | SOL_VLV | M30SYS | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938421 | M30ESD706 | VALVE, SOLENOID | ESD Valve for Loading Bay 261H/J |  | ANALYSER | M30SYS | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938422 | M30FE261H | SENSOR, MASS FLOW | Flow at JET A1 Loading Bay H |  |  | M30SYS | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938423 | M30FE261J | SENSOR, MASS FLOW | Flow at JET A1 Loading Bay J |  |  | M30SYS | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938424 | M30FV261J | VALVE, CONTROL | Flow CONTROL VALVE at JET A1 Loading Bay J |  | CNTR_VLV | M30SYS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938425 | M30FV261H | VALVE, CONTROL | Flow CONTROL VALVE at JET A1 Loading Bay H |  | CNTR_VLV | M30SYS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938426 | M30LY161A | VALVE, SOLENOID | SOV FOR LEVEL FOR FILTER COALSECER 400-L-007 |  | CNTR_VLV | M30LEVEL | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938427 | M30LY162A | VALVE, SOLENOID | Solenoid valve for 30-LV-323 |  | CNTR_VLV | M30LEVEL | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938428 | M30PV261H | VALVE, PNEUMATIC | ESD Valve for Loading Bay 261H |  |  | M30VALVE | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938429 | M30PT261H | TRANSMITTER, PRESSURE, 0-16 BAR | PR.TRANSMTR. Pr. at Loading Bay H |  |  | M30PRESS | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938430 | M30PV262J | VALVE, PNEUMATIC | ESD Valve for Loading Bay 262J |  |  | M30VALVE | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938431 | M30PV262H | VALVE, PNEUMATIC | ESD Valve for Loading Bay 262H |  |  | M30VALVE | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938445 | M30PV261J | VALVE, PNEUMATIC | ESD Valve for Loading Bay 261J |  |  | M30VALVE | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938446 | M30PT261J | TRANSMITTER, PRESSURE, 0-16 BAR | PR.TRANSMTR. Pr. at Loading Bay J |  |  | M30PRESS | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938447 | MQ600G077 | PUMP, CENTRIFUGAL, Vertical Submersible , Sump Pump , Slops , 0.794 - 0.912 , Sp | Sump Pump Mussafah Alain Multi Product Pipeline |  | PUCE | MQ600PUMP | 3 | PUCE | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938448 | MQ600G077 | PUMP, CENTRIFUGAL, Vertical Submersible , Sump Pump , Slops , 0.794 - 0.912 , Sp | Sump Pump Mussafah Alain Multi Product Pipeline |  | PUCE | MQ600PUMP | 3 | PUCE | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938450 | M30TE261H | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 0-200 DEG C , PLATINUM | Temp. at Loading Bay H |  | TEMP_ELE | M30MISC | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131421 | M400FACP002 | PANEL,FIRE ALARM, MINERVA | FIRE ALARM CONTROL PANEL AT SUB STATION BUILDING P&TD. |  | F&G_PNL | M400SUBSTN | 1 | F&G_PNL | 617101-310510 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FACP002-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 07/09/18 | MFPS-PM01.M3
969131423 | M400FACP004 | PANEL,FIRE ALARM, MINERVA | FIRE ALARM CONTROL PANEL AT OLD ADMIN BUILDING- P&TD. |  | F&G_PNL | MADMIN | 1 | F&G_PNL | 617101-310510 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FACP004-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 09/09/18 | MFPS-PM01.M3
938590 | M400T151 | ANTISTATIC CHEMICAL DOSING TANK | ANTISTATIC CHEMICAL DOSING TANK |  | TK |  | 3 | TK | 623101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 50 | 1 | 10 | 5 | 6.0969 | high | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938591 | M400PT17A | TRANSMITTER, PRESSURE, ELECTRONIC , 4-20MA , 10.5 - 36vdc , 1/2" - 14 NPTF , M20 | PLAN 53 B - PRESSURE TXS (SEAL PRESSURE/M400P017A) | 933876 | PRES_TX | M400P017A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT17A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/11/18 | MC-PM-007-Y1
938592 | M400PT17B | TRANSMITTER, PRESSURE, ELECTRONIC , 4-20MA , 10.5 - 36vdc , 1/2" - 14 NPTF , M20 | PLAN 53 B - PRESSURE TXS (SEAL PRESSURE/M400P017B) | 933877 | PRES_TX | M400P017B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT17B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/11/18 | MC-PM-007-Y1
938593 | M400PG17B | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | SEAL OIL PRESSURE GAUGE FOR PUMP M400P17B | 933877 |  | M400P017B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938594 | M400LG551 | GAUGE, LEVEL, REFLEX | Gas Oil Storage Tank 400-V-179 |  | INDICATR | M400LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938595 | M400LT802 | TRANSMITTER, LEVEL , 4-20MA , 10-32VDC | LEVEL TX FOR ANTI STATIC PACKAGE (M400ME001) | 932932 | LVL_TX | M400ME001 | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400LT802-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/08/18 | MC-PM-004-Y1
938596 | M400LT806 | TRANSMITTER, LEVEL , 4-20MA , 10-32VDC | LEVEL TX FOR INJECT GREEN DYE IN ULG-95 (M400ME002 | 932933 | LVL_TX | M400ME002 | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400LT806-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/08/18 | MC-PM-004-Y1
969131428 | M400HSSD002 | DETECTOR,FIRE PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT CONSOLE ROOM PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131435 | M400XSP002 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, 24VDC, YES | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938599 | M400T152 | TANK | GREEN DYE TANK |  | TK |  | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 50 | 1 | 10 | 5 | 6.0969 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938601 | M400T153 | TANK | RED DYE TANK |  | TK |  | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 50 | 1 | 10 | 5 | 6.0969 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938611 | M400ME008 | HVAC INERTIA SAND FILTER MOTOR OF MCR AIR CONDITIONER. | INERTIA SAND FILTER MOTOR OF AIR CONDITIONER MCR. |  | HVAC | MMCR | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400ME008-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 23/01/19 | ME-PM-LT1-6M
938612 | M400AY851 | COLORIMETER ANALYZER MSFH-AAIN MLTI PROD TIE-IN. | Mussafah-Al Ain Multi Product Tie-In P/L | 934842 | ANALYSER | M400AT851 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938613 | M400ME009 | HVAC INERTIA SAND FILTER MOTOR OF S/S AIR CONDITIONER. | INERTIA SAND FILTER MOTOR OF AIR CONDITIONER S/S. |  | HVAC | MS/S | 3 | HVAC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400ME009-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/01/19 | ME-PM-LT1-6M
938614 | M400DI301 | ANALYSER, DENSITY FOR TANK LEVEL. | Level for ULG 95 Tank 400-T-111 |  | ANALYSER | M400T111 | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | M400DI301-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/08/18 | MC-PM-014-M3
936133 | M400ME008A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936134 | M400ME008B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT AT CONTROL ROOM OF IRP MTERMINAL | 936088 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936135 | M400ME008A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936137 | M400ME009A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT AT S/S-400 IN IRP MTERMINAL | 936089 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936138 | M400ME009B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN S/S-400 AT IRP MTERMINAL | 936090 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936139 | M400ME008A | HUMIDIFIER | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936140 | M400ME008A | FILTER, AIR | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 | VESSEL | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936141 | M400ME008B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT AT CONTROL ROOM OF IRP MTERMINAL | 936088 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936142 | M400ME008A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936143 | M400ME008B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT AT CONTROL ROOM OF IRP MTERMINAL | 936088 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936144 | M400ME008A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936145 | M400ME008A | FAN | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936146 | M400ME008B | FAN | AIR COOLED CONDENSING UNIT AT CONTROL ROOM OF IRP MTERMINAL | 936088 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936147 | M400ME008A | FAN | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL | 936087 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936148 | M400ME008B | FAN | AIR COOLED CONDENSING UNIT AT CONTROL ROOM OF IRP MTERMINAL | 936088 |  | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936149 | M400ME009A | FAN | AIR COOLED CONDENSING UNIT AT S/S-400 IN IRP MTERMINAL | 936089 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936150 | M400ME009B | FAN | AIR COOLED CONDENSING UNIT IN S/S-400 AT IRP MTERMINAL | 936090 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936151 | M400ME009A | HUMIDIFIER | AIR COOLED CONDENSING UNIT AT S/S-400 IN IRP MTERMINAL | 936089 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936152 | M400ME009A | FILTER, AIR | AIR COOLED CONDENSING UNIT AT S/S-400 IN IRP MTERMINAL | 936089 | VESSEL | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936153 | M400ME010A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936154 | M400ME010B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936092 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936155 | M400ME010A | HVAC | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 | PACKAGE | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936156 | M400ME010B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936092 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936157 | M400ME010A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936158 | M400ME010B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936092 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936159 | M400ME010A | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936160 | M400ME010B | ELEMENT HEATER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936092 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936161 | M400ME010A | FILTER, AIR | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 | VESSEL | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936162 | M400ME010A | FAN | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936163 | M400ME010B | FAN | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936092 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936164 | M400ME010A | FAN | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936165 | M400ME010A | HUMIDIFIER | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING | 936091 |  | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936166 | MQ600ME001A | ELEMENT HEATER | Air Cooled Condensing Unit | 936093 |  | MQ600 | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936167 | MQ600ME001A | FAN | Air Cooled Condensing Unit | 936093 |  | MQ600 | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936168 | MQ600ME001B | FAN | Air Cooled Condensing Unit | 936094 |  | MQ600 | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936169 | MQ600ME001A | FILTER, AIR | Air Cooled Condensing Unit | 936093 | VESSEL | MQ600 | 4 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937766 | AA213RO147 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY IN ALAIN RECEIVING STATION, |  |  | AA13MISC | 3 | DP_TXTR | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937767 | AA213RO148 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY IN ALAIN RECEIVING STATION, |  |  | AA13MISC | 3 | DP_TXTR | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937772 | AA313RO149 | ORIFICE PLATE | AL AIN RECEIVING STATION ORIFICE PLATE ASSEMBLY |  |  | AA13MISC | 3 | DP_TXTR | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937773 | AA313RO150 | ORIFICE PLATE | AL AIN RECEIVING STATION ORIFICE PLATE ASSEMBLY |  |  | AA13MISC | 3 | DP_TXTR | 617101-310600 | IRPALAIN | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937774 | M400FE001 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 8" , 136.1MM , 6MM , 316 SS , 300 LB , | 400-P-021A Discharge Flow element | 939679 | ORIFICE | M400FI001 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FE001-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/12/18 | MC-PM-001-M6
937775 | M400FE002 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 8" , 136.1MM , 6MM , 316 SS , 300 LB , | 400-P-021B Discharge Flow element | 939680 | ORIFICE | M400FI002 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937776 | M400FE003 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 8" , 136.1MM , 6MM , 316 SS , 300 LB , | 400-P-021C Discharge Flow element | 939681 | ORIFICE | M400FI003 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937777 | M400FE004 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 12" , 175.2MM , 8MM , 316 SS , 300 LB , | Disch. Flow at 400-P-022A/B to 10-T-101/102/103/10 | 939682 | ORIFICE | M400FI004 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937779 | M400FE008 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 4" , 68.88MM , 3MM , 316 SS , 300 LB , | Slop Pump 400-P-024A Disch. flow element | 939683 | ORIFICE | M400FI008 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937780 | M400FE009 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 4" , 68.88MM , 3MM , 316 SS , 300 LB , | Slop Pump 400-P-024B Disch. Flow element | 939684 | ORIFICE | M400FI009 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937781 | M400RO001 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937782 | M400RO002 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937783 | M400RO003 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937784 | M400RO004 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937785 | M400RO005 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937786 | M400RO006 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937787 | M400RO007 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937788 | M400RO008 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937789 | M400RO009 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937790 | M400RO010 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937791 | M400RO011 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937792 | M400RO012 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937793 | M400RO013 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937794 | M400RO014 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937795 | M400RO015 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937796 | M400RO016 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937797 | M400RO017 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937798 | M400RO018 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937799 | M400RO019 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937800 | M400RO020 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937801 | M400RO021 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937802 | M400RO022 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937803 | M400RO023 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937804 | M400RO024 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937805 | M400RO025 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937806 | M400RO026 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937807 | M400RO027 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937808 | M400RO028 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937809 | M400RO029 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937810 | M400RO030 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937811 | M400RO031 | ORIFICE PLATE | ORIFICE PLATE ASSEMBLY |  |  | M400MISC | 3 | ORIFICE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935858 | M400LG417 | GLASS, LEVEL GAUGE, REFLEX , B-4 , 34MM WD X 190MM LG X 17MM THK , 100 BAR @ 40 | ULG95/98/GO/JET A1/KEROS M/L PUMP-LEVEL GAUGE | 935827 | INDICATR | M400P016B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935859 | M400LG462 | GLASS, LEVEL GAUGE, REFLEX , B-4 , 34MM WD X 190MM LG X 17MM THK , 100 BAR @ 40 | OFF SPEC JET A1 M/L PUMP-LEVEL GAUGE |  | INDICATR | M400P019 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935860 | M400LMP016A1 | Motor for Lube Oil Pump 'A' for 400MP016A | MOTOR,ELECTRIC, MOTOR FOR LUBE OIL PUMP, IP55, 3 KW, 50 HZ, 415 V, S1, EXn, 100LA2, 6206-2Z/C3, 2907 RPM, 3, 5.4 AMP, CCW, F, II A, 58 KG, T3, YES |  | MOTOR | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935861 | M400LMP016B1 | Motor for Lube Oil Pump 'A' for 400MP016B | Motor for Lube Oil Pump 'A' for 400MP016B |  | MOTOR | M400P016B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935862 | M400LMP016A2 | Motor for Lube Oil Pump 'B' for 400MP016A | MOTOR,ELECTRIC, Motor for Lube Oil Pump, IP55, 3 KW, 50 HZ, 415 V, S1, EXn, 100LA2, 66206-27-C3, B35, 2899 RPM, 3, 5.5 AMP, CCW, F, IIA ZONE2, 58 KG, T3, YES |  | MOTOR | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935863 | M400LMP016B2 | Motor for Lube Oil Pump 'B' for 400MP016B | MOTOR,ELECTRIC, Motor for Lube Oil Pump, IP55, 3 KW, 50 HZ, 415 V, S1, EXn, 100 LA2, 2899 RPM, 3, 5.5 AMP, CCW, F, IIA ZONE2, 58 KG, T3, YES |  | MOTOR | M400P016B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935864 | M400LMP019A1 | Motor for Lube Oil Pump 'A' for 400MP019 | MOTOR,ELECTRIC, LUBE OIL PUMP, IP55, 2.2 KW, 50 HZ, 415 V, S1, EXn, 100LA4, 6206-27-C3, B35, 1441 RPM, 3, DELTA, 4.4 AMP, CCW, F, IIA ,ZONE2, 58 KG, T3 |  | MOTOR | M400P019 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935865 | M400LMP019A2 | Motor for Lube Oil Pump 'B' for 400MP019 | MOTOR,ELECTRIC, LUBE OIL PUMP, IP55, 2.2 KW, 50 HZ, 415 V, S1, EXn, 100 LA4, B35, 1441 RPM, 3, DELTA, 4.4 AMP, CCW, F, IIA, ZONE2, 58 KG, T3 |  | MOTOR | M400P019 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936087 | M400ME008A | HVAC, DUCTED TYPE SPLIT A/C, 120 TONNS, R22, 415V, 1.0kW, RAUC D12, TRANE, CSHA150K0E00, 12 | AIR COOLED CONDENSING UNIT IN CONTROL ROOM OF IRP MTERMINAL |  | PACKAGE | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936088 | M400ME008B | HVAC, DUCTED TYPE SPLIT, 120 TONNS, R22, 415V, 1.0kW, RAUC D12, TRANE, CSHA150K0E00, 12NOS | AIR COOLED CONDENSING UNIT AT CONTROL ROOM OF IRP MTERMINAL |  | PACKAGE | MMCR | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936089 | M400ME009A | HVAC, DUCTED TYPE SPLIT A/C, 120 TONS, R22, 415V, 1.0kW, RAUC D12, TRANE, CSHA150K0E00, 12NOS | AIR COOLED CONDENSING UNIT AT S/S-400 IN IRP MTERMINAL |  | PACKAGE | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936090 | M400ME009B | HVAC, 120 TONS, R22, 415V, 1.0KW, RAUC D12, TRANE, CSHA150K0E00, 12NOS | AIR COOLED CONDENSING UNIT IN S/S-400 AT IRP MTERMINAL |  | PACKAGE | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936091 | M400ME010A | HVAC, DUCTED TYPE SPLIT A/C, 30 TON, R22, 415V, 1.0kW, RAUC C30, TRANE, CSHA140K0E00, 3 | AIR COOLED CONDENSING UNIT IN ADMINISTRATION BUILDING |  | PACKAGE | M400PKG | 4 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 5 | 1 | 10 | 3.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937666 | M400CAB001 | PANEL, 482.6MM LG X 43.7MM WD X 29.6MM HT , STEEL / THERMOPLASTIC | VOICE AND DATA CABINET - MUSSAFAH PLCR |  | PA_SYS | M400SYS | 1 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937667 | M400CAB002 | PANEL, 482.6MM LG X 43.7MM WD X 29.6MM HT , STEEL / THERMOPLASTIC | VOICE AND DATA CABINET - ADMIN BUILDING-MUSSAFAH |  | PA_SYS | M400SYS | 1 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937668 | M400CAB003 | PANEL, 482.6MM LG X 43.7MM WD X 29.6MM HT , STEEL / THERMOPLASTIC | VOICE AND DATA CABINET - SUBSTATION MUSSAFAH |  | PA_SYS | M400SYS | 1 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937669 | M400CAB004 | PANEL, 482.6MM LG X 43.7MM WD X 29.6MM HT , STEEL / THERMOPLASTIC | VOICE AND DATA CABINET - FIRESTATION MUSSAFAH |  | PA_SYS | M400SYS | 1 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937670 | M400CAB005 | PANEL, 482.6MM LG X 43.7MM WD X 29.6MM HT , STEEL / THERMOPLASTIC | VOICE AND DATA CABINET - WAREHOUSE BLDG MUSSAFAH |  | PA_SYS | M400SYS | 1 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937671 | M400CAB006 | PANEL, 482.6MM LG X 43.7MM WD X 29.6MM HT , STEEL / THERMOPLASTIC | VOICE AND DATA CABINET - GUARD HOUSE MUSSAFAH |  | PA_SYS | M400SYS | 1 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937672 | M400CAB007 | PANEL, 482.6MM LG X 43.7MM WD X 29.6MM HT , STEEL / THERMOPLASTIC | VOICE AND DATA CABINET - AL AIN |  | PA_SYS | M400SYS | 1 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937673 | MQ600CAB001 | SYSTEM | VOICE AND DATA CABINET : AGI MAQTA |  |  | MQ600SYS | 1 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937675 | AT800CAB001 | SYSTEM - VOICE AND DATA CABINET | VOICE AND DATA CABINET - ABUDHABI INTL' AIRPORT |  |  | AT800SYS | 3 | TELECOM | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937681 | M400ELP003 | DISTRIBUTION BOARD LIGHTING IN TRANSFER PUMP HOUSE | LIGHTING POWER DISTR. BOARD AT MPH1-HAZ. AREA |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP003-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 27/09/18 | ME-PNL1-PM-M6
937682 | M400ELP012 | DISTRIBUTION BOARD,LIGHTING, MAIN LINE PUMP HOUSE (400-MPH-001), 400-SS-001,400-PC-001, 63AAMP, 63AAMP, 6, B, 125AAMP, 125AAMP, 1.08kWAMP, 4C X 16 MM2, Ex de | LIGHTING POWER DISTR.BOARD AT MPH1 HAZ. AREA |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400ELP012-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
937683 | M400LP003 | DISTRIBUTION BOARD LIGHTING IN S/S-400 SWGR.ROOM | LIGHTING & SMALL POWER DISTR.BOARDS-HAZ. AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP003-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/10/18 | ME-PNL1-PM-M6
937684 | M400LP008 | DISTRIBUTION BOARD LIGHTING | LIGHTING & SMALL POWER DISTR.BOARDS-HAZ. AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP008-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
937685 | M400LP020 | DISTRIBUTION BOARD LIGHTING | LIGHTING & SMALL POWER DISTR. BOARDS-HAZ. AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400LP020-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 19/10/18 | ME-PNL1-PM-M6
937693 | M400ELP004 | DISTRIBUTION BOARD,LIGHTING, FIRE WATER PUMP HOUSE (400-FPH-001), 400-SS-001,400-PC-001,5ER5, 63A, 63AAMP, 8, B, 125AAMP, 125AAMP, 4.26kWAMP, 4C X 35 SQMM, WP | OUTDOOR EMERGENCY LIGHTING PANEL IN FIRE WATER PUMP HOUSE(TANK AREA) |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400ELP004-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
937694 | M400ELP008 | DISTRIBUTION BOARD,LIGHTING, FIRE WATER PUMP HOUSE (400-FPH-001), 400-SS-001,400-PC-001,4EF3, 63A, 63AAMP, 8, B, 125AAMP, 125AAMP, 4.26kWAMP, 4C X 35 SQMM, YES, WP | LIGHTING&SMALL POWER DISTRIBUTION BOARD-SAFE AREA |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP008-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 01/10/18 | ME-PNL1-PM-M6
937695 | M400LP005 | DISTRIBUTION BOARD LIGHTING | LIGHTING POWER DISTRIBUTION BOARD AT FPH1-SAFE AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP005-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 09/10/18 | ME-PNL1-PM-M6
937696 | M400LP006 | DISTRIBUTION BOARD LIGHTING | LIGHTING & SMALL POWER DISTRIBUTION BOARD-SAFE AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP006-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
937697 | M400LP007 | DISTRIBUTION BOARD LIGHTING IN S/S-400 FOR EXISTING TANK LTG. | LIGHTING & SMALL POWER DISTRIBUTION BOARD-SAFE AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP007-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 11/10/18 | ME-PNL1-PM-M6
937698 | M400LP010 | DISTRIBUTION BOARD LIGHTING | LIGHTING POWER DISTRIBUTION BOARD AT FPH1-SAFE AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP010-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 13/10/18 | ME-PNL1-PM-M6
937699 | M400LP011 | DISTRIBUTION BOARD LIGHTING | LIGHTING POWER DISTRIBUTION BOARD AT FPH1-SAFE AREA. |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400LP011-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
937700 | M400PDB003 | DISTRIBUTION BOARD LIGHTING | LIGHTING&SMALL POWER DISTRIBUTION BOARD-SAFE AREA |  | LIGHT | M400SCB | 3 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937701 | M400PDB004 | DISTRIBUTION BOARD LIGHTING | LIGHTING&SMALL POWER DISTRIBUTION BOARD-SAFE AREA |  | LIGHT | M400SCB | 3 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937702 | M400PP001 | DISTRIBUTION BOARD LIGHTING | LIGHTING AND SMALL POWER DISTRIBUTION BOARD-SAFE AREA |  | LIGHT | M400SCB | 3 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937703 | MQ600LP001 | DISTRIBUTION BOARD LIGHTING | LIGHTING&SMALL POWER DISTRIBUTION BOARD-SAFE AREA |  | LIGHT | MQ600SCB | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937718 | M400MVP001 | PANEL,ELEC POWER, DISTRIBUTION | MOV DISTRIBUTION BOARD |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP001-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/08/18 | ME-PNL1-PM-1Y
937719 | M400MVP002 | PANEL,ELEC POWER, DISTRIBUTION | MOV DISTRIBUTION BOARD AT MAIN LINE PUMP HOUSE AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP002-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 19/08/18 | ME-PNL1-PM-1Y
937720 | M400MVP003 | PANEL,ELEC POWER, DISTRIBUTION | MOV DISTRIBUTION BOARD AT SCRAPPER AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP003-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 20/08/18 | ME-PNL1-PM-1Y
937721 | M400MVP004 | PANEL,ELEC POWER, DISTRIBUTION | MOV DISTRIBUTION BOARD IN SCRAPPER AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP004-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 21/08/18 | ME-PNL1-PM-1Y
937722 | M400MVP005 | PANEL,ELEC POWER, DISTRIBUTION | MOV DISTRIBUTION BOARD AT MAIN PUMP HOUSE AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP005-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 22/08/18 | ME-PNL1-PM-1Y
937723 | M400MVP006 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION PANEL AT MAIN PUMP HOUSE AAREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP006-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 23/08/18 | ME-PNL1-PM-1Y
937724 | M400MVP007 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD AT MAIN PUMP HOUSE AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP007-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 24/08/18 | ME-PNL1-PM-1Y
937725 | M400MVP008 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD AT MAIN LINE PUMP HOUSE AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP008-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/08/18 | ME-PNL1-PM-1Y
937726 | M400MVP009 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD AT SCRAPPER AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP009-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/08/18 | ME-PNL1-PM-1Y
937727 | M400MVP010 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-111 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP010-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 27/08/18 | ME-PNL1-PM-1Y
937728 | M400MVP011 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-112 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP011-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 28/08/18 | ME-PNL1-PM-1Y
937729 | M400MVP012 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR 400-T-112 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP012-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 29/08/18 | ME-PNL1-PM-1Y
937730 | M400MVP013 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-113 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP013-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 30/08/18 | ME-PNL1-PM-1Y
937731 | M400MVP014 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-114 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP014-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 31/08/18 | ME-PNL1-PM-1Y
937732 | M400MVP015 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-115 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP015-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 01/09/18 | ME-PNL1-PM-1Y
937733 | M400MVP016 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-116 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP016-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 02/09/18 | ME-PNL1-PM-1Y
937734 | M400MVP017 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR 400-T-117 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP017-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 03/09/18 | ME-PNL1-PM-1Y
937735 | M400MVP018 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-118 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP018-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
969265895 | PL100GDH621 | GAS DETECTORS | GAS DETECTORS |  | FG_DET | PL100GD | 3 | FG_DET | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265896 | PL100GDH622 | GAS DETECTORS | GAS DETECTORS |  | FG_DET | PL100GD | 3 | FG_DET | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265897 | PL100GTD2001 | GAS TIGHT DAMPER ACTUATOR (EX-PROOF) | GAS TIGHT DAMPER ACTUATOR (EX-PROOF) |  | CNTR_VLV | PL100CNTRVL | 3 | CNTR_VLV | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265898 | PL100HCP00120 | HVAC CONTROL PANEL | HVAC CONTROL PANEL |  | BLDGS | PL100SYS | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265907 | PL100MOV400AA | MOTOR OPERATED VALVE (100-FT-400 METERING SKID) | MOV (RUWAIS) SHEWIHAT RECIVING STATION.(100-FT-400 METERING SKID) |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400AA-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265910 | PL100MOV400BB | MOTOR OPERATED VALVE (100-FT-400 METERING SKID) | MOV (RUWAIS) SHEWIHAT RECIVING STATION. (100-FT-400 METERING SKID) |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400BB-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265918 | PL100PA00120B | SPLIT TYPE AIR CONDITIONER | SPLIT TYPE AIR CONDITIONER |  | HVAC | PL100HVAC | 3 | HVAC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265919 | PL100PA00220 | SPLIT TYPE AIR CONDITIONER | SPLIT TYPE AIR CONDITIONER |  | HVAC | PL100HVAC | 3 | HVAC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IAS59160 | M10LZALL072 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-107 | TNK56616 | LVL_SWT | M10T107 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL072-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/10/18 | MC-PM-024-M6
IAS59167 | M50PSH157F | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-107 | TNK56616 | PRES_SWT | M10T107 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH157F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/06/19 | MC-PM-009-Y1
IAS59168 | M50PSL137F | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FOAM LOW PRESSURE SWITCH FOR TANK T-107 | TNK56616 | PRES_SWT | M10T107 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL137F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/06/19 | MC-PM-009-Y1
IAS59169 | M50PSH157W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-107 | TNK56616 | PRES_SWT | M10T107 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH157W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/06/19 | MC-PM-009-Y1
IAS59170 | M50PSL137W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-107 | TNK56616 | PRES_SWT | M10T107 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL137W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/06/19 | MC-PM-009-Y1
IAS59180 | M10LZALL082 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-108 | TNK56634 | LVL_SWT | M10T108 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL082-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 30/10/18 | MC-PM-024-M6
IAS59181 | M10LZAHH083 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-108 | TNK56634 | LVL_SWT | M10T108 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZAHH083-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 30/10/18 | MC-PM-024-M6
IAS59189 | M50PSH158W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-108 | TNK56634 | PRES_SWT | M10T108 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH158W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/06/19 | MC-PM-009-Y1
IAS59190 | M50PSL138W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-108 | TNK56634 | PRES_SWT | M10T108 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL138W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/06/19 | MC-PM-009-Y1
IAS59197 | M10LZALL092 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-109 | TNK56645 | LVL_SWT | M10T109 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL092-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/10/18 | MC-PM-024-M6
IAS59198 | M10LZAHH093 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-109 | TNK56645 | LVL_SWT | M10T109 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZAHH093-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/10/18 | MC-PM-024-M6
IAS59206 | M50PSH159W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , EXPLOS | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-109 | TNK56645 | PRES_SWT | M10T109 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH159W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 16/06/19 | MC-PM-009-Y1
IAS59207 | M50PSL139W | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-109 | TNK56645 | PRES_SWT | M10T109 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL139W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/06/19 | MC-PM-009-Y1
IAS59215 | M10LZALL102 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-110 | TNK56656 | LVL_SWT | M10T110 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL102-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/10/18 | MC-PM-024-M6
IAS59216 | M10LZAHH103 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-110 | TNK56656 | LVL_SWT | M10T110 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZAHH103-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/10/18 | MC-PM-024-M6
IAS59225 | M50PSH160W | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-110 | TNK56656 | PRES_SWT | M10T110 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH160W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/06/19 | MC-PM-009-Y1
IAS59226 | M50PSL140W | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-110 | TNK56656 | PRES_SWT | M10T110 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL140W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/06/19 | MC-PM-009-Y1
IAS59251 | M40LSHL720 | SWITCH, DISPLACER, RF FLANGE , 250VA , SPDT , ANSI 150 , 4" , VERTICAL , 40 DE | LEVEL SWITCH FOR SLOPS LOADING PUMP 172 ADNOC DIST. | PMC56668 | LVL_SWT | M40P172 | 3 | LVL_SWT | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M40LSHL720-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/05/19 | MC-PM-006-Y1
IAS59254 | M40LSHL730 | SWITCH, DISPLACER, RF FLANGE , 250VA , SPDT , ANSI 150 , 4" , VERTICAL , 40 DE | LEVEL SWITCH FOR SLOPS LOADING PUMP 173 ADNOC DIST. | PMC56670 | LVL_SWT | M40P173 | 2 | LVL_SWT | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M40LSHL730-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/05/19 | MC-PM-006-Y1
IAS59256 | M50PSL136F | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FOAM LOW PRESSURE SWITCH FOR TANK T-106 | TNK56600 | PRES_SWT | M10T106 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL136F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/06/19 | MC-PM-009-Y1
IGP58260 | S15PG124 | GAUGE, PRESSURE, 0-40 BAR , 150MM , 1/2" NPT , 304 SS , 316 SS , BOTTOM , DIRECT | PRESSURE GAUGE OF PRESSURE RELIEF VALVE FOR SCRAPE |  | INDICATR | S15R03 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP58263 | S15PG126 | GAUGE, PRESSURE, 0-40 BAR , 150MM , 1/2" NPT , 304 SS , 316 SS , BOTTOM , DIRECT | PRESSURE GAUGE AFTER PIG LAUNCHER |  | INDICATR | S15R03 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP58264 | S15PG127 | GAUGE, PRESSURE, BOURDON , 0-40 BAR , 150MM , 1/2" NPT , 304 SS , 316 SS , BOTTO | PRESSURE GAUGE AFTER 15MOV116 |  | INDICATR | S15R03 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP58338 | S21PG104A | GAUGE, PRESSURE, BOURDON , 0-60 KG/CM2 , 150MM , 1/2" NPT , 304 SS , SS , BOTTOM | INLET PRESSURE GAUGE TO PIG LAUNCHER |  | INDICATR | S21R02 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP58339 | S21PG106A | GAUGE, PRESSURE, BOURDON , 0-60 KG/CM2 , 150MM , 1/2" NPT , 316 SS , 316 SS , BO | PRESSURE GAUGE OF PIG LAUNCHER |  | INDICATR | S21R02 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP58342 | S21PG105 | GAUGE, PRESSURE, 0-60 KG/CM2 , 150MM , 1/2" NPT , 316 SS , SS , BOTTOM , DIRECT | OUTLET PRESSURE GAUGE OF PIG LAUNCHER |  | INDICATR | S21R02 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP58343 | S21PG107 | GAUGE, PRESSURE, 0-60 BAR , 6" (150MM) , 1/2" , 316 SS , SS , BOTTOM , DIRECT , | OUTLET PRESSURE GAUGE FROM SANT TO AVIATION DEPOT |  | INDICATR | S21R02 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131473 | M400XSP040 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131475 | M400XSP042 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131476 | M400XSP043 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM BETWEN FLOOR AND FALSE FLORR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131481 | M400XSP048 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TELECOM ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131482 | M400XSP049 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TELECOM ROOM BETWEN FLOOR AND FALSE FLORR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131484 | M400XSP051 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR ENGINEERING ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131487 | M400XSP054 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR OPERATOR ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131496 | M400XSP063 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR CORRIDOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131497 | M400XSP064 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TOILET-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131500 | M400XSP067 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR AIR LOCK LOBBY-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131503 | M400XSP070 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR HVAC AIR INTAKE DUCT-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131504 | M400XSP071 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR HVAC AIR INTAKE DUCT-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131505 | M400XSP072 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR HVAC AIR INTAKE DUCT-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131364 | M400KBD001 | CONTROLLER, CLOSED CIRCUIT TELEVISION SYSTEM | CONTROLLER, CLOSED CIRCUIT TELEVISION SYSTEM |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400KBD001-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131934 | MQ600XAC202 | CALL POINT, YES, BREAK GLASS MANUAL, RED | MANUAL CALL POINT AT PIG LAUNCHER AREA MAQTA TERMINAL |  | PB_HS-MC | MQ600FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XAC202-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131947 | MQ600XSP010 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131952 | MQ600XSP015 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT HVAC AIR INTAKE DUCT OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275984 | M400VS918 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 118 | 939611 | VALCH | M400T118 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175982 | M410EG031A | FIRE WATER PUMP- DIESEL ENGINE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN |  | DENGINE | M410P031A | 1 | DENGINE | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 50 | 1 | 10 | 6.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175983 | M410EG031B | FIRE WATER PUMP- DIESEL ENGINE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN |  | DENGINE | M410P031B | 1 | DENGINE | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 50 | 1 | 10 | 6.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175984 | M410EG031C | FIRE WATER PUMP- DIESEL ENGINE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN |  | DENGINE | M410P031C | 1 | DENGINE | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 50 | 1 | 10 | 6.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175985 | M410EG031D | FIRE WATER PUMP- DIESEL ENGINE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN |  | DENGINE | M410P031D | 1 | DENGINE | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 50 | 1 | 10 | 6.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175986 | M410EG031E | FIRE WATER PUMP- DIESEL ENGINE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN |  | DENGINE | M410P031E | 1 | DENGINE | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 50 | 1 | 10 | 6.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175987 | M410EG031F | FIRE WATER PUMP- DIESEL ENGINE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN |  | DENGINE | M410P031F | 1 | DENGINE | 617101-310510 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 50 | 1 | 10 | 6.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205038 | M410T031A | PRESSURE TRANSMITTER | DIESEL DAY TANK (FIREWATER PUMP) | 969147435 | PRES_TX | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175988 | M410EG031G | FIRE WATER PUMP- DIESEL ENGINE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN |  | DENGINE | M410P031G | 1 | DENGINE | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 50 | 1 | 10 | 6.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938767 | M400FALL772 | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-772 |  | ALARMANC |  | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938768 | M400FALL861A | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-861A |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL861A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/04/19 | MC-PM-003-Y1
938769 | M400FALL861B | SYSTEM, FLOW ALARM AND ESD SHUTDOWN | Flow metering skid 400-FT-861B |  | ALARMANC | M400SYS | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400FALL861B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/04/19 | MC-PM-003-Y1
938770 | M400FE015 | ORIFICE, PLATE, SQUARE EDGE CONCENTRIC , 4" , 68.88MM , 3MM , 316 SS , 300 LB , | Gas Oil Storage Tank 400-V-179 |  | ORIFICE | M400MISC | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938771 | M400VE431A | PROBE, VIBRATION | VIBRATION FOR BEARING HOUSE (NCE) 400-P-018A | 935828 | VIBRE_TX | M400P018A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE431A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/08/18 | MC-PM-012-M3
938773 | M400VE433 | PROBE, VIBRATION | VIBRATION FOR MAINLINE PUMP 400-P-018A | 935828 | VIBRE_TX | M400P018A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE433-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 23/08/18 | MC-PM-012-M3
938774 | M400VE448 | PROBE, VIBRATION | VIBRATION FOR DE MAINLINE PUMP 400-P-018B | 935829 | VIBRE_TX | M400P018B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE448-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/09/18 | MC-PM-012-M3
938775 | M400TE431 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP. ELEMENT FOR MAINLINE PUMP 400-P-018A | 935828 | TEMP_ELE | M400P018A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE431-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/11/18 | MC-PM-010-Y1
938776 | M400TE432 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP. ELEMENT FOR MAINLINE PUMP 400-P-018A | 935828 | TEMP_ELE | M400P018A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE432-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 30/11/18 | MC-PM-010-Y1
938777 | M400TE437 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP. ELEMENT FOR MAINLINE PUMP 400-P-018A | 935828 | TEMP_ELE | M400P018A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE437-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/12/18 | MC-PM-010-Y1
938778 | M400TE438 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | TEMP. ELEMENT FOR MAINLINE PUMP 400-P-018-A. | 935829 | TEMP_ELE | M400P018A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE438-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/12/18 | MC-PM-010-Y1
938779 | M400TE440A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100, 3 WIRE, SINGLE , 100 OH | TEMP. ELEMENT FOR CASING MAINLINE PUMP 400-P-018A | 935828 | TEMP_ELE | M400P018A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE440A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/12/18 | MC-PM-010-Y1
969270742 | M410SN219001 | Spray Nozzle (K-factor 54.9) | Spray Nozzle (K-factor 54.9) |  | VESSEL | M410MISC | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270743 | M410SN219002 | Spray Nozzle (K-factor 75) | Spray Nozzle (K-factor 75) |  | VESSEL | M410MISC | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56528 | M50SPR101 | SPRINKLER, FIRE PROTECTION, BRASS , 80 | FIRE FIGHTING SPRINKLERS FOR TANK T-101 |  | F_N_S | M10T101 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936404 | M400P201A | PUMP, CENTRIFUGAL, HORIZONTAL , FIREWATER , FRESH WATER , 0.073 , CENTERLINE , B | FIRE WATER PUMPS-MAIN DIESEL DRIVEN |  | PUCE | M400PUMP | 1 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/05/19 | MC-PM-027-Y1
936405 | M400P201B | PUMP, CENTRIFUGAL, HORIZONTAL , FIREWATER , FRESH WATER , 0.073 , CENTERLINE , B | FIRE WATER PUMP (MAIN) |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/06/19 | MC-PM-027-Y1
936406 | M400P201C | PUMP, CENTRIFUGAL, HORIZONTAL , FIREWATER , FRESH WATER , 0.073 , CENTERLINE , B | FIRE WATER PUMP (MAIN) |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/07/19 | MC-PM-027-Y1
936407 | M400P201D | PUMP, CENTRIFUGAL, HORIZONTAL , FIREWATER , FRESH WATER , 0.073 , CENTERLINE , B | FIRE WATER PUMPS-MAIN DIESEL DRIVEN |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201D-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/08/18 | MC-PM-027-Y1
938793 | M400VT420 | PROBE, VIBRATION , 8MM , 0.5 M | COMPRESSOR CASING FOR M400P016B | 939262 | VIBRE_TX | M400VI420 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938794 | M400XGC201 | DETECTOR, GAS | Flammable GD for Mainline Pump 400-P-015A | 933874 | FG_DET | M400P015A | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC201-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 06/09/18 | MFPS-PM02.M3
938795 | M400XGC202 | DETECTOR, GAS | Flammable GD for Mainline Pump 400-P-015B | 933875 | FG_DET | M400P015B | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC202-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/09/18 | MFPS-PM02.M3
938796 | M400XGC203 | DETECTOR, GAS | Flammable GD for Mainline Pump 400-P-016A | 935826 | FG_DET | M400P016A | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC203-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 13/09/18 | MFPS-PM02.M3
938797 | M400XGC204 | DETECTOR, GAS | Flammable GD for Mainline Pump 400-P-016B | 935827 | FG_DET | M400P016B | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC204-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 15/09/18 | MFPS-PM02.M3
938798 | M400XGC205 | DETECTOR, GAS | Flammable GD for Inter Tank Transfer Pump 400P021A | 934051 | FG_DET | M400P021A | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC205-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 20/09/18 | MFPS-PM02.M3
938799 | M400XGC206 | DETECTOR, GAS | Flammable GD for Inter Tank Transfer Pump 400P021B | 934052 | FG_DET | M400P021B | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC206-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 22/09/18 | MFPS-PM02.M3
938909 | M400VT465 | PROBE, VIBRATION , 8MM , 0.5 M | COMPRESSOR CASING FOR M400P019 | 935830 | VIBRE_TX | M400VI465 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969257161 | M410P010 | SEAL FLUSH SYSTEM FOR JET A1 SUMP PUMP | JET A1 SUMP PUMP ON 410V004. | 969147454 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P010-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-7-Y1
969257165 | M410P007C | SEAL FLUSH SYSTEM FOR ULG 91/95 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP | 969147448 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007C-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/11/18 | MM-PM-7-Y1
969257169 | M410P014B | SEAL FLUSH SYSTEM FOR JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP | 969147452 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-4-Y1
969257168 | M410P014A | SEAL FLUSH SYSTEM FOR JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP | 969147451 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-4-Y1
935371 | SADIAVS2V1 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE 10" AT VALVE STATION # 2 AT KM 2.5 |  |  | SADIAVS2 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131962 | MQ600XHE001 | DETECTOR,FIRE PROTECTION, HEAT, YES | HEAT DETECTOR AT BATTERY ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131963 | MQ600XHE002 | DETECTOR,FIRE PROTECTION, HEAT, YES | HEAT DETECTOR AT BATTERY ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130728 | M400VSD16BTR | TRANSFORMER,DISTRIBUTION, VSD MOTOR, 2000 KVA, DYN 11, 50 HZ, 3, 3300, 1800, 350 AMP, 321 AMP, 7.2/20/60 KV, 7.2/20/60 KV, OFF ,LOAD, ONAN, 5700 KG | INPUT CONVERTER TRANSFORMER FOR 16B VSD MOTOR |  | TRANSFMR | M400SCB | 2 | TRANSFMR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | M400VSD16BTR-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 20/10/18 | ME-PM-009-M6
969130733 | M400EP001 | PANEL,CONTROL | DG SET CONTROL PANEL IN S/S-400,415V,500 KVA, |  | GENRATOR | M400SCB | 1 | GEN | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 1 | 100 | 5 | 100 | 50 | 8.3979 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131119 | M400LP006Y101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT EAST SIDE OF SUB STATION 400 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131120 | M400LP006B101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT EAST SIDE OF SUB STATION 400 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130737 | M400RTCC001 | RTCC FOR TRANSFORMER 400TMM001A | RTCC FOR TRANSFORMER 400TMM001A |  | TRANS | M400TMM001A | 3 | TRANSFMR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131166 | M400LP006B302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SUB STATION SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131229 | M400LP006B401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SOUTH BOUNDARY WALL |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130730 | M400LP001 | DISTRIBUTION BOARD,LIGHTING, SUB STATION 400 SWITCH GEAR ROOM, SUB STATION 400, 10, ELCB F/B, 12KW AMP | DISTRIBUTION BOARD,LIGHTING, SUBSTATION 400 SWITCH GEAR ROOM, SUB STATION 400 |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP001-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/10/18 | ME-PNL1-PM-M6
969130731 | M400ELP001 | DISTRIBUTION BOARD,LIGHTING, FIRE & SAFETY BUILDING, S/S-400,400-PC-001,BUS-C, 7ER3 | INDOOR EMERGENCY LIGHTING PANEL IN FIRE & SAFETY BUILDING. |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP001-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/09/18 | ME-PNL1-PM-M6
969130732 | M400ELP002 | DISTRIBUTION BOARD,LIGHTING, SUBSTATION-400, S/S-4008, 8EF3 | INDOOR EMERGENCY LIGHTING PANEL IN SUB STATION 400 |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP002-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
969130738 | M400RTCC002 | RTCC FOR TRANSFORMER 400TMM001B | RTCC FOR TRANSFORMER 400TMM001B |  | TRANS | M400TMM001B | 2 | TRANS | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131964 | MQ600BATT001A | BATTERY,BANK, Ni-Cad, VN 285-2, 20xVN285-2, 285 AH, 1.14 V, 3079 A, YES | BATTERY BANK FOR 600-UPS-DC-001 |  | BATTERY | MQ600UPSDC001 | 1 | BATTERY | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600BATT001A-ME1 | INACTIVE | ELEC | PM | EDS | 3 | MONTHS | 05/07/18 | ME-PM-001-M3
937736 | M400MVP019 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-119 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP019-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 05/09/18 | ME-PNL1-PM-1Y
937737 | M400MVP020 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR TANK 400-T-120 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP020-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
937738 | M400MVP021 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD IN TRANSFER PUMP HOUSE AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP021-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 07/09/18 | ME-PNL1-PM-1Y
937739 | M400MVP022 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD IN TRANSFER PUMP HOUSE AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP022-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
937740 | M400MVP023 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD IN TRANSFER PUMP HOUSE AREA |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP023-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 09/09/18 | ME-PNL1-PM-1Y
937741 | M400MVP025 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-106 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP025-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 11/09/18 | ME-PNL1-PM-1Y
937742 | M400MVP026 | PANEL,ELEC POWER, DISTRIBUTION, YES | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-105 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP026-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
937743 | M400MVP027 | DISTRIBUTION BOARD LIGHTING | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-106 |  | SWBOARD | M400SCB | 3 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP027-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 13/09/18 | ME-PNL1-PM-1Y
937744 | M400MVP028 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-107 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP028-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
937745 | M400MVP029 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-101 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP029-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 15/09/18 | ME-PNL1-PM-1Y
937746 | M400MVP030 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-102 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP030-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
937747 | M400MVP031 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-103 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP031-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 17/09/18 | ME-PNL1-PM-1Y
937748 | M400MVP032 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-104 |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP032-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
937749 | M400MVP033 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-109. |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP033-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 19/09/18 | ME-PNL1-PM-1Y
937750 | M400MVP034 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-110. |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP034-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 26/10/18 | ME-PNL1-PM-1Y
937751 | M400MVP035 | PANEL,ELEC POWER | MOV DISTRIBUTION BOARD NEAR EXISTING TANK T-108. |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MVP035-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 21/09/18 | ME-PNL1-PM-1Y
FFP57517 | M50XMC001 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-101 |  | PB_HS-MC | M10T101 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC001-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 25/10/18 | MFPS-PM07.M3
FFP57518 | M50XMC002 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-101 |  | PB_HS-MC | M10T101 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC002-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 23/10/18 | MFPS-PM07.M3
FFP57525 | M50XMC004 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP67 , BA | MANUAL CALL POINT FOR TANK T-102 |  | PB_HS-MC | M10T102 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC004-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 06/08/18 | MFPS-PM07.M3
969274291 | M400VDR901 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 117 | 939611 | VALCH | M400T118 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969274292 | M400VDR902 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 119 | 939612 | VALCH | M400T119 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969274293 | M400VDR903 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 120 | 939613 | VALCH | M400T120 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131704 | M400XHD204B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-016B |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD204B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 12/08/18 | MFPS-PM05.M3
969131705 | M400XHD205A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR INTER TANK TRANSFER PUMP 400-MP-021A |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD205A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 12/08/18 | MFPS-PM05.M3
969131706 | M400XHD205B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR INTER TANK TRANSFER PUMP 400-MP-021A |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD205B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 15/08/18 | MFPS-PM05.M3
969131709 | M400XHD207A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR INTER TANK TRANSFER PUMP 400-MP-021C |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD207A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 19/08/18 | MFPS-PM05.M3
969131710 | M400XHD207B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR INTER TANK TRANSFER PUMP 400-MP-021C |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD207B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 19/08/18 | MFPS-PM05.M3
969131711 | M400XHD210A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-111 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD210A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 19/08/18 | MFPS-PM05.M3
969131712 | M400XHD210B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-111 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD210B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 22/08/18 | MFPS-PM05.M3
969131713 | M400XHD211A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-112 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD211A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 22/08/18 | MFPS-PM05.M3
969131715 | M400XHD212A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-113 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD212A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 26/08/18 | MFPS-PM05.M3
969131693 | M400XLF207 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE FOR TANKS T-113/114/115 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131716 | M400XHD212B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-113 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD212B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 26/08/18 | MFPS-PM05.M3
969131725 | M400XHD217A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-118 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD217A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 10/09/18 | MFPS-PM05.M3
969131728 | M400XHD218B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR ULG95 TANK-119 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD218B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 12/09/18 | MFPS-PM05.M3
969131731 | M400XHD221A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR SUMP TANK 400-V-176 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD221A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 26/09/18 | MFPS-PM05.M3
969131733 | M400XHD222A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR SUMP TANK 400-V-175 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD222A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 19/09/18 | MFPS-PM05.M3
969131734 | M400XHD222B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR SUMP TANK 400-V-175 |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD222B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 19/09/18 | MFPS-PM05.M3
969131742 | M400XFB001 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK NO. T-101 TO T-103 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131743 | M400XFB003 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK NO. T-102 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131694 | M400XLF208 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE FOR TANKS T-111/112/116 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131697 | M400XHD201A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-015A |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD201A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/08/18 | MFPS-PM05.M3
969131703 | M400XHD204A | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR MAIN LINE PUMP 400-MP-016B |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD204A-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 12/08/18 | MFPS-PM05.M3
969131708 | M400XHD206B | DETECTOR,FIRE PROTECTION, RATE OF RISE TEMPERATURE, YES | LINEAR HEAT DETECTOR FOR INTER TANK TRANSFER PUMP 400-MP-021B |  | FG_DET | M400TMR001 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XHD206B-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 15/08/18 | MFPS-PM05.M3
969131738 | M50XES003 | HORN, SOUNDER, 24VDC, YES | SOUNDER NEAR TANK NO. T-103 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131740 | M50XES021 | HORN, SOUNDER, 24VDC, YES | SOUNDER NEAR TANK NO. T-06 & T-110 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131741 | M50XFB001 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE NEAR TANK NO. T-101 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131747 | M400XFB012 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK NO. T-105 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131735 | M400TMR001 | PANEL,FIRE ALARM, TMP PANEL | TMR PLC PANEL IN RACK ROOM-PLCR BUILDING |  | F&G_PNL | M400FACP001 | 1 | F&G_PNL | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131748 | M400XFB021 | LIGHT, BEACON, RED | FLASHING BEACON - FIRE FOR TANK NO. T-106 |  | ALARMANC | M400FACP001 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132037 | PL300BATT004A | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-A =38 Nos FOR SV-4. |  | BATTERY | PL300BAT004 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132038 | PL300BATT004B | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-B =38 Nos FOR SV-4. |  | BATTERY | PL300BAT004 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132039 | PL300BATT005A | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-A =38 Nos FOR SV-5. |  | BATTERY | PL300BAT005 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936408 | M400P202 | PUMP, CENTRIFUGAL, HORIZONTAL , FIRE WATER , FRESH WATER , 0.073 , CENTERLINE , | FIRE WATER PUMPS STANDBY MOTOR DRIVEN |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P202-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/04/19 | MC-PM-028-Y1
969271747 | M410STR901 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271748 | M410STR902 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271753 | M410STR905B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271754 | M410STR906 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271755 | M410STR906B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271756 | M410STR907 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271757 | M410STR907B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271758 | M410STR908 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131955 | MQ600XAL001 | ALARM, FIRE, RED | AUDIO VISUAL INDICATOR TA ELECTRICAL ROOM OF MAQTA TERMINAL |  | LIGHT | MQ600FACP001 | 1 | LIGHT | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131960 | MQ600XLF001 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE AT OUTSIDE ELECTRICAL BUILDING OF MAQTA TERMINAL |  | ALARMANC | MQ600FACP001 | 1 | ALARMANC | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131956 | MQ600XAL002 | ALARM, FIRE, RED | AUDIO VISUAL INDICATOR AT HVAC ROOM OF MAQTA TERMINAL |  | LIGHT | MQ600FACP001 | 1 | LIGHT | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131957 | MQ600XAL003 | ALARM, FIRE, RED | AUDIO VISUAL INDICATOR AT BATTERY ROOM OF MAQTA TERMINAL |  | LIGHT | MQ600FACP001 | 1 | LIGHT | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131958 | MQ600XAS001 | HORN, SOUNDER, YES | SOUNDER AT OUTSIDE ELECTRICAL BUILDING OF MAQTA TERMINAL |  | ALARMANC | MQ600FACP001 | 1 | ALARMANC | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131959 | MQ600XAS201 | HORN, SOUNDER, YES | SOUNDER AT INTERMEDIATE STATION |  | ALARMANC | MQ600FACP001 | 1 | ALARMANC | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131961 | MQ600XLF201 | LIGHT, BEACON, RED, 24VDC | FLASHING BEACON-FIRE AT INTERMEDIATE STATION |  | ALARMANC | MQ600FACP001 | 1 | ALARMANC | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131377 | M400MP001 | PANEL,CONTROL CCTV | CCTV PANEL, MONITOR OPERATING IN MAIN C/R |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MP001-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131378 | M400RXTB001 | CONTROL RECEIVER | RECEIVER, ABOVE T-118 , CONTROL THE DATA TO & FROM COMPACT CAMERA |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RXTB001-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131379 | M400RX001 | COMMUNICATION RECEIVER | RECEIVER-ABOVE T-118, FOR COMMUNICATION WITH CONTROL SYSTEM & CONTROLS THE OTHER FUNCTIONS OF THE CAMERAS |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RX001-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131425 | M400FSP001 | PANEL,FIRE ALARM, ANSUL, ANALOG ADDRESSABLE RELEASE & FIRE ALARM SYSTEM. | FIRE SUPPRESSION PANEL AT MTERMINAL CONSOLE ROOM-PLCR |  | F&G_PNL | M400FACP001 | 1 | F&G_PNL | 617101-310510 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FSP001-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 14/09/18 | MFPS-PM10.M3
969131427 | M400HSSD001 | DETECTOR,FIRE PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HIGHLY SENSITIVE SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131429 | M400HSSD003 | DETECTOR,FIRE PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HIGH SENSITIVE SMOKE DETECTOR AT SCADA ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131430 | M400HSSD004 | DETECTOR,FIRE PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HIGH SENSITIVE SMOKE DETECTOR AT SCADA ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131431 | M400HSSD005 | DETECTOR,FIRE PROTECTION, VESDA, 18-30VDC, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT IRP I SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131436 | M400XSP003 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, 24VDC, YES | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131440 | M400XSP007 | DETECTOR,FIRE PROTECTION, 24VDC, YES, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131443 | M400XSP010 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131465 | M400XSP032 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT UPS ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131469 | M400XSP036 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT UPS ROOM BETWEN FLOOR & FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936424 | M400POV653 | VALVE, SEQUENTIAL CONTROL / ESD, 16" X 900 | ESD VALVE RUWAIS-MUSF. P/L TO JET A1/GO/ULG 95/98 |  |  | M400VALVE | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936425 | M400POV706 | VALVE, SEQUENTIAL CONTROL / ESD, 10" X 150 | ESD VALVE FOR B.L. OF LOADING ENTRY |  |  | M400VALVE | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV706-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/12/18 | MC-PM-026-M6
936426 | M400POV801 | VALVE, SEQUENTIAL CONTROL / ESD, 10" X 300 | ESD VALVE MUSF-ADIA JET A1 P/L FROM 400-P-018A/B | 938971 |  | M400PIC801 | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936427 | M400POV887 | VALVE,SEQUENCIAL CONTROL/ESD, ESD VLV MUSSAFFAH-TIE IN MP P/L, 89 - 126 KGF/CM2-G, 45 DEG C, TORMENE, 10 INCH, BALL / ROTARY, 1500, ASTM A 694 F60, ASTM A182 F51, GP-130C-485A/C3 (ROTORK), PNEUMATIC-PISTON, SPRING RETURN | ESD VALVE MUSSAFFAH-TIE IN MP P/L |  |  | M400VALVE | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936432 | AT800EOV405 | VALVE, SEQUENTIAL CONTROL / ESD, 10" X 300 | ESD VALVE JET A1 P/L FROM MUSSAFFAH TO PLR-017 |  |  | AT800VALVE | 3 | VALVE | 617101-310600 | IRPADIA | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936439 | M20DPT267A | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PRESS.TRANSMTR-LOADING PUMP 20P227A STRAINER | 934049 | DP_TXTR | M20P227A | 2 | DP_TXTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936440 | M20DPT267B | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0 | DIFF.PRESS.TRANSMTR-LOADING PUMP 20P227B STRAINER | 934050 | DP_TXTR | M20P227B | 2 | DP_TXTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936441 | M20FT161 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-FLOW , 0 - | FLOW, DIFF.PRESS.TRANSMTR-JET A1, LOADING BAY MIN | 938867 | DP_TXTR | M20FIC161 | 2 | DP_TXTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936442 | M20PT261A | TRANSMITTER, PRESSURE, SMART, (-1)-(+3), 4-20MA, 24VDC | PRESS. TRANSMITTER-SUCTION PRESSURE AT 20-P-227A, | 939661 | PRES_TX | M20PI261A | 1 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936443 | M20PT261B | TRANSMITTER, PRESSURE, SMART, 0-8, 4-20mA , 24V DC, 2 W | PRESS. TRANSMITTER-DISCHARGE PRESSURE AT 20-P-227A | 939660 | PRES_TX | M20PI261B | 1 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936444 | M20PT262A | TRANSMITTER, PRESSURE, SMART, (-1)-(+3), 24V DC, 2 WIRE | SUCTION Pressure at 20-P-227B | 939659 | PRES_TX | M20PI262A | 1 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936445 | M20PT262B | TRANSMITTER, PRESSURE, SMART, 0-8, 4-20mA , 24V DC, 2 W | PRESS.TRANSMITTER-DISCHARGE PRESSURE AT 20-P-227B | 939658 | PRES_TX | M20PI262B | 1 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936446 | M20TT161 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMPERATURE TRANSMITTER - 20-P-227A DISCHARGE | 939652 |  | M20TI161 | 1 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936447 | M20TT162 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 -100 , 4-20mA WITH H | TEMPERATURE TRANSMITTER - 20-P-227B DISCHARGE | 939653 |  | M20TI162 | 1 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IAS59028 | M10LSAL221 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 3" , SINGLE STATION SIDE , 40 | LEVEL SWITCH LOW ALARM |  | LVL_SWT | M10INLETMAN | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IAS59029 | M10LSAH211 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 3" , SINGLE STATION SIDE , 40 | LEVEL SWITCH HIGH ALARM |  | LVL_SWT | M10INLETMAN | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IAS59030 | M10LSAH301 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 3" , SINGLE STATION SIDE , 40 | LEVEL SWITCH FOR DRAIN POT AT MANIFOLD |  | LVL_SWT | M10INLETMAN | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IAS59034 | M10LZALL012 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-101 | TNK56513 | LVL_TX | M10T101 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL012-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/09/18 | MC-PM-024-M6
IAS59035 | M10LZAHH013 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-101 | TNK56513 | LVL_SWT | M10T101 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZAHH013-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/09/18 | MC-PM-024-M6
IAS59043 | M50PSH151A | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY HIGH PRESSURE SWITCH FOR TANK T-101 | TNK56513 | PRES_SWT | M10T101 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH151A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/06/19 | MC-PM-009-Y1
IAS59044 | M50PSL131A | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATERSPRAY LOW PRESSURE SWITCH FOR TANK T-101 | TNK56513 | PRES_SWT | M10T101 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL131A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/06/19 | MC-PM-009-Y1
IAS59045 | M50PSH151B | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY HIGH PRESSURE SWITCH FOR TANK T-101 | TNK56513 | PRES_SWT | M10T101 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH151B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/06/19 | MC-PM-009-Y1
IAS59046 | M50PSL131B | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATERSPRAY LOW PRESSURE SWITCH FOR TANK T-101 | TNK56513 | PRES_SWT | M10T101 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL131B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/06/19 | MC-PM-009-Y1
IAS59056 | M10LZALL022 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-102 | TNK56531 | LVL_SWT | M10T102 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL022-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/09/18 | MC-PM-024-M6
IAS59057 | M10LZAHH023 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-102 | TNK56531 | LVL_SWT | M10T102 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZAHH023-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/09/18 | MC-PM-024-M6
IAS59065 | M50PSH152A | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-102 | TNK56531 | PRES_SWT | M10T102 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH152A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/06/19 | MC-PM-009-Y1
IAS59066 | M50PSL132A | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-102 | TNK56531 | PRES_SWT | M10T102 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL132A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/06/19 | MC-PM-009-Y1
IAS59067 | M50PSH152B | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-102 | TNK56531 | PRES_SWT | M10T102 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH152B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/06/19 | MC-PM-009-Y1
IAS59068 | M50PSL132B | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-102 | TNK56531 | PRES_SWT | M10T102 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL132B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/06/19 | MC-PM-009-Y1
IAS59078 | M10LZALL032 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-103 | TNK56547 | LVL_SWT | M10T103 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL032-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/09/18 | MC-PM-024-M6
IAS59079 | M10LZAHH033 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-103 | TNK56547 | LVL_SWT | M10T103 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZAHH033-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/09/18 | MC-PM-024-M6
IAS59087 | M50PSH153A | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-103 | TNK56547 | PRES_SWT | M10T103 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH153A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/06/19 | MC-PM-009-Y1
IAS59088 | M50PSL133A | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WARE SPRAY LOW PRESSURE SWITCH FOR TANK T-103 | TNK56547 | PRES_SWT | M10T103 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL133A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/06/19 | MC-PM-009-Y1
IAS59089 | M50PSH153B | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-103 | TNK56547 | PRES_SWT | M10T103 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH153B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/06/19 | MC-PM-009-Y1
IAS59090 | M50PSL133B | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-103 | TNK56547 | PRES_SWT | M10T103 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL133B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/06/19 | MC-PM-009-Y1
IAS59100 | M10LZALL042 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-104 | TNK56565 | LVL_SWT | M10T104 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL042-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/09/18 | MC-PM-024-M6
IAS59107 | M50PSH134F | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-104 | TNK56565 | PRES_SWT | M10T104 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH134F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/06/19 | MC-PM-009-Y1
IAS59108 | M50PSL134F | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FOAM LOW PRESSURE SWITCH FOR TANK T-104 | TNK56565 | PRES_SWT | M10T104 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL134F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/06/19 | MC-PM-009-Y1
IAS59109 | M50PSH154F | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-104 | TNK56565 | PRES_SWT | M10T104 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH154F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/06/19 | MC-PM-009-Y1
IAS59110 | M50PSL134W | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-104 | TNK56565 | PRES_SWT | M10T104 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL134W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/06/19 | MC-PM-009-Y1
IAS59120 | M10LZALL052 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-105 | TNK56585 | LVL_SWT | M10T105 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL052-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/09/18 | MC-PM-024-M6
IGP59134 | M50PI221F | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-105 | TNK56585 | INDICATR | M10T105 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59151 | M50PI176W | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-106 | TNK56600 | INDICATR | M10T106 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59152 | M50PI186W | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-106 | TNK56600 | INDICATR | M10T106 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59153 | M50PI202F | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-106 | TNK56600 | INDICATR | M10T106 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59154 | M50PI222F | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-106 | TNK56600 | INDICATR | M10T106 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59171 | M50PI177W | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-107 | TNK56616 | INDICATR | M10T107 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937403 | M400P022B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.375" , SILICON CARBIDE , 5U4X/5U4X , FLUO | GAS OIL INTERNAL TANK TRANSFER PUMP-B. | 934055 | PUMPS | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P022BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-006-M6
937404 | M400P022A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.375" , SILICON CARBIDE , 5U4X/5U4X , FLUO | GAS OIL INTERNAL TANK TRANSFER PUMP-A. | 934054 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P022AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/12/18 | MM-PM-006-M6
937405 | M400P021C | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 2.625" , SILICON CARBIDE , 5U4X/5U4X , FLUO | ULG95/ULG98/ INTERNAL TANK TRANSFER PUMP-C. | 934053 | PUMPS | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P021C-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/08/18 | MM-PM-007-M6
937406 | M400P021A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 2.625" , SILICON CARBIDE , 5U4X/5U4X , FLUO | ULG95/ULG98/ INTERNAL TANK TRANSFER PUMP-A. | 934051 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P021A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/12/18 | MM-PM-007-M6
937407 | M400P021B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 2.625" , SILICON CARBIDE , 5U4X/5U4X , FLUO | ULG95/ULG98/ INTERNAL TANK TRANSFER PUMP-B | 934052 | PUMPS | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P021B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-007-M6
937415 | PL300EOV30306 | UNIT, HYDRAULIC POWER | SVS6 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB | 933062 |  | PL300SVS6 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937416 | PL300EOV30325 | UNIT, HYDRAULIC POWER | SVS5 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB | 933061 |  | PL300SVS5 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30325-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
937417 | PL300EOV30324 | UNIT, HYDRAULIC POWER | SVS4 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB | 933060 |  | PL300SVS4 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 3 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30324-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/11/18 | MM-PM-014-M6
937418 | PL300EOV30323 | UNIT, HYDRAULIC POWER | SVS3 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB | 933059 |  | PL300SVS3 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 2 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30323-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
937419 | PL300EOV30322 | UNIT, HYDRAULIC POWER | SVS2 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB | 933058 |  | PL300SVS2 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30322-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/11/18 | MM-PM-014-M6
937420 | PL300EOV30301 | UNIT, HYDRAULIC POWER | SVS1 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB | 933057 |  | PL300SVS1 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937421 | PL300EOV30217 | UNIT, HYDRAULIC POWER | SVS7 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB | 933056 |  | PL300SVS7 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30217-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
937422 | PL300EOV30216 | UNIT, HYDRAULIC POWER | SVS6 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB | 933055 |  | PL300SVS6 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30216-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
937423 | PL300EOV30215 | UNIT, HYDRAULIC POWER | SVS5 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB | 933054 |  | PL300SVS5 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30215-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
937424 | PL300EOV30214 | UNIT, HYDRAULIC POWER | SVS4 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB | 933053 |  | PL300SVS4 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30214-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/11/18 | MM-PM-014-M6
937425 | PL300EOV30213 | UNIT, HYDRAULIC POWER | SVS3 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB | 933052 |  | PL300SVS3 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30213-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
937426 | PL300EOV30212 | UNIT, HYDRAULIC POWER | SVS2 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB | 933051 |  | PL300SVS2 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30212-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/11/18 | MM-PM-014-M6
937427 | PL300EOV30211 | UNIT, HYDRAULIC POWER | SVS1 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB | 933050 |  | PL300SVS1 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30211-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 09/08/18 | MM-PM-014-M6
937428 | PL300EOV30107 | UNIT, HYDRAULIC POWER | SVS7 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB | 933049 |  | PL300SVS7 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30107-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
937429 | PL300EOV30106 | UNIT, HYDRAULIC POWER | SVS6 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB | 933048 |  | PL300SVS6 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30106-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
937430 | PL300EOV30105 | UNIT, HYDRAULIC POWER | SVS5 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB | 933047 |  | PL300SVS5 | 2 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 10 | 1 | 50 | 10 | 4.699 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | PL300EOV30105-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
937431 | PL300EOV30104 | UNIT, HYDRAULIC POWER | SVS4 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB | 933046 |  | PL300SVS4 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30104-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/11/18 | MM-PM-014-M6
937432 | PL300EOV30103 | UNIT, HYDRAULIC POWER | SVS3 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB | 933045 |  | PL300SVS3 | 2 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 10 | 1 | 50 | 10 | 4.699 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | PL300EOV30103-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
937433 | PL300EOV30102 | UNIT, HYDRAULIC POWER | SVS2 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB | 933044 |  | PL300SVS2 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30102-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/11/18 | MM-PM-014-M6
937434 | PL300EOV30101 | UNIT, HYDRAULIC POWER | SVS1 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB | 933043 |  | PL300SVS1 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30101-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 09/08/18 | MM-PM-014-M6
938850 | M400TT861A | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX MUSSAFAH -ALAIN MULTI PRODUCT P/L | 939222 | TEMP_TX | M400TI861A | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938851 | M400TT861B | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX MUSSAFAH -ALAIN MULTI PRODUCT P/L | 939223 | TEMP_TX | M400TI861B | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938852 | M400PDT861A | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | D.P. TX MUSSAFAH ALAIN MULTI PRODUCT P/L | 939752 |  | M400PDI861A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938853 | M400PDT861B | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | D.P. TX MUSSAFAH ALAIN MULTI PRODUCT P/L | 939753 |  | M400PDI861B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938854 | M400TG416 | THERMOMETER, DIAL, 0-100 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | LUBE OIL RESEVOIR - TEMPERATURE GAUGE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938855 | M400TE429A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 0-200 DEG C , PLATINUM | LUBE OIL HEADER TEMPERATURE |  | TEMP_ELE | M400TEMP | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938856 | M400TE429B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 0-200 DEG C , PLATINUM | LUBE OIL HEADER TEMPERATURE |  | TEMP_ELE | M400TEMP | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938857 | M400PT401 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20mA , 10.5-30 VDC , LOW C | L/O PUMP A DISCHARGE FOR M400P016A |  | PRES_TX | M400PI401C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938858 | M400PT402 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20mA , 10.5-30 VDC , 1/2" NPT , LOW CAST AL | Lube Oil Pump B - Discharge Press. For 400-P-016A |  | PRES_TX | M400PI402C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938867 | M20FIC161 | LOOP, FLOW CONTROL INSTRUMENT, JET A1 , 70M3/HR , 45 DEG.C DEGC, 5.5 KG/CM2 , 5. | JET A1 LOADING PUMPS DISCHARGE MIN FLOW |  | CLOSLOOP | M20SYS | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938868 | M400PIC536 | LOOP, PRESSURE CONTROL, JET A1 , 6 KG/CM2 , 45 DEG.C , 0.751-0.840 , DRESSER , 8 | JET A1 TO FILTER COALESCER SEPARATOR(400-L-003A/B) |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC536-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/12/18 | MC-PM-008-M6
938869 | M400PIC561 | LOOP, PRESSURE CONTROL, JET A1 , 78 KG/CM2 , 45 DEG.C , 0.751-0.841 , MASONEILAN | OFF SPEC JET A1- MAINLINE PUMP DISCHARGE |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC561-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/12/18 | MC-PM-008-M6
938870 | M400PIC670 | LOOP, PRESSURE CONTROL, ULG 95/ULG91/JET A1 , 15 KG/CM2 , 6 KG/CM2 , 45 DEG.C , | INLET OF RUWAIS-MUSSAFAH MP P/L FLOW METERING SKID |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC670-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/12/18 | MC-PM-008-M6
938871 | M400PIC813 | LOOP, PRESSURE CONTROL, JET A1 M/L PUMPS , 24.7 KG/CM2 , 20.4 KG/CM2 , 45 DEG.C | PRESS. AT INLET LINE OF 400-PV-813 |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC813-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/12/18 | MC-PM-008-M6
938872 | M400PIC894 | LOOP, PRESSURE CONTROL INSTRUMENT 400PV894A/B (ULG 95/98/JET A1 , 127.4 KG/CM2 , 56.4 KG/ | MUSSAFAH-AL AIN MP TIE IN MAIN LINE PUMP DISCHARGE |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC894-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 21/12/18 | MC-PM-008-M6
938873 | AT800PIC105 | LOOP, PRESSURE CONTROL, MUSSAFAH-ADIA JET A1 , 11 KG/CM2 , 6 KG/CM2 , 45 DEG.C , | MUSSAFAH-ADIA JET A1 TO EXISTING ADIA STORAGE TANK |  | CLOSLOOP | AT800PRESS | 2 | CLOSLOOP | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938874 | M400LIC753 | LOOP, LEVEL CONTROL, JET A1 , .841 , .751 , 45 DEG.C , DRESSER ****, 88-21114 , | Filter Coalescer (400-L-004B) Blowdown to OWS |  | CLOSLOOP | M400LEVEL | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LIC753-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/12/18 | MC-PM-005-M6
938875 | M30LIC161A | LOOP, LEVEL CONTROL, JET A1 , 0.841 , 0.751 , 45 DEG.C , DRESSER ****, 88-21114 | FILTER COALESCER 400-L-006, |  | CLOSLOOP | M30SYS | 3 | CLOSLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938876 | M30LIC162A | LOOP, LEVEL CONTROL, JET A1 , 0.841 , .751 , 45 DEG.C , DRESSER ****, 88-21114 , | FILTER COALESCER 30-L-007 |  | CLOSLOOP | M30LEVEL | 3 | CLOSLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59031 | M10LIT011 | ENRAF TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-101 | IIL59032 | TANKGAUG | M10LIA011 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT011-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/11/18 | MC-PM067.M6
IIL59032 | M10LIA011 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 101 ON DCS | TNK56513 | TANKGAUG | M10T101 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59033 | M10LI011 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-101 | IIL59032 | TANKGAUG | M10LIA011 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59053 | M10LIT021 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , M20 X 1.5 , ALUMINI | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-102 | IIL59054 | TANKGAUG | M10LIA021 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT021-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/09/18 | MC-PM067.M6
IIL59054 | M10LIA021 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 102 ON DCS | TNK56531 | TANKGAUG | M10T102 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59055 | M10LI021 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-102 | IIL59054 | TANKGAUG | M10LIA021 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59075 | M10LIT031 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-103 | IIL59076 | TANKGAUG | M10LIA031 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT031-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/12/18 | MC-PM067.M6
IIL59076 | M10LIA031 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 103 ON DCS | TNK56547 | TANKGAUG | M10T103 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59077 | M10LI031 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-103 | IIL59076 | TANKGAUG | M10LIA031 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59097 | M10LIT041 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-104 | IIL59098 | TANKGAUG | M10LIA041 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT041-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/12/18 | MC-PM067.M6
IIL59098 | M10LIA041 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 104 ON DCS | TNK56565 | TANKGAUG | M10T104 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59099 | M10LI041 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-104 | IIL59098 | TANKGAUG | M10LIA041 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59117 | M10LIT051 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-105 | IIL59118 | TANKGAUG | M10LIA051 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT051-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM067.M6
IIL59118 | M10LIA051 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 105 ON DCS | TNK56585 | TANKGAUG | M10T105 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59119 | M10LI051 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-105 | IIL59118 | TANKGAUG | M10LIA051 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59137 | M10LIT061 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR TX (SERVO) FOR TANK T-106 | IIL59138 | TANKGAUG | M10LIA061 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT061-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM067.M6
IIL59138 | M10LIA061 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATOR ALARM OF TANK 106 ON DCS. | TNK56600 | TANKGAUG | M10T106 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59139 | M10LI061 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-106 | IIL59138 | TANKGAUG | M10LIA061 | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59157 | M10LIT071 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-107 | IIL59158 | TANKGAUG | M10LIA071 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT071-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/08/18 | MC-PM067.M6
IIL59158 | M10LIA071 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 107 ON DCS | TNK56616 | TANKGAUG | M10T107 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59159 | M10LI071 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-107 | IIL59158 | TANKGAUG | M10LIA071 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59177 | M10LIT081 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-108 | IIL59178 | TANKGAUG | M10LIA081 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT081-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/08/18 | MC-PM067.M6
WWD11305 | U5601L037F | MACHINE, WELDING, DIESEL | WELDING MACHINE, DIESEL ( LINCOLN ) |  |  | MMWS | 4 | 0 | 617101-610411 | MTERMINAL | OPERATING | 5 | 5 | 5 | 5 | 5 | 5 | 4.1938 | Non Critical | Low | Non Critical | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | U5601L037F.UEL | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 19/10/18 | ME-PM-018-M3
935755 | M400PM018B | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935756 | M400PM019 | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935757 | M400PM019SPARE | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935758 | M400PM031A | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935759 | M400PM031B | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935760 | M400TMLSPARE1 | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MMS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935761 | M400TMLSPARE2 | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MMS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935762 | M400TMM001AA | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936843 | AA13RTU001 | SYSTEM | SCADA SYSTEM |  |  | AA13SYS | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936844 | AA13RWS001 | SYSTEM | SCADA SYSTEM |  |  | AA13SYS | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936846 | PL300RTU001 | SYSTEM | SCADA SYSTEM |  |  | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU001-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 27/03/19 | MC-PM-030-M6
936847 | PL300RTU002 | SYSTEM | SCADA SYSTEM |  |  | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU002-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 18/04/19 | MC-PM-030-M6
936848 | PL300RTU003 | SYSTEM | SCADA SYSTEM |  |  | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU003-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 19/04/19 | MC-PM-030-M6
936849 | PL300RTU004 | SYSTEM | SCADA SYSTEM |  |  | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU004-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 20/04/19 | MC-PM-030-M6
936850 | PL300RTU005 | SYSTEM | SCADA SYSTEM |  |  | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU005-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 22/05/19 | MC-PM-030-M6
936851 | PL300RTU006 | SYSTEM | SCADA SYSTEM |  |  | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU006-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 23/05/19 | MC-PM-030-M6
936852 | PL300RTU007 | SYSTEM | SCADA SYSTEM |  |  | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU007-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 25/04/19 | MC-PM-030-M6
936853 | M400DCSMC001 | SYSTEM | DCS SYSTEM |  | PA_SYS | M400SYS | 1 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400DCSMC001-MC1 | ACTIVE | CONT | PM | IN | 6 | MONTHS | 23/08/18 | MC-PM-030-M6
936854 | M400DCSMC002 | SYSTEM | DCS SYSTEM |  | PA_SYS | M400SYS | 1 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400DCSMC002-MC1 | ACTIVE | CONT | PM | IN | 6 | MONTHS | 24/08/18 | MC-PM-030-M6
936855 | M400DCSMC003 | SYSTEM | DCS SYSTEM |  | PA_SYS | M400SYS | 1 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M400DCSMC003-MC1 | ACTIVE | CONT | PM | IN | 6 | MONTHS | 25/08/18 | MC-PM-030-M6
936856 | M400DCSSC001 | SYSTEM | DCS SYSTEM |  | DCS_PNL | M400SYS | 2 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | M400DCSSC001-MC1 | ACTIVE | CONT | PM | IN | 6 | MONTHS | 23/09/18 | MC-PM-030-M6
936857 | M400DCSSC002 | SYSTEM | DCS SYSTEM |  | DCS_PNL | M400SYS | 2 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DCSSC002-MC1 | ACTIVE | CONT | PM | IN | 6 | MONTHS | 24/09/18 | MC-PM-030-M6
936858 | M400ESDMC001 | PANEL, CONTROL | ESD SYSTEM |  | ESD_PNL | M400SYS | 1 | ESD_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936859 | M400ESDMC002 | PANEL, CONTROL | ESD SYSTEM |  | ESD_PNL | M400SYS | 1 | ESD_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936860 | M400ESDSC001 | ESD SYSTEM CONTROL PANEL | ESD SYSTEM |  | ESD_PNL | M400SYS | 1 | ESD_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936861 | M400ESDSC002 | ESD SYSTEM CONTROL PANEL | ESD SYSTEM |  | ESD_PNL | M400SYS | 1 | ESD_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936862 | M400IRP001 | SYSTEM | DCS SYSTEM |  | DCS_PNL | M400SYS | 2 | DCS_PNL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936863 | M400PDB001 | SYSTEM | DCS SYSTEM |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936864 | M400PDB002 | SYSTEM | DCS SYSTEM |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936865 | M400SMCS001 | SYSTEM | SCADA SYSTEM |  |  | M400SYS | 1 | CLSSCS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936866 | MQ600RTU001 | SYSTEM | SCADA SYSTEM |  |  | MQ600SYS | 1 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936868 | AT800RTU001 | SCADA SYSTEM | SCADA SYSTEM |  |  | AT800SYS | 3 | DCS_PNL | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936869 | AT800RWS001 | SYSTEM CPU/MONITOR (SCADA) | SCADA SYSTEM |  |  | AT800SYS | 3 | DCS_PNL | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278933 | PL318CCTV142 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278934 | PL318CCTV143 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278935 | PL318CCTV144 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278936 | PL318CCTV145 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278937 | PL318CCTV146 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278938 | PL318CCTV147 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278939 | PL318CCTV148 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278940 | PL318CCTV149 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278941 | PL318CCTV150 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278942 | PL318CCTV151 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935610 | SMTP11 |  | TEST POINT# 11 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935611 | SMTP12 |  | TEST POINT# 12 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935625 | SMTP26 |  | TEST POINT# 26 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935626 | SMTP27 |  | TEST POINT# 27 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935627 | SMTP28 |  | TEST POINT# 28 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935544 | SALAINTP87 |  | TEST POINT # 87 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935545 | SALAINTP88 |  | TEST POINT # 88 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935547 | SALAINTP89 |  | TEST POINT # 89 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935446 | SALAINTP1 |  | TEST POINT # 1 (C.P.STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935447 | SALAINTP2 |  | TEST POINT # 2 (C.P.STATION-1 KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935448 | SALAINTP3 |  | TEST POINT # 3 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278561 | M400PDB007 | CABINET | PLCR POWER DISTRIBUTION BOARD CABINET | 969195561 | SWBOARD | M400SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP58265 | S15PIA0150 | LOOP, PRESSURE INDICATOR INSTRUMEN, LPG , 40 BAR , 25.15 BAR , DIAPHRAGMN , RO | PRESSURE INDICATION AFTER 15MOV116 |  | OPENLOOP | S15R03 | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | S15PIA0150-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/05/19 | MC-PM-007-Y1
IIP58266 | S15PT150 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , 1/2" NPT , M20 X 1.5 , ALUM | PRESSURE TRANSMITTER AFTER 15MOV116 | IIP58265 | PRES_TX | S15PIA0150 | 1 | PRES_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP58271 | S15XPI121 | SPHERE PASSAGE INDICATOR OFPIG SIGNAL | SPHERE PASSAGE INDICATOR OFPIG SIGNAL |  | INDICATR | S15R03 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | S15XPI121-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/06/19 | MC-PM-007-Y1
IIP58272 | S15XXT121 | SPHERE PASSAGE TRANSMITTER OF PIG SIGNALLER AFTER | SPHERE PASSAGE TRANSMITTER OF PIG SIGNALLER AFTER | IIP58271 | INDICATR | S15XPI121 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP58340 | S21XPI101 | SCRAPER, SCRAPER | SCRAPPER DETECTOR INDICATION |  |  | S21R02 | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | S21XPI101-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/07/19 | MC-PM-007-Y1
IPS59248 | M10L109 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK109 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59249 | M10L110 | SPEAKER, LOUD , 6 , EXPLOSION PROOF | PUBLIC ADDRESS LOUD SPEAKER FOR TANK110 |  | PA_SYS | M10COMMON | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IPS59562 | M10LPSM1 | MODULE, POWER SUPPLY | POWER SUPPLY MODULE PUBLIC ADDRESS LOUD SPEAKER |  | PA_SYS | M10TANKS | 1 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969298005 | PL312LDS004 | LEAK DETECTION SYSTEM CABINET-RUW.-MUSS. PL-KP126+030.660 | LDS SYSTEM CABINET - RUW.-MUSS. PL - KP 126+030.660 |  | BLDGS | PL312 | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281982 | PL312CCTVP001 | CCTV CABINET - RUW.-MUSS. PL - KP 34+385.36 | CCTV CABINET - RUW.-MUSS. PL - KP 34+385.36 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281983 | PL312CCTVP002 | CCTV CABINET - RUW.-MUSS. PL - KP 65+870.00 | CCTV CABINET - RUW.-MUSS. PL - KP 65+870.00 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281984 | PL312CCTVP003 | CCTV CABINET - RUW.-MUSS. PL - KP 94+632.523 | CCTV CABINET - RUW.-MUSS. PL - KP 94+632.523 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281985 | PL312CCTVP004 | CCTV CABINET - RUW.-MUSS. PL - KP 126+030.660 | CCTV CABINET - RUW.-MUSS. PL - KP 126+030.660 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281986 | PL312CCTVP005 | CCTV CABINET - RUW.-MUSS. PL - KP 153+816.970 | CCTV CABINET - RUW.-MUSS. PL - KP 153+816.970 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281987 | PL312CCTVP006 | CCTV CABINET - RUW.-MUSS. PL - KP 178+435.730 | CCTV CABINET - RUW.-MUSS. PL - KP 178+435.730 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281988 | PL315CCTVP001 | CCTV CABINET - TARRIF–MZ. PL - KP 16+180.906 | CCTV CABINET - TARRIF–MZ. PL - KP 16+180.906 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281989 | PL318CCTVP001 | CCTV CABINET - MUSS.–AL AIN PL - KP 36+957.340 | CCTV CABINET - MUSS.–AL AIN PL - KP 36+957.340 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281990 | PL318CCTVP002 | CCTV CABINET - MUSS.–AL AIN PL - KP 66+500.00 | CCTV CABINET - MUSS.–AL AIN PL - KP 66+500.00 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281991 | PL318CCTVP003 | CCTV CABINET - MUSS.–AL AIN PL - KP 88+420.230 | CCTV CABINET - MUSS.–AL AIN PL - KP 88+420.230 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132702 | M400ME020 | MOTOR,ELECTRIC, SCRAPPER MOTOR, 0.18 KW, VARIABLE HZ, 415 V, 1325 RPM, 3, 0.62 AMP, 400-MCC-001 | WWTP SCRAPPER MOTOR |  | MOTOR | M400WWTP | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400ME020-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/11/18 | ME-PM-014-M6
969132706 | M400ME024 | MOTOR,ELECTRIC, GEAR DRIVE MOTOR, 0.37 KW, 50 HZ, 415 V, 1500 RPM, 3, 1.95 AMP, 400-MCC-001 | GEAR DRIVE MOTOR OIL SKIMMER TANK 2 |  | MOTOR | M400WWTP | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400ME024-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/01/19 | ME-PM-014-M6
969132707 | M400ME025 | MOTOR,ELECTRIC, GEAR DRIVE MOTOR, 0.37 KW, 50 HZ, 415 V, 1500 RPM, 3, 1.95 AMP, 400-MCC-001 | GEAR DRIVE MOTOR OIL SKIMMER TANK 3 |  | MOTOR | M400WWTP | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400ME025-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 26/01/19 | ME-PM-014-M6
969281332 | M410EA051AB | AIR BLAST COOLER FOR 410-P-004A/B | AIR BLAST COOLER FOR 410-P-004A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA051AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969281333 | M410EA051BA | AIR BLAST COOLER FOR 410-P-004A/B | AIR BLAST COOLER FOR 410-P-004A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA051BA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969281334 | M410EA051BB | AIR BLAST COOLER FOR 410-P-004A/B | AIR BLAST COOLER FOR 410-P-004A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA051BB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969281335 | M410L050AA | DUPLEX FILTER FOR 410-P-002A/B | DUPLEX FILTER FOR 410-P-002A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56503 | M10AE001 | AIR ELIMINATOR UNIT1 FOR INLET METERING | AIR ELIMINATOR UNIT1 MULTIPRODUCT INLET METERING. |  | VESPOP | M10INLETMET | 3 | VALVE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56504 | M10AE002 | AIR ELIMINATOR UNIT2 FOR INLET METERING | AIR ELIMINATOR UNIT1 MULTIPRODUCT INLET METERING. |  | VESPOP | M10INLETMET | 3 | VALVE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56505 | M10PQIA303 | COLOUR METER SAMPLING PUMP1 | COLOUR MT. SAMPL. PUMP1 MULTIPRODUCT I/L METERING |  |  | M10INLETMET | 3 | PURECI | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | M10PQIA303-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 19/09/18 | MM-PM-038-M6
XXX56506 | M10PQIA304 | COLOUR METER SAMPLING PUMP2 | COLOUR MT. SAMPL. PUMP2 MULTIPRODUCT I/L METERING |  |  | M10INLETMET | 3 | PURECI | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | M10PQIA304-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 16/10/18 | MM-PM-038-M6
XXX56523 | M50PIPE101 | PIPELINE, POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-101 |  | PIPING | M10T101 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 |  | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56524 | M50T183A | FOAM | FIRE FIGHTING FOAM BAG TANK T101,T102,T103 |  |  | M10TANKS | 1 | TK | 617101-310510 | MTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56525 | M50T183B | FOAM | FIRE FIGHTING FOAM BAG TANK T101,T-102,T103 |  |  | M10TANKS | 1 | TK | 617101-310510 | MTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56526 | M50WOV131A | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-101 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-101 |  | VALVE | M10T101 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271759 | M410STR908B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56663 | M10PVRV101B | VALVE, SAFETY RELIEF, FIG 700 , KEROSEN , 6" , FLANGED , SS AISI 316 , PLAIN LIF | VACUUM RELIEF VALVE FOR TANK T-110 |  | PSV | M10T110 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56672 | M51RV106 | VALVE SAFETY RELIEF | RELIEF VALVE AT LPG PIPELEINE PIG RECEIVER IN MTF |  | PSV | M5101R02 | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56673 | M51RV107 | VALVE SAFETY RELIEF | RELIEF VALVE AT LPG PIPELEINE PIG RECEIVER IN MTF |  | PSV | M5101R02 | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56674 | M51RV108 | VALVE SAFETY RELIEF | RELIEF VALVE AT LPG PIPELEINE PIG RECEIVER IN MTF |  | PSV | M5101R02 | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56675 | M51RV112 | VALVE SAFETY RELIEF | RELIEF VALVE AT LPG PIPELEINE PIG RECEIVER IN MTF |  | PSV | M5101R02 | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56677 | M15RV130 | VALVE SAFETY RELIEF | RV AT MULTI PRODUCT PIPELEINE PIG RECEIVER IN MTF |  | PSV | M15R04 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56678 | M15RV140 | VALVE SAFETY RELIEF | RV AT MULTI PRODUCT PIPELEINE PIG RECEIVER IN MTF |  | PSV | M15R04 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56679 | M15RV137 | VALVE SAFETY RELIEF | RV AT MULTI PRODUCT PIPELEINE PIG RECEIVER IN MTF |  | PSV | M15R04 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275535 | PL312PT31201B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275536 | PL312PT31202A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275537 | PL312PT31202B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275538 | PL312PT31203A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275539 | PL312PT31203B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275540 | PL312PT31204A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275541 | PL312PT31204B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275542 | PL312PT31205A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275543 | PL312PT31205B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275544 | PL312PT31206A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275545 | PL312PT31206B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275546 | PL312PT31301A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275547 | PL312PT31301B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275548 | PL312PT31302A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275549 | PL312PT31302B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275550 | PL312PT31303A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275551 | PL312PT31303B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275552 | PL312PT31304A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275553 | PL312PT31304B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275554 | PL312PT31305A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275555 | PL312PT31305B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275556 | PL312PT31306A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275557 | PL312PT31306B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275558 | PL312RTU001 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275559 | PL312RTU002 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275560 | PL312RTU003 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275561 | PL312RTU004 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275562 | PL312RTU005 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275563 | PL312RTU006 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275564 | PL312SCR101 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL312SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275565 | PL312SCR201 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL312SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275566 | PL312SCR301 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL312SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275567 | PL312SCR401 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL312SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275568 | PL312SCR501 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL312SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275569 | PL312SCR601 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL312SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275572 | PL312SPS101 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL312SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275661 | PL312YYIS002 | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275662 | PL312YYIS003 | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275663 | PL312YYIS004 | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275664 | PL312YYIS31201A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275665 | PL312YYIS31201B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275666 | PL312YYIS31202A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275667 | PL312YYIS31202B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275668 | PL312YYIS31203A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275669 | PL312YYIS31203B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275670 | PL312YYIS31204A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275671 | PL312YYIS31204B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275672 | PL312YYIS31205A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275673 | PL312YYIS31205B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275674 | PL312YYIS31206A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275675 | PL312YYIS31206B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275676 | PL312YYIS31301A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275677 | PL312YYIS31301B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275678 | PL312YYIS31302A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275679 | PL312YYIS31302B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275680 | PL312YYIS31303A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275681 | PL312YYIS31303B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275682 | PL312YYIS31304A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275683 | PL312YYIS31304B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275684 | PL312YYIS31305A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275685 | PL312YYIS31305B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275686 | PL312YYIS31306A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275687 | PL312YYIS31306B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275688 | PL315BAV21243001 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275689 | PL315BAV21243002 | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275690 | PL315BAV21243003 | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275691 | PL315BAV21243004 | 10" 7.80mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 10" 7.80mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275692 | PL315BAV21243005 | 10" 7.80mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe | 10" 7.80mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe |  | CONTHNDV | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275693 | PL315BAV21243006 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275694 | PL315BB1301 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL315BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275358 | PL315EOV31513 | ELECTRO HYDRAULIC VALVE, SV STATION-13 | ELECTRO HYDRAULIC VALVE, SV STATION-13 |  | CONTHNDV | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275695 | PL315EOV31513 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 315-EOV-315-13 | ELECTRO HYDRAULIC VALVE, SV STATION-13 | 969275358 | MOV | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275359 | PL315EOV31613 | ELECTRO HYDRAULIC VALVE, SVSTATION-13 | ELECTRO HYDRAULIC VALVE, SVSTATION-13 |  | CONTHNDV | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275696 | PL315EOV31613 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 315-EOV-316-13 | ELECTRO HYDRAULIC VALVE, SVSTATION-13 | 969275359 | MOV | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275697 | PL315GAV21223001 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275698 | PL315GAV21223002 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275699 | PL315GAV21223003 | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275700 | PL315GAV21223004 | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275701 | PL315GAV21223005 | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL315VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275702 | PL315GDH1305 | HC GAS DETECTOR | HC GAS DETECTOR |  | FG_DET | PL315GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275705 | PL315PG31513A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL315PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275706 | PL315PG31513B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL315PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275707 | PL315PG31613A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL315PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275708 | PL315PG31613B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL315PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275709 | PL315PT31513A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL315PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275710 | PL315PT31513B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL315PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275711 | PL315PT31613A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL315PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275712 | PL315PT31613B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL315PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275713 | PL315RTU001 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL315MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275714 | PL315SCR1301 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL315SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275715 | PL315SPS1301 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL315SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938910 | M400SE461 | PROBE, VIBRATION , 8MM , 0.5 M | Pump-Keyphasor FOR M400P019 | 935830 | VIBRE_TX | M400P019 | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400SE461-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-012-M3
938911 | M400FIC771 | CONTROLLER, FLOW | MUSSAFFAH-ADIA JET A1 P/L,CUSTODY METERING SYSTEM |  | CLOSLOOP | M400FLOW | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FIC771-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/08/18 | MC-PM-002-Y1
938912 | M400FIC772 | CONTROLLER, FLOW | FLOW METER SKID 400-FT-772,CUSTODY METERING SYSTEM |  | CLOSLOOP | M400FLOW | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FIC772-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/08/18 | MC-PM-002-Y1
938913 | M400FIC861 | CONTROLLER, FLOW | MUSSAFFAH-TIE IN TO AL-AIN,CUSTODY METERING SYSTEM |  | CLOSLOOP | M400FLOW | 3 | CLOSLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400FIC861-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 11/08/18 | MC-PM-002-Y1
938914 | M400LY540 | VALVE, SOLENOID, 1/2" | ON/OFF VALVE FILTER COALESCER 400-L-003A(SOV) | 938742 | SOL_VLV | M400LIC540 | 1 | SOL_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938915 | M400LY541 | VALVE, SOLENOID, 1/2" | ON/OFF VALVE FILTER COALESCER 400-L-003B(SOV) | 938743 | SOL_VLV | M400LIC541 | 1 | SOL_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938916 | M400LY751 | VALVE, SOLENOID, 1/2" | ON/OFF VALVE FILTER COALESCER 400-L-004A(SOV) | 938744 | SOL_VLV | M400LIC751 | 1 | SOL_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938917 | M400LY753 | VALVE, SOLENOID, 1/2" | ON/OFF VALVE FILTER COALESCER 400-L-004B(SOV) | 938874 | SOL_VLV | M400LIC753 | 1 | SOL_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938918 | M400MOS001 | SWITCH | Master MOS for Jet A1 Reverse Pumping |  | WS_SYS | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOS001-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/01/19 | MC-PM-016-M6
938919 | M400MOS002 | SWITCH | Master MOS for Al-Ain M/P P/L |  | WS_SYS | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS002-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/01/19 | MC-PM-016-M6
938920 | M400MOS003 | SWITCH | Master MOS for ADIA Jet A1 P/L |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS003-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/01/19 | MC-PM-016-M6
938921 | M400MOS532 | SWITCH | MOS for 400-PT-532 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS532-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/01/19 | MC-PM-016-M6
938922 | M400MOS533 | SWITCH | MOS for 400-PT-533 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS533-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/01/19 | MC-PM-016-M6
938923 | M400MOS534 | SWITCH | MOS for 400-PT-534 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS534-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 20/01/19 | MC-PM-016-M6
938924 | M400MOS547 | SWITCH | MOS for 400-PT-547 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS547-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 20/01/19 | MC-PM-016-M6
938925 | M400MOS550 | SWITCH | MOS for 400-PT-550 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS550-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 21/01/19 | MC-PM-016-M6
938926 | M400MOS554 | SWITCH | MOS for 400-PT-554 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS554-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/01/19 | MC-PM-016-M6
938927 | M400MOS556 | SWITCH | MOS for 400-PT-556 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS556-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 25/01/19 | MC-PM-016-M6
938928 | M400MOS558 | SWITCH | MOS for 400-PT-558 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS558-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 26/01/19 | MC-PM-016-M6
938929 | M400MOS559 | SWITCH | MOS for 400-PT-559 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS559-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 27/01/19 | MC-PM-016-M6
938930 | M400MOS560 | SWITCH | MOS for 400-PT-560 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS560-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/01/19 | MC-PM-016-M6
938931 | M400MOS658 | SWITCH | MOS for 400-PT-658 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS658-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/01/19 | MC-PM-016-M6
938932 | M400MOS659 | SWITCH | MOS for 400-PT-659 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS659-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 29/01/19 | MC-PM-016-M6
938933 | M400MOS660 | SWITCH | MOS for 400-PT-660 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS660-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 29/01/19 | MC-PM-016-M6
938934 | M400MOS756 | SWITCH | MOS for 400-PT-756 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS756-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/08/18 | MC-PM-016-M6
938935 | M400MOS755 | SWITCH | MOS for 400-PT-755 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS755-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/08/18 | MC-PM-016-M6
938936 | M400MOS761 | SWITCH | MOS for 400-PT-761 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS761-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 02/08/18 | MC-PM-016-M6
938937 | M400MOS762 | SWITCH | MOS for 400-PT-762 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS762-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 02/08/18 | MC-PM-016-M6
938938 | M400MOS804 | SWITCH | MOS for 400-PT-804 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS804-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/08/18 | MC-PM-016-M6
938939 | M400MOS807 | SWITCH | MOS for 400-PT-807 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS807-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/08/18 | MC-PM-016-M6
938940 | M400MOS808 | SWITCH | MOS for 400-PT-808 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS808-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/08/18 | MC-PM-016-M6
938941 | M400MOS811 | SWITCH | MOS for 400-PT-811 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS811-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/08/18 | MC-PM-016-M6
938942 | M400MOS814 | SWITCH | MOS for 400-PT-814 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS814-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/01/19 | MC-PM-016-M6
938943 | M400MOS815 | SWITCH | MOS for 400-PT-815 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS815-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/01/19 | MC-PM-016-M6
938944 | M400MOS816 | SWITCH | MOS for 400-PT-816 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS816-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/08/18 | MC-PM-016-M6
938945 | M400MOS853 | SWITCH | MOS for 400-PT-853 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS853-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/08/18 | MC-PM-016-M6
938946 | M400MOS854 | SWITCH | MOS for 400-PT-854 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS854-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/08/18 | MC-PM-016-M6
938947 | M400MOS857 | SWITCH | MOS for 400-PT-857 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS857-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/08/18 | MC-PM-016-M6
938948 | M400MOS858 | SWITCH | MOS for 400-PT-858 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS858-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 15/08/18 | MC-PM-016-M6
938949 | M400MOS884 | SWITCH | MOS for 400-PT-884 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS884-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/08/18 | MC-PM-016-M6
938950 | M400MOS886 | SWITCH | MOS for 400-PT-886 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS886-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/08/18 | MC-PM-016-M6
938951 | M400MOS887 | SWITCH | MOS for 400-PT-887 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS887-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/01/19 | MC-PM-016-M6
938952 | M400MOS889 | SWITCH | MOS for 400-PT-887 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS889-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/08/18 | MC-PM-016-M6
938953 | M400MOS895 | SWITCH | MOS for 400-PT-895 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS895-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 21/08/18 | MC-PM-016-M6
938954 | M400MOS896 | SWITCH | MOS for 400-PT-896 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS896-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/08/18 | MC-PM-016-M6
938955 | M400MOS897 | SWITCH | MOS for 400-PT-897 |  |  | M400SYS | 2 | WS_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MOS897-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 23/08/18 | MC-PM-016-M6
938957 | M400PT889 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-200 BAR , 4-20mA , 10.5-30 | PR.TR. DISCHARGE LINE MAIN LINE PUMP 400-P-016B | 935827 | PRES_TX | M400P016B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT889-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/10/18 | MC-PM-007-Y1
938958 | M400PAL406 | ALARM, OIL PRESSURE | Lube Oil Header - Press. For 400-P-016A | 935826 | ALARMANC | M400P016A | 2 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938959 | M400PALL406 | ALARM, OIL PRESSURE | Lube Oil Header - Press. For 400-P-016A | 935826 | ALARMANC | M400P016A | 1 | ALARMANC | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938960 | M400PB537 | SWITCH, PUSHBUTTON | ESD Valve 400-POV-537 Partial Stroke Push Button |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PB537-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 24/08/18 | MC-PM-016-M6
938961 | M400PB571 | SWITCH, PUSHBUTTON | ESD Valve 400-POV-571 Partial Stroke Push Button |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PB571-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 25/08/18 | MC-PM-016-M6
938962 | M400PB653 | SWITCH, PUSHBUTTON | ESD Valve 400-POV-653 Partial Stroke Push Button |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PB653-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 27/11/18 | MC-PM-016-M6
938963 | M400PB801 | SWITCH, PUSHBUTTON | ESD Valve 400-POV-801 Partial Stroke Push Button | 938971 |  | M400PIC801 | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PB801-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/12/18 | MC-PM-016-M6
938964 | M400PB882 | SWITCH, PUSHBUTTON | Station ESD Push Button (HWC) |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PB882-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/08/18 | MC-PM-016-M6
938965 | M400PB883 | SWITCH, PUSHBUTTON | Station ESD Push Button (SCADA) |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PB883-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/08/18 | MC-PM-016-M6
938966 | M400PB887 | SWITCH, PUSHBUTTON | ESD Valve 400-POV-881 Partial Stroke Push Button |  |  | M400SYS | 1 | WS_SYS | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PB887-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/08/18 | MC-PM-016-M6
938967 | M400PG956 | GAUGE, PRESSURE, INDICATION , 0-25 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Line 400-P-201D | 936407 |  | M400P201D | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938968 | M400PIC531 | LOOP, PRESSURE CONTROL, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-50 KG/CM2 , 24 V | From Naphtha/Reformate P/L |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC531-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/12/18 | MC-PM-008-M6
938969 | M400PIC551 | LOOP, PRESSURE CONTROL, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-12 KG/CM2 , 24 V | Oulet line metering skid 400-FT-772 |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC551-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/12/18 | MC-PM-008-M6
938970 | M400PIC656 | CONTROLLER, PRESSURE | Pressure at inlet line 400-PV-670 |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC656-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 15/12/18 | MC-PM-008-M6
938971 | M400PIC801 | CONTROLLER, PRESSURE | ESD valve at Muss.-Adia Jet A1 P/L from 400-P-018A |  | CLOSLOOP | M400PRESS | 1 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PIC801-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/12/18 | MC-PM-008-M6
938972 | M400PIC881 | CONTROLLER, PRESSURE | Pressure Outlet line of metering skid 400-FT-861 |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC881-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 20/12/18 | MC-PM-008-M6
938973 | M400PIC929 | CONTROLLER, PRESSURE | PR. CONT. VALVE ON COMON HEADER TO FIRE PUMP. |  | CLOSLOOP | M400PRESS | 3 | CLOSLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PIC929-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/12/18 | MC-PM-008-M6
938974 | M400POY801A | VALVE, SOLENOID | Solenoid valve for 400-POV-801 | 938971 | SOL_VLV | M400PIC801 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938975 | M400POY801B | VALVE, SOLENOID | Solenoid valve for 400-POV-801 | 938971 | SOL_VLV | M400PIC801 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938976 | M400POY537A | VALVE, SOLENOID, 1/4" , 5.7MM , 110VAC , NPT , 316 SS , 3/2-WAY , UNIVERSAL , 0- | O/P for ESD Valve 400-POV-537 | 936422 | SOL_VLV | M400POV537 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938977 | M400POY537B | VALVE, SOLENOID, 1/4" , 5.7MM , NPT , 316 SS , 3/2-WAY , UNIVERSAL , 0-10 BAR , | ESD Valve at Nap/Ref. P/L to 400-L-003A/B | 936422 | SOL_VLV | M400POV537 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938978 | M400POY571A | VALVE, SOLENOID, 1/4" , 5.7MM , 110VAC , NPT , 316 SS , 3/2-WAY , UNIVERSAL , 0- | Solenoid valve for 400-POV-571 | 936423 | SOL_VLV | M400POV571 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938979 | M400POY571B | VALVE, SOLENOID, 1/4" , 5.7MM , 110VAC , NPT , 316 SS , 3/2-WAY , UNIVERSAL , 0- | Solenoid valve for 400-POV-571 | 936423 | SOL_VLV | M400POV571 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938980 | M400POY653A | VALVE, SOLENOID, 1/4" , 5.7MM , 110VAC , NPT , 316 SS , 3/2-WAY , UNIVERSAL , 0- | Solenoid valve for 400-POV-653 | 936424 | SOL_VLV | M400POV653 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938981 | M400POY653B | VALVE, SOLENOID, 1/4" , 5.7MM , 110VAC , NPT , 316 SS , 3/2-WAY , UNIVERSAL , 0- | ESD valve Rws-Muss. MP P/L to Jet A1/GO/ULG 95/98 | 936424 | SOL_VLV | M400POV653 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938982 | M400POY887A | VALVE, SOLENOID | O/P for 400-POV-887 | 936427 | SOL_VLV | M400POV887 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938983 | M400POY887B | VALVE, SOLENOID | O/P for 400-POV-887 | 936427 | SOL_VLV | M400POV887 | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938984 | M400PSH831 | SWITCH, PRESSURE | Switch Pressure, M/L Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSH831-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 23/12/18 | MC-PM-009-M6
938985 | M400PSH832 | SWITCH, PRESSURE | Pressure Switch,M/L Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSH832-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 24/12/18 | MC-PM-009-M6
938986 | M400PSH833 | SWITCH, PRESSURE | Switch Pressure, M/L Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSH833-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 26/12/18 | MC-PM-009-M6
938987 | M400PSH834 | SWITCH, PRESSURE | Switch Pressure, Booster Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSH834-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 27/12/18 | MC-PM-009-M6
938988 | M400PSH835 | SWITCH, PRESSURE | Switch Pressure, Booster Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSH835-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 27/12/18 | MC-PM-009-M6
938989 | M400PSH836 | SWITCH, PRESSURE | Switch Pressure, Transfer Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSH836-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 26/12/18 | MC-PM-009-M6
938990 | M400PSH837 | SWITCH, PRESSURE | Switch Pressure, Transfer Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSH837-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/12/18 | MC-PM-009-M6
938991 | M400PSL837 | SWITCH, PRESSURE | Transfer Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSL837-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM-009-M6
938992 | M400PSL831 | SWITCH, PRESSURE | Switch Pressure, M/L Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSL831-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 29/12/18 | MC-PM-009-M6
938993 | M400PSL836 | SWITCH, PRESSURE | Transfer Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSL836-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM-009-M6
938994 | M400PSL832 | SWITCH, PRESSURE | Switch Pressure, M/L Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSL832-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 29/12/18 | MC-PM-009-M6
938995 | M400PSL835 | SWITCH, PRESSURE | Booster Pumps Deluge Valve |  | PRES_SWT | M400PRESS | 1 | PRES_SWT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400PSL835-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM-009-M6
939547 | M400VH003 | O/HEAD CRANE AT FIRE PUMP HOUSE. | O/HEAD CRANE AT FIRE PUMP HOUSE. |  | CRHO | MPH3 | 4 | CRANE | 616101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 5 | 1 | 1 | 10 | 2.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939549 | M400VH004A | MANUAL HOIST FOR INTERTANK TRANSFER PUMP HOUSE | MANUAL HOIST FOR INTERTANK TRANSFER PUMP HOUSE |  | CRHO | MPH2 | 4 | CRHO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939568 | U29TI702 | LOOP, TEMPERATURE INDICATOR INSTRU, ENDRESS HAUSER , TMT162-RB4A41N31XB + TEMP | TEMP.FOR NAPHTHA REFORMATE/HSGO LINE TO SV STATION |  | OPENLOOP | U2902L | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29TI702-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/05/19 | MC-PM-010-Y1
939569 | U29TI703 | LOOP, TEMPERATURE INDICATOR INSTRU, ENDRESS HAUSER , TMT162-RB4A41N31XB + TEMP | TEMP.TRANS.2902-L SCRAPER LAUNCHER TO SV STATION-7 |  | OPENLOOP | U2902L | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | U29TI703-SC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/05/19 | MC-PM-010-Y1
939786 | M400PI501 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-12 | Pressure for ADR 10" Naphtha Reformate P/L |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI501-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/03/19 | MC-PM-007-Y1
939787 | M400PI504 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-12 | Pr. Between ADR 10" & Ruwais 10" Naphtha P/L |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI504-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/03/19 | MC-PM-007-Y1
939788 | M400PI505 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-12 | Pr. Between ADR 10" & Ruwais 10" Naphtha P/L |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI505-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/03/19 | MC-PM-007-Y1
939789 | M400PI508 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-12 | Pr. for To/From Ruwais 10" Naphtha P/L |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI508-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/03/19 | MC-PM-007-Y1
939790 | M400PI531 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-50 | PR.TR. JET A1 RECEIVING END NAPHTHA REFORMATE P/L | 938968 |  | M400PIC531 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI531-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/02/19 | MC-PM-007-Y1
939791 | M400PI532 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-25 | PRESS. INLET TO FLOW METERING SKID 400-FT-541 |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI532-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/03/19 | MC-PM-007-Y1
939792 | M400PI533 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-25 | PRESS. INLET TO FLOW METERING SKID 400-FT-541 |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI533-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/03/19 | MC-PM-007-Y1
939793 | M400PI534 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-25 | PRESS. INLET TO FLOW METERING SKID 400-FT-541 |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI534-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/03/19 | MC-PM-007-Y1
939794 | M400PI536 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-10 | PR.TR. JET A1 RECEIVING END NAPHTHA REFORMATE P/L | 938868 |  | M400PIC536 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI536-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/02/19 | MC-PM-007-Y1
939795 | M400PI541A | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-10 | PRESS. NEPTHA/REFORM P/L, JET A1,CUSTODY METER | 938681 |  | M400FC541A | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI541A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/06/19 | MC-PM-008-Y1
939796 | M400PI541B | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-10 | PRESS. NEPTHA/REFORM P/L, JET A1,CUSTODY METER | 938682 |  | M400FC541B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI541B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/06/19 | MC-PM-008-Y1
939797 | M400PI545 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1MB1RHABU , -1 T | PR. JET A1 FROM STORAGE TANK TO BOOSTER PUMP |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI545-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 09/03/19 | MC-PM-007-Y1
939798 | M400PI547 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , -1 T | PR. SUCTION LINE BOOSTER PUMP 400-P-020 | 933878 |  | M400P020 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI547-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
939799 | M400PI554 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-10 | PR. SUCTION LINE MAIN LINE PUMP 400-P-019 | 935830 |  | M400P019 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI554-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
939800 | M400PI550 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-12 | Discharge line pressure Booster pump 400-P-020 | 933878 |  | M400P020 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI550-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
969184816 | M410MP018A | MOTOR,ELECTRIC, Anti-Static Chemical Injection Package, IP 55, 50 Hertz, 415 Volts V, TEFC : 4A1A1 (IC411), _071M, Ball, Vertical, 3, Star, Limited to 7 times rated, Counter clockwise, F, II-C ZONE 1 T4, 36.0_ kg, 180 ºC For Alarm _190 ºC For Shutdown | Anti-Static Neat Chemical Injection Pump Motor |  | MOTOR | M410P018A | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP018A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-LT1-6M
969184817 | M410MP018B | MOTOR,ELECTRIC, Anti-Static Chemical Injection Package, IP 55, 50 Hertz, 415V V, TEFC : 4A1A1 (IC411), _071M, Ball, Vertical, RPM _870, 3, Star, Limited to 7 times rated, Counter clockwise, F, II-C 1, 36.0_ kg, 180 ºC For Alarm _190 ºC For Shutdown | Anti-Static Neat Chemical Injection Pump Motor |  | MOTOR | M410P018B | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP018B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-LT1-6M
969184818 | M410MP019A | Anti-Static Neat Chemical Injection Pump Motor | Anti-Static Chemical Dilution Pump Motor |  | MOTOR | M410P019A | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP019A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-LT1-6M
969184819 | M410MP019B | Anti-Static Neat Chemical Injection Pump Motor | Anti-Static Chemical Dilution Pump Motor |  | MOTOR | M410P019B | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP019B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-LT1-6M
969184820 | M410FT501 | Coriolis Flow Meter ENDRESS + HAUSER 410FT501. | FLOW TX ON ANTY STATIC CHEMICAL Coriolis Flow Meter |  | FL_MTR | M410FLOW | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184821 | M410L030 | Static Mixer | Static Mixer |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 10 | 5 | 50 | 10 | 5 | 6.0969 | Non Critical | Medium | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275281 | M410MOV662 | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270049 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275282 | M410SDV400A | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269436 | CNTR_VLV | M410L005A | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275283 | M410SDV400B | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269437 | CNTR_VLV | M410L005B | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275284 | M410SDV400C | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269438 | CNTR_VLV | M410L005C | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275285 | M410SDV400D | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269439 | CNTR_VLV | M410L005D | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275286 | M410SDV400E | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269440 | CNTR_VLV | M410L005E | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275287 | M410SDV401A | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269441 | CNTR_VLV | M410L001A | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275288 | M410SDV401B | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269442 | CNTR_VLV | M410L001B | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275289 | M410SDV401C | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269443 | CNTR_VLV | M410L001C | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275290 | M410SDV401D | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269444 | CNTR_VLV | M410L001D | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275291 | M410SDV403 | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 28 X 24, 300#, A105 | 969269445 | CNTR_VLV | M410PLR007 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275292 | M410SDV403A | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269446 | CNTR_VLV | M410L011A | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275293 | M410SDV403B | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 2 x 1.5, 300#, A216 WCB | 969269447 | CNTR_VLV | M410L011B | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275294 | M410SDV415 | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 28 X 24, 600#, A105 | 969269448 | CNTR_VLV | M410PT412 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275295 | M410SDV427 | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 12 X 10, 900#, A216 WCB | 969269449 | CNTR_VLV | M410PLR005 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275296 | M410SDV435 | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 12 X 10, 900#, A216 WCB | 969269450 | CNTR_VLV | M410PLR006 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275297 | M410SDV448 | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 20 X 16, 300#, A216 WCB | 969269451 | CNTR_VLV | M410PLR007 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275298 | M410SDV463 | ACTUATOR for PNEUMATIC OPERATED VALVE (ESD) | Valve, Ball, 10 X 8, 300#, A216 WCB | 969269452 | CNTR_VLV | M410PLR007 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275299 | M410GLV2123304 | 2" Globe Valve, BS 1873, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Plug Disc, ASME B16.5 | 2" Globe Valve, BS 1873, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Plug Disc, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275300 | M400DCSSC005 | DCS SYSTEM CABINET | DCS SYSTEM CABINET |  | BLDGS | M400MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275302 | M400DCSSRC002 | DCS SYSTEM CABINET | DCS SYSTEM CABINET |  | BLDGS | M400MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275303 | M400DCSSRC003 | DCS SYSTEM CABINET | DCS SYSTEM CABINET |  | BLDGS | M400MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275304 | M400ESDMC004 | DCS SYSTEM CABINET | DCS SYSTEM CABINET |  | BLDGS | M400MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275305 | M400ESDMC005 | DCS SYSTEM CABINET | DCS SYSTEM CABINET |  | BLDGS | M400MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275306 | M400ESDSC004 | DCS SYSTEM CABINET | DCS SYSTEM CABINET |  | BLDGS | M400MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275310 | M400ME002 | INJECTION SYSTEM FOR DYE (GREEN) | TANK GREEN DYE INJECTION IN ULG-95. |  | PACKAGE | M400CINJ | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275311 | M400ME003 | CHEMICAL INJECTION PACKAGE | TANK FOR RED DYE INJECTION IN ULG-91. |  | PACKAGE | M400CINJ | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275371 | PL312BAV21243001 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275372 | PL312BAV21243002 | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275373 | PL312BAV21243003 | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-160 Nipple Plain End L=100mm, Fire Safe | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-160 Nipple Plain End L=100mm, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275374 | PL312BAV21243004 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275375 | PL312BAV21243005 | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 |  | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275376 | PL312BAV21243006 | 10" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 |  | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275377 | PL312BAV21243007 | 12" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 12" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275378 | PL312BAV21243008 | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275394 | PL312BAV21243024 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275395 | PL312BAV21243025 | 10" 6.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 300, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" 6.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 300, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275396 | PL312BAV21243026 | 10" 6.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 600, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" 6.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 600, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275397 | PL312BAV21243027 | 12" 8.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 600, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 12" 8.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 600, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275398 | PL312BAV21243028 | 10" Ball Valve Long Pattern Reduced Bore, API 6D, Class 300, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe | 10" Ball Valve Long Pattern Reduced Bore, API 6D, Class 300, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275399 | PL312BB101 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL312BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275400 | PL312BB201 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL312BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275401 | PL312BB301 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL312BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275402 | PL312BB401 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL312BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275403 | PL312BB501 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL312BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275404 | PL312BB601 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL312BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275405 | PL312BB602 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL312BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275406 | PL312CCTV008 | Short Range Thermal Camera | Short Range Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275407 | PL312CHV21233001 | 3" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 3" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275408 | PL312CHV21263001 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 600, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 600, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275409 | PL312CHV21263002 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 900, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 900, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275410 | PL312CPPSM001 | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE |  | TRANSFMR | PL312SCB | 3 | TRANSFMR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275411 | PL312CPPSM002 | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE |  | TRANSFMR | PL312SCB | 3 | TRANSFMR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275412 | PL312CPPSM003 | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE |  | TRANSFMR | PL312SCB | 3 | TRANSFMR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275342 | PL312EOV001 | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"ULG PIPELINE | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"ULG PIPELINE |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275413 | PL312EOV001 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-001 | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"ULG PIPELINE | 969275342 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275343 | PL312EOV002 | ELECTRO HYDRAULIC VALVE, ULG FROM TARRIFTAPOFF AT SV STATION-4 | ELECTRO HYDRAULIC VALVE, ULG FROM TARRIFTAPOFF AT SV STATION-4 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275414 | PL312EOV002 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-002 | ELECTRO HYDRAULIC VALVE, ULG FROM TARRIFTAPOFF AT SV STATION-4 | 969275343 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275344 | PL312EOV003 | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"GAS OIL PIPELINE | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"GAS OIL PIPELINE |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275415 | PL312EOV003 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-003 | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"GAS OIL PIPELINE | 969275344 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275345 | PL312EOV004 | ELECTRO HYDRAULIC VALVE, GAS OIL FROM TARRIFTAPOFF AT SV STATION-4 | ELECTRO HYDRAULIC VALVE, GAS OIL FROM TARRIFTAPOFF AT SV STATION-4 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275416 | PL312EOV004 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-004 | ELECTRO HYDRAULIC VALVE, GAS OIL FROM TARRIFTAPOFF AT SV STATION-4 | 969275345 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275346 | PL312EOV31201 | ELECTRO HYDRAULIC VALVE, SV STATION-1 | ELECTRO HYDRAULIC VALVE, SV STATION-1 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275417 | PL312EOV31201 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-01 | ELECTRO HYDRAULIC VALVE, SV STATION-1 | 969275346 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275347 | PL312EOV31202 | ELECTRO HYDRAULIC VALVE, SV STATION-2 | ELECTRO HYDRAULIC VALVE, SV STATION-2 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275418 | PL312EOV31202 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-02 | ELECTRO HYDRAULIC VALVE, SV STATION-2 | 969275347 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275348 | PL312EOV31203 | ELECTRO HYDRAULIC VALVE, SV STATION-3 | ELECTRO HYDRAULIC VALVE, SV STATION-3 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275419 | PL312EOV31203 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-03 | ELECTRO HYDRAULIC VALVE, SV STATION-3 | 969275348 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275929 | PL100BAV21243001 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195633 | M410PDB001 | POWER DISTRIBUTION BOARD CABINET FOR SIS-001DCSSYSTEM | POWER DISTRIBUTION BOARD CABINET FOR SIS-001DCSSYSTEM |  | SWBOARD | M410SCB | 3 | SWBOARD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PDB001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 20/10/18 | ME-PNL1-PM-M6
969195634 | M410FG001 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195635 | M410FG002 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195636 | M410FG003 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195637 | M410FG004 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195638 | M410FG005 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195639 | M410FG006 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195640 | M410FG007 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195641 | M410FG008 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195642 | M410FG009 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195643 | M410FG010 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195644 | M410FG011 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195645 | M410FG012 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195646 | M410FG013 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195647 | M410FG014 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195648 | M410FG015 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195649 | M410FG016 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195650 | M410FG017 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195651 | M410FG018 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195652 | M410FG019 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195653 | M410FG020 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195654 | M410FG021 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195655 | M410FG022 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195656 | M410FG023 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195657 | M410FG024 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195658 | M410FG025 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195659 | M410FG026 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195660 | M410FG027 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195661 | M410FG028 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195662 | M410FG029 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195663 | M410FG030 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195664 | M410FG031 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195665 | M410FG032 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195666 | M410FG033 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195667 | M410FG034 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195668 | M410FG035 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195669 | M410FG036 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195670 | M410FG037 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195671 | M410FG038 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195672 | M410FG039 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195673 | M410FG040 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195674 | M410FG041 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195675 | M410FG042 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195676 | M410FG043 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195677 | M410FG044 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195678 | M410FG045 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195679 | M410FG046 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195680 | M410FG047 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195681 | M410FG048 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195682 | M410FG049 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195683 | M410FG050 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195684 | M410FG051 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195685 | M410FG052 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195686 | M410FG053 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195687 | M410FG054 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195688 | M410FG055 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195689 | M410FG056 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195690 | M410FG057 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195691 | M410FG058 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195692 | M410FG059 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195693 | M410FG060 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195694 | M410FG061 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195695 | M410FG062 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205137 | M410MOV0808 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175641 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0808-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205138 | M410MOV0809 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175642 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0809-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205139 | M410MOV0810 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175643 | MOV | M410T008 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0810-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205140 | M410MOV0811 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175644 | MOV | M410T008 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0811-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205141 | M410MOV0812 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-008 | 969175645 | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0812-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205142 | M410MOV0901 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175646 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0901-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205143 | M410MOV0902 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175647 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0902-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205144 | M410MOV0903 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175648 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0903-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205145 | M410MOV0904 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175649 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0904-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205146 | M410MOV0905 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175650 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0905-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205147 | M410MOV0906 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175651 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0906-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205148 | M410MOV0907 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175652 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0907-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205149 | M410MOV0908 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175653 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0908-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205150 | M410MOV0909 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175654 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0909-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969205151 | M410MOV0910 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175655 | MOV | M410T009 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0910-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/01/19 | ME-PM-002-M6
969205152 | M410MOV0911 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175656 | MOV | M410T009 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0911-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/01/19 | ME-PM-002-M6
969205153 | M410MOV0912 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-009 | 969175657 | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0912-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/01/19 | ME-PM-002-M6
969205154 | M410MOV1001 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175658 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1001-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 31/01/19 | ME-PM-002-M6
969205155 | M410MOV1002 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175659 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1002-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 31/01/19 | ME-PM-002-M6
969205156 | M410MOV1003 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175660 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1003-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/02/19 | ME-PM-002-M6
969205157 | M410MOV1004 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175661 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1004-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/02/19 | ME-PM-002-M6
969205158 | M410MOV1005 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175662 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1005-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/02/19 | ME-PM-002-M6
969274272 | M400LG531A | GAUGE,LEVEL, TRANSPARENT | Level for Filter Coalescer Seperator 400-L-003A |  | INDICATR | M400L003A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969274273 | M400LG532A | GAUGE,LEVEL, TRANSPARENT | Level for Filter Coalescer Seperator 400-L-003B |  | INDICATR | M400L003B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969274274 | M400LG751A | GAUGE,LEVEL, TRANSPARENT | Level for Filter Coalescer 400-L-004A |  | INDICATR | M400L004A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969274275 | M400LG752A | GAUGE,LEVEL, TRANSPARENT | Level for Filter Coalescer 400-L-004B |  | INDICATR | M400L004B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281271 | PL300RTU007 | RTU Cabinet | SCADA SYSTEM | 936852 | BLDGS | PL300SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | PL300RTU007-MC1 | ACTIVE | CONT | PM | IN | 12 | MONTHS | 25/04/19 | MC-PM-030-M6
969270361 | M410PT743 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME010 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT743-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270362 | M410PT744 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME010 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT744-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270363 | M410PT701 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M400ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT701-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270364 | M410PT702 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M400ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT702-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270365 | M410PT711 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M400ME003 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT711-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270366 | M410PT712 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M400ME003 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT712-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270367 | M410PT761 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME201 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT761-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270368 | M410PT762 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME201 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT762-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270369 | M410PT102 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX |  | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT102-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270370 | M410PT103 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX |  | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT103-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270371 | M410PT104 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX |  | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT104-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270372 | M410PT105 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX |  | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT105-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270373 | M410PT106 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX | M410ME106 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT106-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270374 | M410PT107 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX | M410ME107 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT107-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270375 | M410PT108 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX | M410ME108 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT108-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270376 | M410PT001 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT001-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270377 | M410PT002 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410V006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT002-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270378 | M410PT003 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410V006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT003-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270379 | M410PT004 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410V006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT004-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270380 | M410PT052 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410ME011 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT052-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270381 | M410PT053 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410ME010 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT053-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270382 | M410PT245A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT245A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270383 | M410PT245B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT245B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270384 | M410PT267 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT267-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270385 | M410PT268 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT268-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270386 | M410PT269 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT269-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270387 | M410PT270 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT270-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270388 | M410PT277A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P002A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT277A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270389 | M410PT277B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P002B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT277B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270390 | M410PT280 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P002A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT280-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270391 | M410PT281 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P002A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT281-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270392 | M410PT282 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P002B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT282-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270393 | M410PT283 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P002B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT283-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270394 | M410PT290 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P003A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT290-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270395 | M410PT291 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P003A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT291-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270396 | M410PT292 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P003B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT292-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270397 | M410PT293 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P003B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT293-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270398 | M410PT300A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P004A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT300A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270399 | M410PT300B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P004B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT300B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270400 | M410PT303 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P004A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT303-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270401 | M410PT304 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P004A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT304-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270402 | M410PT305 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P004B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT305-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969133411 | M400LT557 | TRANSMITTER,LIQUID LEVEL, CAST ALUMINIUM - WP TO IP65, ASTM A105, 4-20mA + HART, 1/2" NPT, 24 V DC, 2 WIRE, GUIDED WAVE RADAR | LEVEL INDICATOR OF LUBRICITY IMPROVER TANK 302. | 937601 | LVL_TX | M400T302 | 2 | TNK_GUG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969133412 | M400LT558 | TRANSMITTER,LIQUID LEVEL, CAST ALUMINIUM - WP TO IP65, ASTM A105, 4-20mA + HART, 1/2" NPT, 24 V DC, 2 WIRE, ELECTRONIC | LEVEL INDICATOR OF LUBRICITY IMPROVER TANK 302. | 937601 | LVL_TX | M400T302 | 2 | TNK_GUG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131434 | M400XSP001 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, 24VDC, YES | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131439 | M400XSP006 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, 24VDC, YES | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131441 | M400XSP008 | DETECTOR,FIRE PROTECTION, 24VDC, YES, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131444 | M400XSP011 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131446 | M400XSP013 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131447 | M400XSP014 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN FLOOR AND FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131450 | M400XSP017 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN FLOOR AND FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131452 | M400XSP019 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131456 | M400XSP023 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131458 | M400XSP025 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM BETMEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131460 | M400XSP027 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT CONTROL ROOM BETWEN FLOOR AND FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131462 | M400XSP029 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL ROOM BETWEN FLOOR AND FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131437 | M400XSP004 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, 24VDC, YES | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131438 | M400XSP005 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, 24VDC, YES | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131442 | M400XSP009 | DETECTOR,FIRE PROTECTION, 24VDC, YES, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131445 | M400XSP012 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131448 | M400XSP015 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN FLOOR AND FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131449 | M400XSP016 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT RACK ROOM BETWEN FLOOR AND FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131451 | M400XSP018 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131453 | M400XSP020 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131454 | M400XSP021 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM BETMEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131455 | M400XSP022 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131457 | M400XSP024 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM BETMEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131459 | M400XSP026 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT CONTROL/CONSOLE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131461 | M400XSP028 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT CONTROL ROOM BETWEN FLOOR AND FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131463 | M400XSP030 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT UPS ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131464 | M400XSP031 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT UPS ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131466 | M400XSP033 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT UPS ROOM BETWEN CEILING & FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131471 | M400XSP038 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131480 | M400XSP047 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TELECOM ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131486 | M400XSP053 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR CORRIDOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131488 | M400XSP055 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR CONFERENCE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131490 | M400XSP057 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR DOCUMENTATION ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131491 | M400XSP058 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR LOBBY-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131493 | M400XSP060 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR PRAYER ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131494 | M400XSP061 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR LOCKER ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131501 | M400XSP068 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR HVAC ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131507 | M400XSP082 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131509 | M400XSP084 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131510 | M400XSP085 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131474 | M400XSP041 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM BETWEN CEILING AND FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131477 | M400XSP044 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM BETWEN FLOOR AND FALSE FLORR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131479 | M400XSP046 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TELECOM ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131498 | M400XSP065 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TOILET-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131512 | M400XSP087 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131514 | M400XSP089 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131515 | M400XSP090 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131522 | M400XSP097 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR FOR OFFICE ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131525 | M400XSP100 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SUB STATION HVAC AIR INTAKE DUCT |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131526 | M400XSP101 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SUB STATION HVAC AIR INTAKE DUCT |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131528 | M400XSP106 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN TOILET OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131529 | M400XSP107 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN PRINTER/FAX ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131530 | M400XSP108 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CONFERENCE ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131209 | M400LP008Y502 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WEST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131210 | M400LP008B502 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WEST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131211 | M400LP008R503 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WEST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131212 | M400LP011Y301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WEST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131213 | M400LP011Y302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WEST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131214 | M400LP011Y303 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WEST BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131215 | M400LP008Y402 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131216 | M400LP008Y102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANKTK-111 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131217 | M400LP008R101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANKTK-112 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131218 | M400LP008Y201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANKTK-116 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131219 | M400LP008R201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANKTK-116 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131220 | M400LP010Y101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-117 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131221 | M400LP010R101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-117 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131222 | M400LP010B101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-118 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131223 | M400LP010R102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-119 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131224 | M400LP010B102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-120 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131225 | M400LP010Y102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-120 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131226 | M400LP008B102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-115 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131162 | M400LP006Y603 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131171 | M400LP011Y102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131172 | M400LP011R102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131173 | M400LP011B102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131174 | M400LP011B101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131175 | M400LP011Y101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131176 | M400LP011R101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131177 | M400LP011R103 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131178 | M400LP011Y103 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131179 | M400LP011R202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF WAREHOUSE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131180 | M400LP011Y201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF ADMIN BLDG. ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131181 | M400LP011B103 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT BACK SIDE OF ADMIN BLDG. ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131182 | M400LP011R201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT FIRE WATER PUMP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131183 | M400LP011Y202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT FIRE WATER PUMP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131184 | M400LP011B201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT FIRE WATER PUMP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131163 | M400LP006R602 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131164 | M400LP006Y201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR TERMINAL MAIN ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131165 | M400LP006R303 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SUB STATION SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131167 | M400LP006R201 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT SUB STATION SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131168 | M400LP006Y303 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT CONTROL ROOM SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131185 | M400LP011B202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WWTP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131187 | M400LP011B401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WWTP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131188 | M400LP011Y401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WWTP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131189 | M400LP011R401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT WWTP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131190 | M400LP010B202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT FIRE WATER PUMP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131191 | M400LP010Y202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT FIRE WATER PUMP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131192 | M400LP010R202 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT FIRE WATER PUMP AREA ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131193 | M400LP010R303 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT TANK TK-120 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131194 | M400LP010B302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT TANK TK-119 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131195 | M400LP010Y302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT TANK TK-119 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131196 | M400LP010R302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT TANK TK-118 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131197 | M400LP010B301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT TANK TK-118 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131198 | M400LP010Y301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT TANK TK-117 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131199 | M400LP010R301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE AT TANK TK-117 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131227 | M400LP008B102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-115 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131228 | M400LP008B101 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE NEAR TANK TK-116 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969486628 | M410PSV31B | PRESSURE SAFETY VALVE 18KG. | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P031B | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969486629 | M410PSV31C | PRESSURE SAFETY VALVE 18KG. | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P031C | 1 | PSV | 617101-310600 | IRPMTERMINAL | NOT READY | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969486630 | M410PSV31D | PRESSURE SAFETY VALVE 18KG. | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P031D | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935614 | SMTP15 |  | TEST POINT# 15 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935615 | SMTP16 |  | TEST POINT# 16 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935616 | SMTP17 |  | TEST POINT# 17 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935629 | SMTP30 |  | TEST POINT# 30 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935630 | SMTP32 |  | TEST POINT# 32 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935631 | SMTP33 |  | TEST POINT# 33 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275125 | M410GAV21233002 | 3" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 3" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275126 | M410GAV21233003 | 4" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 4" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275127 | M410GAV21233004 | 14" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 14" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275128 | M410GAV21233005 | 16" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 16" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275129 | M410GAV21233006 | 18" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 18" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275130 | M410GAV21233007 | 2" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275131 | M410GAV21233008 | 3" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 3" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275132 | M410GAV21233009 | 14" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 14" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275133 | M410GAV21233010 | 16" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 16" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275134 | M410GAV21233011 | 18" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 18" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275135 | M410GAV21233012 | 12" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5, UL/FM Approved | 12" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275136 | M410GAV21233013 | 3" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5, UL/FM Approved | 3" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275137 | M410GAV21233014 | 2" Gate Valve, ISO 10434, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275138 | M410GAV21233015 | 2" Gate Valve, ISO 10434, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275139 | M410GAV21233016 | 10" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 10" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275140 | M410GAV21233017 | 14" Gate Valve, ISO 10434, Class 600, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 | 14" Gate Valve, ISO 10434, Class 600, Raised Face, Bolted Bonnet OS&Y, Gear Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275141 | M410GAV21233018 | 6" Gate Valve, ISO 10434, Class 900, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 | 6" Gate Valve, ISO 10434, Class 900, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275142 | M410GAV21273001 | 0.5" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge | 0.5" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275143 | M410GAV21273002 | 0.75" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge | 0.75" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275144 | M410GAV21273003 | 1" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge | 1" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275145 | M410GAV21273004 | 2" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge | 2" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275146 | M410GAV21273005 | 3" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge | 3" Gate Valve, BS 5154 Series. A, PN 25, Female Threaded End, Union Bonnet, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275147 | M410GAV21273006 | 2" Gate Valve, BS 5154 Series. A, Class 150, Flat Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge, ASME B16.5 | 2" Gate Valve, BS 5154 Series. A, Class 150, Flat Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275148 | M410GAV21273007 | 3" Gate Valve, BS 5154 Series. A, Class 150, Flat Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge, ASME B16.5 | 3" Gate Valve, BS 5154 Series. A, Class 150, Flat Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275149 | M410GAV21273008 | 2" Gate Valve, BS 5154 Series. A, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge, ASME B16.5 | 2" Gate Valve, BS 5154 Series. A, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM B148 Class C95800, Trim Al-Bronze, Solid Wedge, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275150 | M410GLV21223001 | 0.75" Globe Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Plug Disc | 0.75" Globe Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Plug Disc |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275151 | M410GLV21223002 | 1" Globe Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Plug Disc | 1" Globe Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Plug Disc |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275152 | M410GLV21233001 | 2" Globe Valve, BS 1873, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 | 2" Globe Valve, BS 1873, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275153 | M410GLV21233002 | 2" Globe Valve, BS 1873, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 | 2" Globe Valve, BS 1873, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275154 | M410GLV21233003 | 4" Globe Valve, BS 1873, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 | 4" Globe Valve, BS 1873, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132805 | M400P208B | PUMP, SUBMERSIBLE | FEED PUMP B- CHAIN I |  | PUCE | M400WWTPPUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P208B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 02/11/18 | MM-PM-016-M6
969132808 | M400P210A | PUMP, DIAPHRAGM | COAQULATION DOSING PUMP A |  | PURE | M400WWTPPUMP | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P210A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/12/18 | MM-PM-019-M6
969132809 | M400P210B | PUMP, DIAPHRAGM | COAQULATION DOSING PUMP B |  | PURE | M400WWTPPUMP | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P210B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/12/18 | MM-PM-019-M6
969132810 | M400P211A | PUMP, DIAPHRAGM | CAUSTIC SODA DOSING PUMP A |  | PURE | M400WWTPPUMP | 3 | PURE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P211A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-019-M6
969132811 | M400P211B | PUMP, DIAPHRAGM | CAUSTIC SODA DOSING PUMP B |  | PURE | M400WWTPPUMP | 2 | PURE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P211B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-019-M6
969132812 | M400P212A | PUMP, SCREW | POLY ELECTROLYTE PUMP - A |  | PUSC | M400WWTPPUMP | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P212A-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 10/05/19 | MM-PM-015-Y1
969132813 | M400P212B | PUMP, SCREW | POLY ELECTROLYTE PUMP - B |  | PUSC | M400WWTPPUMP | 2 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P212B-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 11/05/19 | MM-PM-015-Y1
969259607 | M410PKG2306003 | COMPRESSOR, ELECTRIC | Electrical Compressor |  | VESSEL | M410MISC | 3 | COMPRS | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969259608 | M410SSW2306001 | SHOWER, EYE WASHER, SAFETY | SAFETY SHOWER & EYE WASHER |  | VESSEL | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | o | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132470 | PL300XAC001/03 | CALL POINT, FIRE ALARM PUSH BUTTON, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, RED, YES | MANUAL CALL POINT AT MAIN GATE SV STATION - 3 |  | PB_HS-MC | PL300SVS3 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC001/03-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM07.M3
969132471 | PL300XAC002/03 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT EMERGENCY GATE SV STATION - 3 |  | PB_HS-MC | PL300SVS3 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC002/03-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 25/08/18 | MFPS-PM07.M3
969132472 | PL300XAC001/04 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT MAIN GATE SV STATION - 4 |  | PB_HS-MC | PL300SVS4 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC001/04-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM07.M3
969132473 | PL300XAC002/04 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT EMERGENCY GATE SV STATION - 4 |  | PB_HS-MC | PL300SVS4 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC002/04-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM07.M3
969132474 | PL300XAC001/05 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT MAIN GATE SV STATION - 5 |  | PB_HS-MC | PL300SVS5 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC001/05-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM07.M3
969132475 | PL300XAC002/05 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT EMERGENCY GATE SV STATION - 5 |  | PB_HS-MC | PL300SVS5 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC002/05-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM07.M3
969132476 | PL300XAC001/06 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT MAIN GATE SV STATION - 6 |  | PB_HS-MC | PL300SVS6 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC001/06-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM07.M3
969132477 | PL300XAC002/06 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT EMERGENCY GATE SV STATION - 6 |  | PB_HS-MC | PL300SVS6 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC002/06-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM07.M3
969132478 | PL300XAC001/07 | CALL POINT, RED, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON | MANUAL CALL POINT AT MAIN GATE SV STATION - 7 |  | PB_HS-MC | PL300SVS7 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC001/07-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM07.M3
969132479 | PL300XAC002/07 | CALL POINT, YES, IP66 & IP 67, EEx emd IIT4 or EEx ed IIT6, FIRE ALARM PUSH BUTTON, RED | MANUAL CALL POINT AT EMERGENCY GATE SV STATION - 7 |  | PB_HS-MC | PL300SVS7 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC002/07-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM07.M3
969132043 | PL300BATT007A | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-A =38 Nos FOR SV-7. |  | BATTERY | PL300BAT007 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934399 | PL300ODF005 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | PL300MUX005 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934400 | PL300ODF006 | TELECOM MAIN DISTRIBUTlON FRAME | OPTICAL DIST FRAME, 48 PORT |  |  | PL300MUX006 | 2 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936305 | M400PT437 | TRANSMITTER, PRESSURE, ELECTRONIC , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , | PLAN 53 B - PRESSURE TXS (SEAL PRESSURE/M400P018A) | 935828 | PRES_TX | M400P018A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400PT437-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 25/11/18 | MC-PM-007-Y1
936306 | M400PT438 | TRANSMITTER, PRESSURE, ELECTRONIC , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , | PLAN 53 B - PRESSURE TRANSMITTER FOR M400P018B | 935829 | PRES_TX | M400P018B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT438-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/12/18 | MC-PM-007-Y1
936307 | M400PT452 | TRANSMITTER, PRESSURE, ELECTRONIC , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , | PLAN 53 B - PRESSURE TRANSMITTER (M400P018B) | 935829 | PRES_TX | M400P018B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT452-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/12/18 | MC-PM-007-Y1
936308 | M400PT453 | TRANSMITTER, PRESSURE, ELECTRONIC , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , | PLAN 53 B - PRESSURE TRANSMITTER (M400P018B) | 935829 | PRES_TX | M400P018B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT453-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/12/18 | MC-PM-007-Y1
936309 | M400PT467 | TRANSMITTER, PRESSURE, ELECTRONIC , -1 TO 55.2 BAR , 4-20MA , 10.5 - 36vdc , 1/2 | PLAN 53 B - PRESSURE TRANSMITTER (M400P019) | 935830 | PRES_TX | M400P019 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400PT467-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
936310 | M400PT468 | TRANSMITTER, PRESSURE, ELECTRONIC , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , | PLAN 53 B - PRESSURE TRANSMITTER (M400P019) | 935830 | PRES_TX | M400P019 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400PT468-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
936311 | M400SSP16AR1 | SYSTEM, PUMP MECHANICAL SEAL | ULG95/98/GASOIL/JETA1/KEROSENE M/LINEPUMP SEAL SYS |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936312 | M400SSP16AR2 | SYSTEM, PUMP MECHANICAL SEAL | ULG95/98/GASOIL/JETA1/KEROSENE M/LINEPUMP SEAL SYS |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936313 | M400SSP16BR1 | SYSTEM, PUMP MECHANICAL SEAL | ULG95/98/GASOIL/JETA1/KEROSENE M/LINEPUMP SEAL SYS |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936328 | M400LCP016AA | PANEL CONTROL | ULG95/98/GO/JETA1/KEROSE M/LINE PUMP-PANEL |  | CLDCPS | M400P016A | 1 | CLDCPS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936329 | M400LCP016AB | PANEL CONTROL | ULG95/98/GO/JETA1/KEROSE M/LINE PUMP-PANEL |  |  | M400P016A | 1 | CLDCPS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936330 | M400LCP016BA | PANEL CONTROL | ULG95/98/GO/JETA1/KEROSE M/LINE PUMP-PANEL |  |  | M400P016B | 1 | CLDCPS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936331 | M400LCP016BB | PANEL CONTROL | ULG95/98/GO/JETA1/KEROSE M/LINE PUMP-PANEL |  |  | M400P016B | 1 | CLDCPS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936332 | M400LCP019A | PANEL CONTROL | OFF SPEC JET A1 MAIN LINE PUMP-PANEL |  |  | M400P019 | 1 | CLDCPS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936333 | M400LCP019B | PANEL CONTROL | OFF SPEC JET A1 MAIN LINE PUMP-PANEL |  |  | M400P019 | 1 | CLDCPS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130776 | M400LP002 | DISTRIBUTION BOARD,LIGHTING, CONTROL ROOM, S/S-400 | INDOOR LIGHTING & SMALL POWER PANEL AT CONTROL ROOM |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP002-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
969130778 | M400LP013 | DISTRIBUTION BOARD,LIGHTING, FIRE WATER PUMP HOUSE, S/S-400 | INDOOR LIGHTING AND SMALL POWER PANEL AT WWTP MUSAFFAH TERMINAL |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400LP013-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
969130779 | M400LP012 | DISTRIBUTION BOARD,LIGHTING, WWTP ELECTRICAL ROOM, WWTP SUB STATION,400-MCC-001 | INDOOR LIGHTING & SMALL POWER DISTRIBUTION PANEL AT WWTP |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400LP012-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/11/18 | ME-PM-011-M6
969130780 | M400LP016 | DISTRIBUTION BOARD,LIGHTING, WARE HOUSE, WWTP ELECTRICAL ROOM | INDOOR LIGHTING PANEL AT WAREHOUSE BUILDING |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400LP016-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 17/10/18 | ME-PNL1-PM-M6
969130781 | M400LP017 | DISTRIBUTION BOARD,LIGHTING, FIRE STATION, S/S-400,400-PC-001,FED FROM 400-LP-005 | INDOOR LIGHTING PANEL AT FIRE STATION |  | LIGHT | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400LP017-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
969130783 | M400ELP007 | DISTRIBUTION BOARD,LIGHTING, ADMINISTRATION BUILDING,ELECTRICAL ROOM, S/S-400,FED FROM 400-ELP-001 FIRE & SAFETY | INDOOR EMERGENCY LIGHTING PANEL AT ADMINISTRATION BUILDING ELECT.ROOM |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP007-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
969130785 | M400ELP011 | DISTRIBUTION BOARD,LIGHTING, CONTROL ROOM-UPS ROOM, S/S-400,FED FROM 400-ELP-002 | INDOOR EMERGENCY LIGHTING DISTRIBUTION PANEL AT CONTROL ROOM-UPS ROOM |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP011-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/10/18 | ME-PNL1-PM-M6
969130777 | M400LP004 | DISTRIBUTION BOARD,LIGHTING, ADMINISTRATION BUILDING ELECTRICAL ROOM, S/S-400 | INDOOR LIGHTING & SMALL POWER PANEL AT ADMIN.BUILDING ELECT.ROOM |  |  | M400SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400LP004-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
ELS57584 | MLIGHTPOLE012 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT AT METERING SKID AREA |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57585 | MLIGHTPOLE013 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT INTERNAL SIDE BET T-101 & 102. |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57586 | MLIGHTPOLE014 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET T-103 & 104 INTERNAL SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57587 | MLIGHTPOLE015 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET T-104 & 105 INTERNAL SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57589 | MLIGHTPOLE016 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET T-105 & 106 INTERNAL SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELS57590 | MLIGHTPOLE017 | LIGHT, SODIUM VAPOUR , 240VAC 50HZ , WHITE | POLE LIGHT BET T-106 & 107 INTERNAL SIDE |  | LIGHT | MLIGHTING | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278770 | PL315CCTV009 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278771 | PL315CCTV010 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265941 | PL100PG415 | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265942 | PL100PP001 | 400V POWER PANEL | 400V POWER PANEL |  | SWBOARD | PL100SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265943 | PL100PSV400A | PRESSURE SAFETY VALVE, 2" 300# X 3" 150# RF, SET PR:18KG/CM2G | PRESSURE SAFETY VALVE |  | PSV | PL100VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265944 | PL100PSV400B | PRESSURE SAFETY VALVE, 2" 300# X 3" 150# RF, SET PR:18KG/CM2G | PRESSURE SAFETY VALVE |  | PSV | PL100VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265945 | PL100PT400 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265946 | PL100PT400A | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265947 | PL100PT400B | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265948 | PL100PT401 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265949 | PL100PT402A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265950 | PL100PT402B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265951 | PL100PT404A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265952 | PL100PT404B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265953 | PL100PT404C | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265860 | PL100PV402 | 16" GLOBE VALVE, CLASS 300 TO RUWAIS SHWEIHAT GAS OIL PIPELINE | 16" GLOBE VALVE, CLASS 300 TO RUWAIS SHWEIHAT GAS OIL PIPELINE |  | CNTR_VLV | PL100CNTRVL | 3 | CNTR_VLV | 615101-310600 | SHWEIHAT TERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265954 | PL100PV402 | ACTUATOR FOR 16" GLOBE VALVE, CLASS 300 | 16" GLOBE VALVE, CLASS 300 TO RUWAIS SHWEIHAT GAS OIL PIPELINE | 969265860 | CNTR_VLV | PL100CNTRVL | 3 | CNTR_VLV | 615101-310600 | SHWEIHAT TERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265955 | PL100RTU001 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL100MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265957 | PL100TG400A | Temperature gauge | Temperature gauge |  | INDICATR | PL100MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265958 | PL100TG400B | Temperature gauge | Temperature gauge |  | INDICATR | PL100MISC | 3 | INDICATR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265959 | PL100TSV400 | THERMAL RELIEF VALVE, 3/4" 300# X 1" 150# RF, SET PR:31KG/CM2G | THERMAL RELIEF VALVE |  | PSV | PL100VALVE | 3 | PSV | 616101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265960 | PL100TSV400A | Thermal Reliefe Valve | Thermal Relief Valve |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265961 | PL100TSV400B | Thermal Reliefe Valve | Thermal Relief Valve |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132049 | MQ600XGH001 | GAS, HYDROGEN | HYDROGEN GAS DETECTOR IN BATTERY ROOM |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XGH001-MFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM02.M3
969132050 | MQ600XGH002 | GAS, HYDROGEN | HYDROGEN GAS DETECTOR IN BATTERY ROOM |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XGH002-MFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM02.M3
969132051 | MQ600XGH003 | GAS, HYDROGEN | HYDROGEN GAS DETECTOR IN BATTERY ROOM |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XGH003-MFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM02.M3
969132055 | MQ600XGC204 | GAS FLAMMABLE GAS DETECTOR | FLAMMABLE GAS DETECTOR SUMP TANK |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XGC204-MFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM02.M3
9527652 | M400V184 | WWTP STRIPPER VESSEL | STRIPPER VESSEL |  |  | M400WWTP | 2 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57049 | S14MOV114 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A DEGC, DATA N/A , MOTOR OPERATED VA | MOTOR OPERATED VALVE TO PIG LAUNCHER |  | MOV | S15R03 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57050 | S14MOV115 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A DEGC, DATA N/A , BY PASS MOV OF PI | BY PASS MOTOR OPERATED OF PIG LAUNCHER |  | MOV | S15R03 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57051 | S15MOV116 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , MOV AFTER PIG LAUNCHER , ROTORK | MOTOR OPERATED VALVE AFTER PIG LAUNCHER |  | MOV | S15R03 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57070 | S21MOV111 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE TO PIG LAUNCHER |  | MOV | S21R02 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269270 | M410BAV21243029 | 1.5" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe, UL/FM Approved | 1.5" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269271 | M410BAV21243045 | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269272 | M410BAV21243049 | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269254 | M410BD001C | 0.6kV Grade Bus Duc twith Necessary Accessories | 0.6KV GRADE BUS DUCT WITH NECESSARY ACCESSORIES, SUBSTATION BUILDING 410(MUSTAFFAH TERMINAL) |  | PACKAGE | M410MISC | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269255 | M410BD001D | 0.6kV Grade Bus Duc twith Necessary Accessories | 0.6KV GRADE BUS DUCT WITH NECESSARY ACCESSORIES, SUBSTATION BUILDING 410(MUSTAFFAH TERMINAL) |  | PACKAGE | M410MISC | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269256 | M410BAV21243018 | 0.75" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 0.75" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269269 | M410BAV21243003 | 1.5" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe | 1.5" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935655 | SMLPGTP10 | CP TEST POINT | TEST POINT # 10 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935656 | SMLPGTP11 | CP TEST POINT | TEST POINT # 11 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935657 | SMLPGTP12 | CP TEST POINT | TEST POINT # 12 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935671 | SMLPGTP26 | CP TEST POINT | TEST POINT # 26 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935672 | SMLPGTP27 | CP TEST POINT | TEST POINT # 27 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935673 | SMLPGTP28 | CP TEST POINT | TEST POINT # 28 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935686 | SMLPGTP41 | CP TEST POINT | TEST POINT # 41 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935687 | SMLPGTP42 | CP TEST POINT | TEST POINT # 42 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935688 | SMLPGTP43 | CP TEST POINT | TEST POINT # 43 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935561 | SALAINTP101 |  | TEST POINT # 101 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935562 | SALAINTP102 |  | TEST POINT # 102 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935563 | SALAINTP103 |  | TEST POINT # 103 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935578 | SADIATP9 |  | TEST POINT# 9 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935579 | SADIATP10 |  | TEST POINT# 10 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935580 | SADIATP11 |  | TEST POINT# 11 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935594 | SADIACP1IJ2 |  | INSULATING JOINT 2 AT KM 0.75 (A.D.INT'L AIRPORT) |  |  | SADIAPIPE | 1 | PIPING | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 5 | 1 | 1 | 5 | 3.0969 | Low | Low | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935596 | SADIACP1IJ3 |  | INSULATING JOINT 3 AT KM 0.76 (A.D.INT'L AIRPORT) |  |  | SADIAPIPE | 1 | PIPING | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 5 | 1 | 1 | 5 | 3.0969 | Low | Low | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935597 | SADIACP1IJ4 |  | INSULATING JOINT 4 AT KM 17 (A.D.INT'L AIRPORT) |  |  | SADIAPIPE | 1 | PIPING | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 5 | 1 | 1 | 5 | 3.0969 | Low | Low | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IDH57539 | M50XHD011 | DETECTOR, FIRE PROTECTION, HEAT , 24VDC , EXPLOSION PROOF , YES | LINEAR HEAT DETECTOR FOR TANK T-104 |  | FG_DET | M10T104 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XHD011-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 19/09/18 | MFPS-PM05.M3
IDH57544 | M50XHD012 | DETECTOR, FIRE PROTECTION, HEAT , 24VDC , EXPLOSION PROOF , YES | LINEAR HEAT DETECTOR FOR TANK T-105 |  | FG_DET | M10T105 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XHD012-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 24/09/18 | MFPS-PM05.M3
IDH57554 | M50XHD022 | DETECTOR, FIRE PROTECTION, HEAT , 24VDC , EXPLOSION PROOF , YES | LINEAR HEAT DETECTOR FOR TANK T-107 |  | FG_DET | M10T107 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XHD022-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 24/09/18 | MFPS-PM05.M3
969147438 | M410T031D | DIESEL DAY TANK (FIREWATER PUMP) | DIESEL DAY TANK (FIREWATER PUMP) |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147439 | M410T031E | DIESEL DAY TANK (FIREWATER PUMP) | DIESEL DAY TANK (FIREWATER PUMP) |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147440 | M410T031F | DIESEL DAY TANK (FIREWATER PUMP) | DIESEL DAY TANK (FIREWATER PUMP) |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147441 | M410T031G | DIESEL DAY TANK (FIREWATER PUMP) | DIESEL DAY TANK (FIREWATER PUMP) |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147443 | M410T051 | FIRE WATER STORAGE TANK | FIRE WATER STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 5 | 50 | 50 | 7.4949 | Low | Medium | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147444 | M410T052 | FIRE WATER STORAGE TANK | FIRE WATER STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 5 | 50 | 50 | 7.4949 | Low | Medium | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147446 | M410P007A | ULG 91/95 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-7-Y1
969147447 | M410P007B | ULG 91/95 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 11/11/18 | MM-PM-7-Y1
933029 | M400PV670 | VALVE, CONTROL, GLOBE RECIPROCATING , 12" , 900 , 87 , RF FLANGE , A216 GR WCC , | INLET OF RUWAIS-MUSSAFAH MP P/L FLOW METERING SKID | 938870 | CNTR_VLV | M400PIC670 | 3 | CNTR_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933030 | M400PV813 | VALVE, CONTROL, GLOBE RECIPROCATING , 6" X 4" , 300 LB , 6 , RF FLANGE , A216 GR | FROM ADIA MUSSAFAH JET A1 M/L PUMPS | 938871 | CNTR_VLV | M400PIC813 | 3 | CNTR_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933031 | M400PV894A | VALVE, CONTROL, GLOBE RECIPROCATING , 6" X 3" , 1500 LB , 87 , RTJ FLANGE , A216 | MUSSAFAH-AL AIN MP TIE IN MAIN LINE PUMP DISCHARGE | 938872 | CNTR_VLV | M400PIC894 | 3 | CNTR_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933032 | M400PV894B | VALVE, CONTROL, GLOBE RECIPROCATING , 6" , 1500 LB , 87 , RTJ FLANGE , A216 GR W | MUSSAFAH-AL AIN MP TIE IN MAIN LINE PUMP DISCHARGE | 938872 | CNTR_VLV | M400PIC894 | 3 | CNTR_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933042 | AT800PV105 | VALVE, CONTROL, GLOBE RECIPROCATING , 6" , 300 LB , 87 , RF FLANGE , A216 GR WCC | MUSSAFAH-ADIA JET A1 TO EXISTING ADIA STORAGE TANK | 938873 | CNTR_VLV | AT800PIC105 | 2 | CNTR_VLV | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933043 | PL300EOV30101 | VALVE, BALL, 10" , 600 LB , 60 , BW , ASTM A216 GR WCB , ELECTRO-HYDRAULIC ACTUA | SVS1 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB |  | VALVE | PL300SVS1 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30101-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 09/08/18 | MM-PM-014-M6
933044 | PL300EOV30102 | VALVE, BALL, 10" , 600 LB , 60 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS2 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB |  | VALVE | PL300SVS2 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30102-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/11/18 | MM-PM-014-M6
933045 | PL300EOV30103 | VALVE, BALL, 10" , 600 LB , 60 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS3 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB |  | VALVE | PL300SVS3 | 2 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 10 | 1 | 50 | 10 | 4.699 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | PL300EOV30103-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
933046 | PL300EOV30104 | VALVE, BALL, 10" , 600 LB , 60 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS4 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB |  | VALVE | PL300SVS4 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30104-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/11/18 | MM-PM-014-M6
933047 | PL300EOV30105 | VALVE, BALL, 10" , 600 LB , 60 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS5 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB |  | VALVE | PL300SVS5 | 2 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 10 | 1 | 50 | 10 | 4.699 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | PL300EOV30105-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
933048 | PL300EOV30106 | VALVE, BALL, 10" , 600 LB , 60 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS6 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB |  | VALVE | PL300SVS6 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30106-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
933049 | PL300EOV30107 | VALVE, BALL, 10" , 600 LB , 60 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS7 NAPHTHA / REFORMATE-HOV BALL TYPE,10"X600LB |  | VALVE | PL300SVS7 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30107-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
933050 | PL300EOV30211 | VALVE, BALL, 12" , 600 LB , 95 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS1 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB |  | VALVE | PL300SVS1 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30211-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 09/08/18 | MM-PM-014-M6
933051 | PL300EOV30212 | VALVE, BALL, 12" , 600 LB , 95 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS2 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB |  | VALVE | PL300SVS2 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30212-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/11/18 | MM-PM-014-M6
933052 | PL300EOV30213 | VALVE, BALL, 12" , 600 LB , 95 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS3 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB |  | VALVE | PL300SVS3 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30213-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
933053 | PL300EOV30214 | VALVE, BALL, 12" , 600 LB , 95 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS4 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB |  | VALVE | PL300SVS4 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30214-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/11/18 | MM-PM-014-M6
933054 | PL300EOV30215 | VALVE, BALL, 12" , 600 LB , 95 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS5 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB |  | VALVE | PL300SVS5 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30215-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
933055 | PL300EOV30216 | VALVE, BALL, 12" , 600 LB , 95 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS6 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB |  | VALVE | PL300SVS6 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30216-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
933056 | PL300EOV30217 | VALVE, BALL, 12" , 600 LB , 95 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (H | SVS7 STRAGHT RUN RESIDUE-HOV BALL TYPE,12"X600LB |  | VALVE | PL300SVS7 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30217-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
933057 | PL300EOV30301 | VALVE, BALL, 16" , 900LB , 45 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (HP | SVS1 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB |  | VALVE | PL300SVS1 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 | 12 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933058 | PL300EOV30322 | VALVE, BALL, 16" , 900LB , 45 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (HP | SVS2 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB |  | VALVE | PL300SVS2 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 1 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30322-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/11/18 | MM-PM-014-M6
933059 | PL300EOV30323 | VALVE, BALL, 16" , 900LB , 45 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (HP | SVS3 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB |  | VALVE | PL300SVS3 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 2 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30323-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
933060 | PL300EOV30324 | VALVE, BALL, 16" , 900LB , 45 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (HP | SVS4 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB |  | VALVE | PL300SVS4 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 3 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30324-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/11/18 | MM-PM-014-M6
933061 | PL300EOV30325 | VALVE, BALL, 16" , 900LB , 45 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (HP | SVS5 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB |  | VALVE | PL300SVS5 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 1 | 12 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30325-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/10/18 | MM-PM-014-M6
933062 | PL300EOV30306 | VALVE, BALL, 16" , 900LB , 45 , BW , ASTM A216 GR WCB , HYDRAULIC POWER UNIT (HP | SVS6 MULTI PRODUCT-HOV. BALL TYPE,16"X900LB |  | VALVE | PL300SVS6 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 1 | 12 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933063 | AA213LT147 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0 - 13600MM , 240VAC , 8" 150 LB | REC. STATION LEVEL TRANSMITTER GAS OIL TANK 13-T-01C |  | TRANS | AA13LEVEL | 4 | LVL_TX | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933064 | AA313LT149 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-13000 MM , 240VAC , 8" 150 LB R | AL AIN RECEIVING STATION LEVEL TRANSMITTER ULG95 TANK 13-T-02E |  | TRANS | AA13LEVEL | 4 | LVL_TX | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933065 | M400LT302 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MMMM , 240VAC , 8" 150 LB | LEVEL TRANSMITTER ULG95 TANK 400-T-111 | 939696 | TANKGAUG | M400LI302 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933066 | M400LT304 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER ULG95 TANK 400-T-112 | 939697 | TANKGAUG | M400LI304 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933067 | M400LT306 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER ULG95 TANK 400-T-113 | 939699 | TANKGAUG | M400LI306 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933068 | M400LT308 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER ULG95 TANK 400-T-114 | 939701 | TANKGAUG | M400LI308 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933069 | M400LT310 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER ULG95 TANK 400-T-115 | 939703 | TANKGAUG | M400LI310 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933070 | M400LT312 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER GAS OIL TANK 400-T-116 | 939706 | TANKGAUG | M400LI312 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933071 | M400LT314 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER JET A1 TANK 400-T-117 | 939708 | TANKGAUG | M400LI314 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933072 | M400LT316 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER JET A1 TANK 400-T-118 | 939710 | TANKGAUG | M400LI316 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933073 | M400LT318 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER JET A1 TANK 400-T-119 | 939712 | TANKGAUG | M400LI318 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933074 | M400LT320 | TRANSMITTER, LIQUID LEVEL, GUIDED WAVE RADAR , 0-17800 MM , 240VAC , 8" 150 LB R | LEVEL TRANSMITTER JET A1 TANK 400-T-120 | 939714 | TANKGAUG | M400LI320 | 3 | TANKGAUG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933526 | M400MOV313 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR T-107 INLET SHELL (ULG 98, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV313-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/02/19 | ME-PM-002-M6
969132746 | M400LSLL260 | SWITCH,LEVEL | LEVEL SWITCH OIL COLLECTING TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132611 | M400MP217A | MOTOR,ELECTRIC, FEED PUMP, IP68, 3.0 KW, 50 HZ, 415 V, 3, 8.5 AMP, F | MOTOR FOR FEED PUMP-A TO AC FILTER |  | MOTOR | M400P217A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP217A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 12/12/18 | ME-PM-014-M6
969132612 | M400MP217B | MOTOR,ELECTRIC, FEED PUMP, IP68, 3.0 KW, 50 HZ, 415 V, 3, 8.5 AMP, F | MOTOR FOR FEED PUMP-B TO AC FILTER |  | MOTOR | M400P217B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP217B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 13/12/18 | ME-PM-014-M6
969132613 | M400MP218A | MOTOR,ELECTRIC, OUTFLOW PUMP, IP68, 3.0 KW, 50 HZ, 415 V, 2760 RPM, 3, 8.5 AMP, F | MOTOR FOR OUTFLOW PUMP-A |  | MOTOR | M400P218A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP218A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 12/01/19 | ME-PM-014-M6
969132614 | M400MP218B | MOTOR,ELECTRIC, OUTFLOW PUMP B, IP68, 3.0 KW, 50 HZ, 415 V, 2760 RPM, 3, 8.5 AMP, F | MOTOR FOR OUTFLOW PUMP-B |  | MOTOR | M400P218B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP218B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 13/01/19 | ME-PM-014-M6
969132615 | M400MP212A | MOTOR,ELECTRIC, STAR, 0.37 KW, 1.19 AMP, 1390 RPM, 3, 415 V, 50 HZ, F, IP55, POLY ELECTROLYTE DOSING PUMP, S1 | MOTOR FOR POLYELECTROLYTE DOSING PUMP-A |  | MOTOR | M400P212A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP212A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 10/11/18 | ME-PM-014-M6
969132616 | M400MP212B | MOTOR,ELECTRIC, POLYELECTROLYTE DOSING PUMP, IP55, 0.37 KW, 50 HZ, 415 V, 1390 RPM, 3, 1.19 AMP, F | MOTOR FOR POLYELECTROLYTE DOSING PUMP-B |  | MOTOR | M400P212B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP212B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 11/11/18 | ME-PM-014-M6
969132617 | M400MP218A | PLEASE DELETE THIS ASSET NUMBER | MOTOR FOR OUTFLOW PUMP-A |  |  | M400P218A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP218A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 12/01/19 | ME-PM-014-M6
969132618 | M400MP209A | MOTOR,ELECTRIC, FEED PUMP A TO DAF, 1.10 KW, VARIABLE HZ, 415 V, 1445 RPM, 3, 2.98 AMP | MOTOR FOR FEED PUMP-A TO DAF |  | MOTOR | M400P209A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132619 | M400MP209B | MOTOR,ELECTRIC, FEED PUMP B TO DAF, 1.10 KW, VARIABLE HZ, 415 V, 1445 RPM, 3, 2.98 AMP | MOTOR FOR FEED PUMP-A TO DAF |  | MOTOR | M400P209B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132620 | M400MP210A | MOTOR,ELECTRIC, COAQUALATION DOSAGE PUMP A, 0.09 KW, 50 HZ, 415 V, 3, 0.22 AMP | MOTOR FOR COAQUALATION DOSING PUMP-A |  | MOTOR | M400P210A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP210A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/12/18 | ME-PM-014-M6
969132621 | M400MP210B | MOTOR,ELECTRIC, COAQUALATION DOSING PUMP B, 0.09 KW, 50 HZ, 415 V, 3, 0.22 AMP | MOTOR FOR COAQUALATION DOSING PUMP-B |  | MOTOR | M400P210B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP210B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/12/18 | ME-PM-014-M6
969271735 | M410STR005C | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278099 | M410ELP001 | DISTRIBUTION PANEL | Small Power Distribution Board | 969195256 | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410ELP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 12/01/19 | ME-PNL1-PM-M6
969271395 | M400MOV322 | MOV FOR OUTLET OF PPD TANK | MOV FOR OUTLET OF PPD TANK |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV322-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969271396 | M400MOV323 | LOWERING MOV ON LUBRICITY IMPROVER TANK 302. | LOWERING MOV ON LUBRICITY IMPROVER TANK 302. |  | MOV | M400T302 | 3 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV323-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/09/18 | ME-PM-002-M6
969271394 | M400MOV321 | MOV FOR INLET OF PPD TANK | MOV FOR INLET OF PPD TANK |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV321-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/09/18 | ME-PM-002-M6
969205446 | M410LS31A | Level switch | Level switch |  | LVL_SWT | M410P031A | 3 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205447 | M410LT31A | Level transmitter Fuel tank level | Level transmitter Fuel tank level |  | LVL_TX | M410T031A | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205273 | M410INS2308001 | FMM-1 MODULE | INERGEN GAS SYSTEM | 969175977 |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205274 | M410INS2308001 | KDM- R2 DISPLAY MODULE | INERGEN GAS SYSTEM | 969175977 |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205289 | M410FACP001 | COMMUNCIATION CARD ( MS-PANEL) | FIRE ALARM CONTROL PANEL IN THE SIS BUILDING. | 969195600 |  | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37123 | UTOYOTA52389 | 11 / 52389 - TOYOTA FORTUNER (SR. PIPELINE ENGINEER) | TOYOTA FORTUNER 11 / 52389 (SR. PIPELINE ENGINEER) |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA52389-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 02/08/18 | MM-PM-029-M1
VHC37125 | UTOYOTA57781 | 11 / 57781 - TOYOTA FORTUNER (SECURITY OFFICER, P & T DEPT.) | TOYOTA FORTUNER 11 / 57781 (SECURITY OFFICER, P & T DEPT.) |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA57781-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 14/08/18 | MM-PM-029-M1
969132622 | M400MP213A | MOTOR,ELECTRIC, RECIRCULATION PUMP-A, 4 KW, 50 HZ, 415 V, 2905 RPM, 3, 7.80 AMP | MOTOR FOR RECIRCULATION PUMP-A |  | MOTOR | M400P213A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP213A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/12/18 | ME-PM-014-M6
EMV57534 | M10MOV572 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-104 |  | MOV | M10T104 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57540 | M10MOV573 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-105 |  | MOV | M10T105 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV573-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57541 | M10MOV574 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-105 |  | MOV | M10T105 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV574-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57545 | M10MOV581 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-106 |  | MOV | M10T106 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV581-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57546 | M10MOV582 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-106 |  | MOV | M10T106 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV582-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57550 | M10MOV583 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-107 |  | MOV | M10T107 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV583-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
EMV57551 | M10MOV584 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-107 |  | MOV | M10T107 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV584-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
EMV57555 | M10MOV591 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-108 |  | MOV | M10T108 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV591-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57556 | M10MOV592 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-108 |  | MOV | M10T108 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV592-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57558 | M50MOV128 | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY FOR TANK T-108 , REM | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-108. |  | MOV | M10T108 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV128-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/09/18 | ME-PM-002-M6
EMV57561 | M10MOV601 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-109 |  | MOV | M10T109 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV601-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57562 | M10MOV602 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-109 |  | MOV | M10T109 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV602-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57564 | M50MOV129 | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY MOV FOR TANK T-109 , | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-109. |  | MOV | M10T109 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV129-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/10/18 | ME-PM-002-M6
EMV57567 | M10MOV603 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET OF TANK T110 MOTOR OPERATED VALVE. |  | MOV | M10T110 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV603-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57568 | M10MOV604 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-110 |  | MOV | M10T110 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV604-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57570 | M50MOV130 | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY MOV FOR TANK T-110 , | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-110 |  | MOV | M10T110 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV130-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/10/18 | ME-PM-002-M6
ERC57514 | M10CPR101 | CATHODIC PROTECTION, NO MODIFIER, C.P.RECTIFIER FOR TANK T-101 , 415/2500 VA KVA | C.P. RECTIFIER FOR TANK T-101 |  | CATHPRO | M10T101 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR101-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 18/11/18 | ME-PM-008-M6
ERC57521 | M10CPR102 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/2500VA KVA, ONAN , | C.P RECTIFIER FOR TANK T-102 |  | CATHPRO | M10T102 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR102-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/11/18 | ME-PM-008-M6
ERC57528 | M10CPR103 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/2500VA KVA, ONAN , | C.P RECTIFIER FOR TANK T-103 |  | CATHPRO | M10T103 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR103-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 09/12/18 | ME-PM-008-M6
ERC57535 | M10CPR104 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/1600VA KVA, ONAN , | C.P RECTIFIER FOR TANK T-104 |  | CATHPRO | M10T104 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR104-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 16/12/18 | ME-PM-008-M6
ERC57542 | M10CPR105 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/1600VA KVA, ONAN , | C.P RECTIFIER FOR TANK T-105 |  | CATHPRO | M10T105 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR105-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 07/01/19 | ME-PM-008-M6
ERC57547 | M10CPR106 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/1600VA KVA, ONAN , | C.P RECTIFIER FOR TANK T-106 |  | CATHPRO | M10T106 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR106-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 14/01/19 | ME-PM-008-M6
ERC57552 | M10CPR107 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/1600VA KVA, ONAN , | C.P RECTIFIER FOR TANK T-107 |  | CATHPRO | M10T107 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR107-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 11/08/18 | ME-PM-008-M6
ERC57557 | M10CPR108 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/675VA KVA, ONAN , H | C.P RECTIFIER FOR TANK T-108 |  | CATHPRO | M10T108 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR108-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 18/08/18 | ME-PM-008-M6
ERC57563 | M10CPR109 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/675VA KVA, ONAN , H | C.P RECTIFIER FOR TANK T-109 |  | CATHPRO | M10T109 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR109-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 08/09/18 | ME-PM-008-M6
ERC57569 | M10CPR110 | CATHODIC PROTECTION, NO MODIFIER, CATHODIC PROTECTION , 415V/675VA KVA, ONAN , H | C.P RECTIFIER FOR TANK T-110 |  | CATHPRO | M10T110 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M10CPR110-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/10/18 | ME-PM-008-M6
IIM59041 | M10QI012 | DETECTOR, LEVEL GAUGE , 4 TO 20 Ma | OIL/WATER INTERFACE DETECTOR FOR TANK T-101 | TNK56513 | TNK_GUG | M10T101 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59063 | M10QI022 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-102 | TNK56531 | TNK_GUG | M10T102 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59085 | M10QI032 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-103 | TNK56547 | TNK_GUG | M10T103 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59105 | M10QI042 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-104 | TNK56565 | TNK_GUG | M10T104 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59125 | M10QI052 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-105 | TNK56585 | TNK_GUG | M10T105 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59145 | M10QI062 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-106 | TNK56600 | TNK_GUG | M10T106 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59165 | M10QI072 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-107 | TNK56616 | TNK_GUG | M10T107 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59187 | M10QI082 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR KEROSINTANK T-108 | TNK56634 | TNK_GUG | M10T108 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59204 | M10QI092 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-109 | TNK56645 | TNK_GUG | M10T109 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIM59222 | M10QI102 | DETECTOR, LEVEL GAUGE , 4-20 MA | OIL/WATER INTERFACE DETECTOR FOR TANK T-110 | TNK56656 | TNK_GUG | M10T110 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 100 | 5 | 5 | 5 | 4.7959 | Low | Low | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132646 | M400FACP006 | PANEL,FIRE ALARM, TYCO | FIRE ALARM CONTROL PANEL AT EMERGENCY DIESEL GENERATOR CONTAINER. |  | F&G_PNL | M400EPB001 | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FACP006-MFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 13/08/18 | MFPS-PM01.M6
969132647 | M400XHE022 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 15-32VDC, IP43, YES | HEAT DETECTOR AT MUSAFFHA IRP-1 EMERGENCY DIESEL GENERATOR SET CONTAINER |  | FG_DET | M400FACP006 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132649 | M400XAL010 | ALARM, SOUNDER, 24VDC, AUDIBLE & VISUAL, RED | FLASHER WITH SOUNDER AT MTERMINAL IRP-1 EMERGENCY DIESEL GENERATOR CONTAINER |  | ALARMANC | M400FACP006 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132650 | M400XAL011 | ALARM, SOUNDER, 24VDC, AUDIBLE & VISUAL, RED | FLASHER WITH SOUNDER AT MTERMINAL IRP-1 EMERGENCY DIESEL GENERATOR SET CONTAINER |  | ALARMANC | M400FACP006 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132651 | M400XAS006 | HORN, SOUNDER, 24VDC, YES | SOUNDER AT MTERMINAL EMERGENCY DIESEL GENERATOR IRP-1 |  | LIGHT | M400FACP006 | 1 | LIGHT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132652 | M400XAS007 | HORN, SOUNDER, 24VDC, YES | SOUNDER AT M TERMINAL EMERGENCY DIESEL GENERATOR IRP-1 |  | LIGHT | M400FACP006 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132653 | M400XAS008 | HORN, SOUNDER, 24VDC, YES | SOUNDER AT M TERMINAL EMERGENCY DIESEL GENERATOR IRP-1 |  | LIGHT | M400FACP006 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132654 | M400XLF006 | LIGHT, BEACON, RED, 24VDC | BEACON(FLASHER)AT M TERMINAL EMERGENCY DIESEL GENERATOR CONTAINER IRP-1 |  | ALARMANC | M400FACP006 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132655 | M400XLF007 | LIGHT, BEACON, RED, 24VDC | BEACON(FLASHER)AT M TERMINAL IRP-1 EMERGENCY DIESEL GENERATOR SET CONTAINER |  | ALARMANC | M400FACP006 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132656 | M400XLF008 | LIGHT, BEACON, RED, 24VDC | BEACON(FLASHER)AT M TERMINAL IRP-1 EMERGENCY DIESEL GENERATOR IRP-1 |  | ALARMANC | M400FACP006 | 1 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132657 | M400XAC006 | CALL POINT, MANUAL GAS DISCHARGE PUSH BUTTON, IP42, YELLOW, YES | MANUAL CALL POINT AT MTERMINAL IRP-1 EMERGENCY DIESEL GENERATOR SET |  | PB_HS-MC | M400FACP006 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC006-MFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 11/08/18 | MFPS-PM07.M3
969132658 | M400XAC007 | CALL POINT, MANUAL GAS DISCHARGE PUSH BUTTON, IP42, YELLOW, YES | MANUAL CALL POINT AT MTERMINAL IRP-1 EMERGENCY DIESEL GENERATOR CONTAINER |  | PB_HS-MC | M400FACP006 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC007-MFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 12/08/18 | MFPS-PM07.M3
969132686 | UCHEVROLET69435 | 69435 CHEVROLET SILVERADO PICK-UP (RAPID INTERVENTION & RESCUE) | CHEVROLET SILVERADO PICK-UP 69435 (RAPID INTERVENTION & RESCUE) |  |  | MREDUNDANT | 4 | 0 | 648701-610920 | MTERMINAL | DECOMMISSIONED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | o | 0 | N | N |  | 0 | Y | UCHEVROLET69435UHE | INACTIVE | MECH | PM | EDS | 1 | MONTHS | 05/07/18 | MM-PM-029-M1
969271736 | M410STR006A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147427 | M410T016 | JET A1 STORAGE TANK | JET A1 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147428 | M410V003 | ULG/GAS OIL SUMP VESSEL | ULG/GAS OIL SUMP VESSEL |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 10 | 5 | 10 | 100 | 1 | 5.699 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147429 | M410V004 | JET A1 SUMP VESSEL | JET A1 SUMP VESSEL |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 10 | 5 | 10 | 100 | 1 | 5.699 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147430 | M410L004A | JET A1 INTER-TANK TRANSFER FILTER COALESCER 15 & 6 SEPERATORS | JET A1 INTER-TANK TRANSFER FILTER 15PCs. COALESCER |  | VESSEL | M410FILTER | 2 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147431 | M410L004B | JET A1 INTER-TANK TRANSFER FILTER COALESCER 15 & 6 SEPERATORS | JET A1 INTER-TANK TRANSFER FILTER COALESCER |  | VESSEL | M410FILTER | 2 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 1 | 5 | 10 | 5.0969 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147432 | M410L004C | JET A1 INTER-TANK TRANSFER FILTER COALESCER 15 & 6 SEPERATORS. | JET A1 INTER-TANK TRANSFER FILTER COALESCER |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 1 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132700 | M400ME017 | MOTOR,ELECTRIC, GEAR DRIVE MOTOR, 0.37 KW, 50 HZ, 415 V, 1500 RPM, 3, 1.95 AMP, 400-MCC-001 | WWTP GEAR DRIVE MOTOR OIL SEPERATOR CHAIN-I |  | MOTOR | M400WWTP | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400ME017-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 20/01/19 | ME-PM-014-M6
IIF58261 | S15XPI120 | SPHERE PASSAGE INDICATOR | SPHERE PASSAGE INDICATOR |  | INDICATR | S15R03 | 3 | INDICATR | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIF58262 | S15XXT120 | SPHERE PASSAGE INDICATOR TRANSMITTER | SPHERE PASSAGE INDICATOR TRANSMITTER | IIF58261 |  | S15XPI120 | 2 | TRANSMIT | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175277 | M410RO807 | WATER SPRAY FOR 410-T-010FROM 410-STR-807 TO 410-PG-807 | WATER SPRAY FOR 410-T-010FROM 410-STR-807 TO 410-PG-807 |  | ORIFICE | M410T010 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175346 | M410PG753 | WATER SPRAY FOR 410-T-015FROM 410-RO-753 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-753 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175347 | M410PG754 | WATER SPRAY FOR 410-T-015FROM 410-RO-754 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-754 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936409 | M400P203A | PUMP, CENTRIFUGAL, HORIZONTAL, OH2 , FIREWATER (JOCKEY) , FRESH WATER , 0.073 , | FIRE WATER PUMPS (JOCKEY) |  | PUCE | M400PUMP | 1 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P203A-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 02/12/18 | MC-PM-02-M6
936410 | M400P203B | PUMP, CENTRIFUGAL, HORIZONTAL, OH2 , FIREWATER (JOCKEY) , FRESH WATER , 0.073 , | FIRE WATER PUMPS (JOCKEY) |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P203B-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 02/12/18 | MC-PM-02-M6
936411 | M400P201A | ENGINE, DIESEL | FIRE WATER PUMPS-MAIN DIESEL DRIVEN | 936404 | ENGINE | M400PUMP | 1 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/05/19 | MC-PM-027-Y1
936412 | M400P201B | ENGINE, DIESEL | FIRE WATER PUMP (MAIN) | 936405 | ENGINE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/06/19 | MC-PM-027-Y1
936413 | M400P201C | ENGINE, DIESEL | FIRE WATER PUMP (MAIN) | 936406 | ENGINE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/07/19 | MC-PM-027-Y1
936414 | M400P201D | ENGINE, DIESEL | FIRE WATER PUMPS-MAIN DIESEL DRIVEN | 936407 | ENGINE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400P201D-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/08/18 | MC-PM-027-Y1
969270077 | M410NEP1 | #1 NEPTUNE 10K GPM SOURCE PUMP UNIT. BIG FLOW SYSTEM. | #1 NEPTUNE UNIT 10K GPM BIG FLOW SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175348 | M410PG755 | WATER SPRAY FOR 410-T-015FROM 410-RO-755 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-755 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175349 | M410PG756 | WATER SPRAY FOR 410-T-015FROM 410-RO-756 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-756 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175873 | M410TSV108 | JET A1 AL DHAFRA BOOSTER PUMPS(FUTURE) | JET A1 AL DHAFRA BOOSTER PUMPS(FUTURE) |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175874 | M410TSV109 | AL AIN BOOSTER PUMPS 410-P-001A/B | AL AIN BOOSTER PUMPS 410-P-001A/B |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175875 | M410TSV110 | ULG 95 TO TANKER LOADING PUMPS 410-P-XXX(FUTURE) | ULG 95 TO TANKER LOADING PUMPS 410-P-XXX(FUTURE) |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175876 | M410TSV111 | GAS OIL INTER-TANK TRANSFER BASKET FILTERS 410-L-007A/B INLET MANIFOLD | GAS OIL INTER-TANK TRANSFER BASKET FILTERS 410-L-007A/B INLET MANIFOLD |  | PUCE | M410VALVE | 1 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175877 | M410TSV112 | AL AIN BOOSTER PUMPS 410-P-001A/B | AL AIN BOOSTER PUMPS 410-P-001A/B |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175878 | M410TSV113 | ULG 91 TO TANKER LOADING PUMPS 410-P-XXX(FUTURE) | ULG 91 TO TANKER LOADING PUMPS 410-P-XXX(FUTURE) |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175879 | M410TSV114 | GAS OIL TANKS 410-T-009/010 | GAS OIL TANKS 410-T-009/010 |  | PSV | M410T009 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175880 | M410TSV115 | AL AIN BOOSTER PUMPS 410-P-003A/B | AL AIN BOOSTER PUMPS 410-P-003A/B |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175881 | M410TSV116 | GAS OIL TO TANKER LOADING PUMPS(FUTURE) | GAS OIL TO TANKER LOADING PUMPS(FUTURE) |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175882 | M410TSV120 | JET A1 INTER-TANK FILTER COALESCERS 410-L-004A/B/C OUTLET MANIFOLD | JET A1 INTER-TANK FILTER COALESCERS 410-L-004A/B/C OUTLET MANIFOLD |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Verty High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175883 | M410TSV150 | ULG GAS OIL SUMP PUMP 410-P-009 DISCHARGE HEADER | ULG GAS OIL SUMP PUMP 410-P-009 DISCHARGE HEADER |  | PUCE | M410P009 | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175884 | M410TSV151 | JET A1 SUMP PUMP 410-P-010 DISCHARGE HEADER | JET A1 SUMP PUMP 410-P-010 DISCHARGE HEADER |  | PUCE | M410P010 | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175885 | M410TSV200 | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175886 | M410TSV201 | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C SUCTION HEADER |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175887 | M410TSV202 | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008A/B DISCHARGE HEADER | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008A/B DISCHARGE HEADER |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175888 | M410TSV203 | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008A/B SUCTION HEADER | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008A/B SUCTION HEADER |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175889 | M410TSV204 | GAS OIL INTER-TANK TRANSFER BASKET FILTERS 410-L-007A/B OUTLET MANIFOLD | GAS OIL INTER-TANK TRANSFER BASKET FILTERS 410-L-007A/B OUTLET MANIFOLD |  | PUCE | M410VALVE | 1 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175890 | M410TSV250 | JET A1 INTER-TANK TRANSFER PUMPS 410-P-014A/B DISCHARGE HEADER | JET A1 INTER-TANK TRANSFER PUMPS 410-P-014A/B DISCHARGE HEADER |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175891 | M410TSV251 | JET A1 INTER-TANK TRANSFER PUMPS 410-P-014A/B SUCTION HEADER | JET A1 INTER-TANK TRANSFER PUMPS 410-P-014A/B SUCTION HEADER |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175892 | M410TSV252 | JET A1 INTER-TANK FILTER COALESCERS 410-L-004A/B/C OUTLET MANIFOLD | JET A1 INTER-TANK FILTER COALESCERS 410-L-004A/B/C OUTLET MANIFOLD |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175893 | M410SDV451A | BLOWDOWN OF 410-L-004A | BLOWDOWN OF 410-L-004A |  | CNTR_VLV | M410L004A | 1 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175894 | M410SDV451B | BLOWDOWN OF 410-L-004B | BLOWDOWN OF 410-L-004B |  | CNTR_VLV | M410L004B | 1 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175895 | M410SDV451C | BLOWDOWN OF 410-L-004C | BLOWDOWN OF 410-L-004C |  | CNTR_VLV | M410L004C | 1 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175896 | M410PV357 | From 410-P-031/032/033 TO 410-T-051/052 | From 410-P-031/032/033 TO 410-T-051/052 |  | CNTR_VLV | M410FIRE | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175897 | M410LV451A | BLOWNDOWN OF 410-L-004A | BLOWNDOWN OF 410-L-004A |  | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175898 | M410LV451B | BLOWNDOWN OF 410-L-004A | BLOWNDOWN OF 410-L-004A |  | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175899 | M410LV451C | BLOWNDOWN OF 410-L-004A | BLOWNDOWN OF 410-L-004A |  | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175900 | M410FV450A | OUTLET OF 410-L-004A | OUTLET OF 410-L-004A |  | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175901 | M410FV450B | OUTLET OF 410-L-004A | OUTLET OF 410-L-004A |  | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175902 | M410FV450C | OUTLET OF 410-L-004A | OUTLET OF 410-L-004A |  | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175903 | M410LT011 | ENRAF ULG 91 TANK 410-T-001 | ENRAF ULG 91 TANK 410-T-001 |  | LVL_TX | M410T001 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT011-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/12/18 | MC-PM067.M6
969175904 | M410LT021 | ENRAF ULG 91 TANK 410-T-002 | ENRAF ULG 91 TANK 410-T-002 |  | LVL_TX | M410T002 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT021-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/12/18 | MC-PM067.M6
969175905 | M410LT031 | ENRAF ULG 91 TANK 410-T-003 | ENRAF ULG 91 TANK 410-T-003 |  | LVL_TX | M410T003 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT031-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/12/18 | MC-PM067.M6
969175906 | M410LT041 | ENRAF ULG 91 TANK 410-T-004 | ENRAF ULG 91 TANK 410-T-004 |  | LVL_TX | M410T004 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT041-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/12/18 | MC-PM067.M6
969175907 | M410LT051 | ENRAF ULG 95 TANK 410-T-005 | ENRAF ULG 95 TANK 410-T-005 |  | LVL_TX | M410T005 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT051-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/12/18 | MC-PM067.M6
969175908 | M410LT061 | ENRAF ULG 95 TANK 410-T-006 | ENRAF ULG 95 TANK 410-T-006 |  | LVL_TX | M410T006 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT061-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/12/18 | MC-PM067.M6
969175909 | M410LT071 | ENRAF ULG 95 TANK 410-T-007 | ENRAF ULG 95 TANK 410-T-007 |  | LVL_TX | M410T007 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT071-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/12/18 | MC-PM067.M6
969175910 | M410LT081 | ENRAF ULG 95 TANK 410-T-008 | ENRAF ULG 95 TANK 410-T-008 |  | LVL_TX | M410T008 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT081-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/12/18 | MC-PM067.M6
969175911 | M410LT091 | ENRAF GAS OIL TANK 410-T-009 | ENRAF GAS OIL TANK 410-T-009 |  | LVL_TX | M410T009 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT091-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/12/18 | MC-PM067.M6
969175912 | M410LT101 | ENRAF GAS OIL TANK 410-T-010 | ENRAF GAS OIL TANK 410-T-010 |  | LVL_TX | M410T010 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT101-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/12/18 | MC-PM067.M6
969175913 | M410LT111 | ENRAF JET A1 TANK 410-T-011 | ENRAF JET A1 TANK 410-T-011 |  | LVL_TX | M410T011 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT111-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/12/18 | MC-PM067.M6
969175914 | M410LT121 | ENRAF JET A1 TANK 410-T-012 | ENRAF JET A1 TANK 410-T-012 |  | LVL_TX | M410T012 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT121-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/12/18 | MC-PM067.M6
969175915 | M410LT131 | ENRAF JET A1 TANK 410-T-013 | ENRAF JET A1 TANK 410-T-013 |  | LVL_TX | M410T013 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT131-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/12/18 | MC-PM067.M6
969175916 | M410LT141 | ENRAF JET A1 TANK 410-T-014 | ENRAF JET A1 TANK 410-T-014 |  | LVL_TX | M410T014 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT141-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 15/12/18 | MC-PM067.M6
969175917 | M410LT151 | ENRAF JET A1 TANK 410-T-015 | ENRAF JET A1 TANK 410-T-015 |  | LVL_TX | M410T015 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT151-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/12/18 | MC-PM067.M6
969175918 | M410LT161 | ENRAF JET A1 TANK 410-T-016 | ENRAF JET A1 TANK 410-T-016 |  | LVL_TX | M410T016 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M410LT161-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/12/18 | MC-PM067.M6
969175923 | M410LT023B | ULG 91 TANK 410-T-002 | SAAB ROSEMOUNT ULG 91 TANK 410-T-002 |  | LVL_TX | M410T002 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175924 | M410LT023C | ULG 91 TANK 410-T-002 | SAAB ROSEMOUNT ULG 91 TANK 410-T-002 |  | LVL_TX | M410T002 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175925 | M410LT033A | ULG 91 TANK 410-T-003 | SAAB ROSEMOUNT ULG 91 TANK 410-T-003 |  | LVL_TX | M410T003 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175926 | M410LT033B | ULG 91 TANK 410-T-003 | SAAB ROSEMOUNT ULG 91 TANK 410-T-003 |  | LVL_TX | M410T003 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37120 | UTOYOTA61986 | 6 / 61986 - TOYOTA LAND CRUISER (PIPELINE PATROLLING) | TOYOTA LAND CRUISER 6 / 61986 (PIPELINE PATROLLING) |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA61986-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 03/08/18 | MM-PM-029-M1
969282144 | M400MP851 | MOTOR,ELECTRIC | PUMP MOTOR FOR COLORIMETER ANALYZER MSFH-AAIN MLTI PROD TIE-IN. |  | ANALYSER | M400AT851 | 2 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400MP851-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 22/01/19 | ME-PM-LT1-6M
937387 | M400MP024B | MOTOR,ELECTRIC, SLOP TRANSFER, IP55, 37KW, 50HZ, 415V, IP55, M3GP225SMB 2V1, 6312M/C3, 6313M/C3, VERTCAL MOUNTING, 2965 RPM, 3, 61A, F, EExnAII T3 | MOTOR SLOP TRANSFER PUMP |  | MOTOR | M400P024B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP024B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
937388 | M400MP021C | MOTOR,ELECTRIC, ULG-95/98 INTER TANK TRANSFER, IP55, 55KW, 50HZ, 415V, S1, IP55, 280SMA4, 6316M/C3, 6316M/C3, VERTICAL MOUNTING, 1483 RPM, 3, STAR, 94A, F, EExnAII T3, 625 KG, T3 | VERTICAL MOTOR, ULG95/ULG98/ INTER TANK TRANSFER PUMP |  | MOTOR | M400P021C | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP021C-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 01/08/18 | ME-PM-014-M6
937389 | M400MP022A | MOTOR,ELECTRIC, GAS OIL INTER TANK TRANSFER, IP55, 75KW, 50HZ, 415V, IP 55, M3GP 280SMB 4B3, 6316M/C3, 6316M/C3, FOOT MOUNTING, 1484 RPM, 3, 127A, F, EExnAII T3 | MOTOR GAS OIL INTAKE TRANSFER PUMP |  | MOTOR | M400P022A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP022A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/12/18 | ME-PM-014-M6
937390 | M400MP022B | MOTOR,ELECTRIC, GAS OIL INTER TANK TRANSFER, IP55, 75KW, 50HZ, 415V, M3GP 280SMB 4B3, 6316M/C3, 6316M/C3, FOOT MOUNTING, 1484 RPM, 3, 127A, F, EExnAII T3 | MOTOR,ELECTRIC |  | MOTOR | M400P022B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP022B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
937391 | M400MP024A | MOTOR,ELECTRIC, SLOP TRANSFER, 37KW, 50HZ, 415V, IP55, M3GP 225SMB 2V1, 6312M/C3, 6313M/C3, VERTCAL MOUNTING, 2965 RPM, 3, 61A, F, EExnAII T3 | MOTOR,ELECTRIC |  | MOTOR | M400P024A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP024A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/12/18 | ME-PM-014-M6
969281273 | M410PSV001A | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410V006 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Non Critical | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275379 | PL312BAV21243009 | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275380 | PL312BAV21243010 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275381 | PL312BAV21243011 | 2" Ball Valve Long Pattern Reduced Bore, API 6D, Class 1500, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, API 6D, Class 1500, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275382 | PL312BAV21243012 | 0.75" Ball Valve Reduced Bore, ASME B16.34, Class 1500, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/Devlon V, Fire Safe | 0.75" Ball Valve Reduced Bore, ASME B16.34, Class 1500, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/Devlon V, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275383 | PL312BAV21243013 | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275384 | PL312BAV21243014 | 6" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275385 | PL312BAV21243015 | 10" S-100, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 10" S-100, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275386 | PL312BAV21243016 | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275387 | PL312BAV21243017 | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275388 | PL312BAV21243018 | 4" S-80, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275389 | PL312BAV21243019 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275390 | PL312BAV21243020 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275391 | PL312BAV21243021 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275392 | PL312BAV21243022 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275393 | PL312BAV21243023 | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269822 | M410JBEI741 | JUNCTION BOX FOR CORROSION INHIBITOR 410-ME-010 | JUNCTION BOX FOR CORROSION INHIBITOR 410-ME-010 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269823 | M410JBEI751 | JUNCTION BOX FOR ANTI-FREEZE INJECTION SYSTEM 410-ME-011 | JUNCTION BOX FOR ANTI-FREEZE INJECTION SYSTEM 410-ME-011 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269824 | M410LG921 | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269825 | M410LG047 | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410V006 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269826 | M410LG401A | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L001A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269827 | M410LG401B | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L001B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269828 | M410LG401C | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L001C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269829 | M410LG401D | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L001D | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269830 | M410LG403A | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L011A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269831 | M410LG403B | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L011B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269832 | M410LG400D | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L005D | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269833 | M410LG400E | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L005E | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269834 | M410LG400A | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L005A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269835 | M410LG400B | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L005B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269836 | M410LG400C | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410L005C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269837 | M410LG721 | LEVEL GAUGE | BLUE DYE LEVEL GAUGE |  | INDICATR | M410ME001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269838 | M410LG731 | LEVEL GAUGE | ANTI-STATIC LEVEL GAUGE |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269839 | M410LG741 | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410ME010 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269840 | M410LG761 | LEVEL GAUGE | LEVEL GAUGE |  | INDICATR | M410ME201 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269841 | M410LT400A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005A | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269842 | M410LT400B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005B | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269843 | M410LT400C | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005C | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269844 | M410LT400D | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005D | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269845 | M410LT400E | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005E | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269846 | M410LT401A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005A | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269847 | M410LT401B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005B | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269848 | M410LT401C | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005C | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269849 | M410LT401D | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005D | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269850 | M410LT401E | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L005E | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269851 | M410LT402A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001A | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269852 | M410LT402B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001B | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269853 | M410LT402C | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001C | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269854 | M410LT402D | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001D | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269855 | M410LT403A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001A | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269856 | M410LT403B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001B | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269857 | M410LT403C | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001C | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269858 | M410LT403D | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L001D | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269859 | M410LT406A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L011A | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269860 | M410LT406B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L011B | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269861 | M410LT407A | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L011A | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269862 | M410LT407B | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410L011B | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269863 | M410LT451 | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410T030 | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269864 | M410LT453 | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410T031 | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269865 | M410LT921 | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | M410SYS | 3 | POWER_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269866 | M410LT761 | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | LVL_TX | M410ME201 | 3 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269867 | M410XHD600A | LINEAR HEAT DETECTOR | LINEAR HEAT DETECTOR FOR TANK-011 |  | FGBHFD | M410T011 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269868 | M410P050AA | LUB OIL PUMP FOR 410P002A ALAIN. | LUB OIL PUMP FOR 410P002A ALAIN. |  | PUCEOH | M410P002A | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P050AA-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269869 | M410P050AB | LUB OIL PUMP FOR 410P002A ALAIN. | LUB OIL PUMP FOR 410P002A ALAIN. |  | PUCEOH | M410P002A | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P050AB-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269870 | M410P051AA | LUB OIL PUMP FOR 410-P-004A PUMP | LUBE OIL PUMP FOR 410-P-004A PUMP |  | PUCEOH | M410P004A | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P051AA-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269871 | M410P051AB | LUB OIL PUMP FOR 410-P-004A PUMP | LUBE OIL PUMP FOR 410-P-004A PUMP |  | PUCEOH | M410P004A | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P051AB-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269872 | M410PT753A | LUBE OIL PRESSURE TRANSMITTER | LUBE OIL PRESSURE TRANSMITTER |  | PRES_TX | M410K001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT753A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269873 | M410PT753B | LUBE OIL PRESSURE TRANSMITTER | LUBE OIL PRESSURE TRANSMITTER |  | PRES_TX | M410K001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT753B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269874 | M410PT754A | LUBE OIL PRESSURE TRANSMITTER | LUBE OIL PRESSURE TRANSMITTER |  | PRES_TX | M410K001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT754A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269875 | M410PT754B | LUBE OIL PRESSURE TRANSMITTER | LUBE OIL PRESSURE TRANSMITTER |  | PRES_TX | M410K001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT754B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269876 | M410TT755A | Main Motor Bearing (Front) Temperature Transmitter | Main Motor Bearing (Front) Temperature Transmitter |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269877 | M410TT755B | Main Motor Bearing (Front) Temperature Transmitter | Main Motor Bearing (Front) Temperature Transmitter |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269878 | M410VT751A | MAIN MOTOR VIBRATION SENSOR(DE) WITH TRANSMITTER | MAIN MOTOR VIBRATION SENSOR(DE) WITH TRANSMITTER |  | VIBRMON | M410K001A | 2 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269879 | M410VT751B | MAIN MOTOR VIBRATION SENSOR(DE) WITH TRANSMITTER | MAIN MOTOR VIBRATION SENSOR(DE) WITH TRANSMITTER |  | VIBRMON | M410K001B | 2 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269880 | M410VT752A | MAIN MOTOR VIBRATION SENSOR(NDE) WITH TRANSMITTER | MAIN MOTOR VIBRATION SENSOR(NDE) WITH TRANSMITTER |  | VIBRMON | M410K001A | 2 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269881 | M410VT752B | MAIN MOTOR VIBRATION SENSOR(NDE) WITH TRANSMITTER | MAIN MOTOR VIBRATION SENSOR(NDE) WITH TRANSMITTER |  | VIBRMON | M410K001B | 2 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269882 | M410CMS001 | MARSHALLING CABINET FOR CORROSION MONITORINGSYSTEM | MARSHALLING CABINET FOR CORROSION MONITORINGSYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269884 | M410FY203A | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 |  | FL_MTR | M410FT203 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269885 | M410FY203B | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 |  | FL_MTR | M410FT203 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269886 | M410FY206A | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 |  | FL_MTR | M410FT206 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269887 | M410FY206B | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-001 |  | FL_MTR | M410FT206 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269888 | M410FY400A | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 |  | FL_MTR | M410FT400 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269889 | M410FY400B | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 |  | FL_MTR | M410FT400 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269890 | M410FY400C | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 |  | FL_MTR | M410FT400 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269891 | M410FY401A | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 |  | FL_MTR | M410FT401 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269892 | M410FY401B | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 |  | FL_MTR | M410FT402 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269893 | M410FY401C | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 | FLOW COMPUTER OMNI6000 FOR CUSTODY TRANSFER METERING SYSTEM 410-FMS-003 |  | FL_MTR | M410FT403 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269894 | M410FT761 | MASS FLOW METER YOKOGAWA 410FT761. | FLOW TX ANTI STATIC MASS FLOW METER |  | FL_MTR | M410ME201 | 3 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269895 | M410MMC001 | MCM MARSHALING CABINET, MUSSAFAH DEPOT TERMINAL RACK 01,02 | MCM MARSHALING CABINET, MUSSAFAH DEPOT TERMINAL RACK 01,02 |  | PACKAGE | M410PCH | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269896 | M410MMC002 | MCM MARSHALING CABINET, MUSSAFAH DEPOT TERMINAL RACK 03,04 | MCM MARSHALING CABINET, MUSSAFAH DEPOT TERMINAL RACK 03,04 |  | PACKAGE | M410PCH | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269897 | M410MMC003 | MCM MARSHALING CABINET, MUSSAFAH DEPOT TERMINAL RACK 05,06,07 | MCM MARSHALING CABINET, MUSSAFAH DEPOT TERMINAL RACK 05,06,07 |  | PACKAGE | M410PCH | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269898 | M410MCM003 | MCM SYSTEM CABINET, MUSSAFAH DEPOT TERMINAL RACK 01,02 | MCM SYSTEM CABINET, MUSSAFAH DEPOT TERMINAL RACK 01,02 |  | PACKAGE | M410PCH | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269899 | M410MCM004 | MCM SYSTEM CABINET, MUSSAFAH DEPOT TERMINAL RACK 03,04 | MCM SYSTEM CABINET, MUSSAFAH DEPOT TERMINAL RACK 03,04 |  | PACKAGE | M410PCH | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269900 | M410MCM005 | MCM SYSTEM CABINET, MUSSAFAH DEPOT TERMINAL RACK 05,06,07 | MCM SYSTEM CABINET, MUSSAFAH DEPOT TERMINAL RACK 05,06,07 |  | PACKAGE | M410PCH | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269901 | M410P003A | MECHANICAL SEAL | AL AIN GAS OIL BOOSTER PUMP | 969269204 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269902 | M410P003B | MECHANICAL SEAL | AL AIN GAS OIL BOOSTER PUMP | 969269205 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269903 | M410P023A | MECHANICAL SEAL | AL DHAFRA JP-8 BOOSTER PUMP. | 969269206 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269904 | M410P023B | MECHANICAL SEAL | AL DHAFRA JP-8 BOOSTER PUMP. | 969269207 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269905 | M410P023C | MECHANICAL SEAL | AL DHAFRA JP-8 BOOSTER PUMP. | 969269208 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269906 | M410P040A | MECHANICAL SEAL | ANTI FREEZE CHEMICAL OFFLOADING PUMP-A | 969269209 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P040A-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269907 | M410P040B | MECHANICAL SEAL | ANTI FREEZE CHEMICAL OFFLOADING PUMP-B | 969269210 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P040B-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269908 | M410P001A | MECHANICAL SEAL | AL AIN ULG BOOSTER PUMP | 969269211 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269909 | M410P001B | MECHANICAL SEAL | AL AIN ULG BOOSTER PUMP | 969269212 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281638 | M410PG656 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281639 | M410PG661 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281640 | M410PG662 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269301 | M410BAV21243023 | 2" S-80, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" S-80, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269273 | M410BAV21243027 | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269274 | M410BAV21243052 | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 10" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269276 | M410BAV21243025 | 12" Ball Valve Long Pattern Full Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 12" Ball Valve Long Pattern Full Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269277 | M410BAV21243034 | 12" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 12" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269278 | M410BAV21243007 | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 12" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269293 | M410BAV21243047 | 2" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269294 | M410BAV21243032 | 2" Ball Valve Long Pattern Reduced Bore, API 6D, Class 1500, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, API 6D, Class 1500, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269295 | M410BAV21243044 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269296 | M410BAV21243039 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A351 Grade CF3M, Trim 316LSS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A351 Grade CF3M, Trim 316LSS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269297 | M410BAV21243013 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269298 | M410BAV21243064 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A351 Grade CF3M, Trim 316LSS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A351 Grade CF3M, Trim 316LSS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269299 | M410BAV21243026 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269302 | M410BAV21243020 | 20" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 20" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269303 | M410BAV21243021 | 28" Ball Valve Long Pattern Reduced Bore, API 6D, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.47 Series A, Fire Safe | 28" Ball Valve Long Pattern Reduced Bore, API 6D, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.47 Series A, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269304 | M410BAV21243022 | 28" Ball Valve Long Pattern Reduced Bore, API 6D, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.47 Series A, Fire Safe | 28" Ball Valve Long Pattern Reduced Bore, API 6D, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.47 Series A, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269306 | M410PT752B | 2ND DISCH PRESSURE TRANSMITTER | 2ND DISCH PRESSURE TRANSMITTER |  | PRES_TX | M410K001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT752B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269307 | M410D092A | 2nd DRAIN SEPARATOR FOR COMPRESSOR | 2nd DRAIN SEPARATOR FOR COMPRESSOR |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269308 | M410D092B | 2nd DRAIN SEPARATOR FOR COMPRESSOR | 2nd DRAIN SEPARATOR FOR COMPRESSOR |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269309 | M410VH092A | 2nd SILENCER FOR COMPRESSOR | 2nd SILENCER FOR COMPRESSOR |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269310 | M410VH092B | 2nd SILENCER FOR COMPRESSOR | 2nd SILENCER FOR COMPRESSOR |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269311 | M410K092A | 2ND STAGE OF COMPRESSOR FOR 410-K-001A AIR COMPRESSOR UNIT | 2ND STAGE OF COMPRESSOR FOR 410-K-001A AIR COMPRESSOR UNIT |  | COMPRS | M410K001A | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269312 | M410K092B | 2ND STAGE OF COMPRESSOR FOR 410-K-001B AIR COMPRESSOR UNIT | 2ND STAGE OF COMPRESSOR FOR 410-K-001B AIR COMPRESSOR UNIT |  | COMPRS | M410K001B | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269313 | M410PT751A | 2ND SUCTION PRESSURE TRANSMITTER | 2ND SUCTION PRESSURE TRANSMITTER |  | PRES_TX | M410K001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT751A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269314 | M410PT751B | 2ND SUCTION PRESSURE TRANSMITTER | 2ND SUCTION PRESSURE TRANSMITTER |  | PRES_TX | M410K001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT751B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269315 | M410BAV21243054 | 3" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 3" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269316 | M410BAV21243016 | 3" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 3" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269317 | M410BAV21243056 | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269318 | M410XV751A | 3Way Solenoid Valve (for Load / Unload) | 3Way Solenoid Valve (for Load / Unload) |  | SOL_VLV | M410K001A | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Non Critical | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269319 | M410XV751B | 3Way Solenoid Valve (for Load / Unload) | 3Way Solenoid Valve (for Load / Unload) |  | SOL_VLV | M410K001B | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Non Critical | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269320 | M410BAV21243055 | 4" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269321 | M410BAV21243017 | 4" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269322 | M410BAV21243035 | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269323 | M410BAV21243057 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269324 | M410BAV21243030 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269325 | M410BAV21243040 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A351 Grade CF3M, Trim 316LSS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A351 Grade CF3M, Trim 316LSS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269326 | M410BAV21243014 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269327 | M410BAV21243028 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269328 | M410BAV21243053 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269329 | M410BAV21243024 | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269330 | M410BAV21243042 | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269331 | M410BAV21243038 | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269332 | M410BAV21243041 | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269333 | M410BAV21243043 | 4" S-80, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269334 | M410PC002 | 415V SWITCH GEAR-2 | 415V SWITCH GEAR-2 |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269335 | M410TOLPOD | POD CONTAINER UNIT FOR LOOSE TOOLS & EQUIPMENT, BIG FLOW SYSTEM. | OPEN PARTS STORAGE POD, BIG FLOW FIRE FIGHTING SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 1 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269336 | M410FFE2101308 | 6 kg BC DCP Fire Extinguisher (Indoor) | 6 kg BC DCP Fire Extinguisher (Indoor) |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269337 | M410BAV21243048 | 6" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Full Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269338 | M410BAV21243036 | 6" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269339 | M410BAV21243031 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132036 | PL300BATT003B | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-B =38 Nos FOR SV-3. |  | BATTERY | PL300BAT003 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935606 | SMTP7 |  | TEST POINT# 7 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935607 | SMTP8 |  | TEST POINT# 8 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935608 | SMTP9 |  | TEST POINT# 9 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935474 | SALAINTP26 |  | TEST POINT # 26 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935475 | SALAINTP27 |  | TEST POINT # 27 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935476 | SALAINTP28 |  | TEST POINT # 28 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132602 | M400MP208A | MOTOR,ELECTRIC, 3 KW, 50 HZ, 415 V | WTP MOTOR FOR FEED PUMP A-CHAIN I |  | MOTOR | M400P208A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP208A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 01/11/18 | ME-PM-012-M6
969132603 | M400MP208B | MOTOR,ELECTRIC, 3 KW, 50 HZ, 415 V, S1 | MOTOR FOR FEED PUMP A-CHAIN I |  | MOTOR | M400P208B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP208B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 02/11/18 | ME-PM-012-M6
969132609 | M400MP211A | MOTOR,ELECTRIC, CAUSTIC SODA PUMP, 0.09 KW, 50 HZ, 415 V, S1, 1365 RPM, 3, STAR, 0.37 AMP, F | MOTOR FOR CAUSTIC SODA DOSING PUMP-A |  | MOTOR | M400P211A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP211A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
969132610 | M400MP211B | MOTOR,ELECTRIC, CAUSTIC SODA DOSING PUMP, 0.09 KW, 50 HZ, 415 V, S1, 1365 RPM, 3, STAR, 0.37 AMP | MOTOR FOR CAUSTIC SODA DOSING PUMP-B |  | MOTOR | M400P211B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP211B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
969132623 | M400MP213B | MOTOR,ELECTRIC, RECIRCULATION PUMP-B, 4.0 KW, 50 HZ, 415 V, 2905 RPM, 3, 7.80 AMP | MOTOR FOR RECIRCULATION PUMP-B |  | MOTOR | M400P213B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP213B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 08/12/18 | ME-PM-014-M6
969132624 | M400MP214A | MOTOR,ELECTRIC, FEED PUMP-A CHAIN II, 3.0 KW, 50 HZ, 415 V, 2800 RPM, 3, 3.0 AMP | MOTOR FOR FEED PUMP A-CHAIN II |  | MOTOR | M400P214A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP214A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 01/12/18 | ME-PM-012-M6
969132625 | M400MP214B | MOTOR,ELECTRIC, FEED PUMP-B CHAIN II, 3.0 KW, 50 HZ, 415 V, 2800 RPM, 3, 7.80 AMP | MOTOR FOR FEED PUMP B-CHAIN II |  | MOTOR | M400P214B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP214B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 02/12/18 | ME-PM-012-M6
969132626 | M400MP215A | MOTOR,ELECTRIC, EVACUATION PUMP-A, 0.55 KW, 50 HZ, 415 V, 1375 RPM, 3, 1.52 AMP | MOTOR FOR EVACUATION PUMP-A |  | MOTOR | M400P215A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP215A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 10/01/19 | ME-PM-014-M6
969132627 | M400MP215B | MOTOR,ELECTRIC, EVACUATION PUMP-B, 0.55 KW, 50 HZ, 415 V, 1375 RPM, 3, 1.52 AMP | MOTOR FOR EVACUATION PUMP-B |  | MOTOR | M400P215B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP215B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 11/01/19 | ME-PM-014-M6
969132040 | PL300BATT005B | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-B =38 Nos FOR SV-5. |  | BATTERY | PL300BAT005 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132041 | PL300BATT006A | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-A =38 Nos FOR SV-6. |  | BATTERY | PL300BAT006 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132042 | PL300BATT006B | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V | BATTERY BANK-B =38 Nos FOR SV-6. |  | BATTERY | PL300BAT006 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGL56050 | S15R03 | PIG, LAUNCHER, VT-15503-31120 , ID :400 X 300 MM : LENGTH 4300 X 1500 MM , ANS | PIG LAUNCHER FOR MULTI PRODUCT PIPELINE. |  |  | S-PIG-LAUNCHERS | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGL56063 | S21R02 | PIG, LAUNCHER | PIG LAUNCHER FOR JET A1 PIPELINE. |  |  | S-PIG-LAUNCHERS | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGL56064 | U5101R01 | PIG, LAUNCHER | PIG LAUNCHER FOR LPG PIPELINE. |  |  | S-PIG-LAUNCHERS | 2 | PIPING | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 10 | 10 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGR56196 | M15R04 | RECEIVER, PIG, 14" , 600 LB | PIG RECEIVER AT MTF FOR MULTI PRODUCT PIPELINE |  |  | SMLPGPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGR56198 | M5101R02 | RECEIVER, PIG | PIG RECEIVER AT MTF FOR LPG BOTTLING PLANT |  |  | SMLPGPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD99111 | U51PLL146 | SYSTEM, PRESSURE ALARM AND ESD SHUTDOW, LPG , 20.6 BAR , 17.46 BAR , 20 TO 22 DE | LPG PIPELINE INLET PRESS. LOW LOW |  | EMERSDD | U5101R01 | 1 | EMERSDD | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935458 | SALAINTP13 |  | TEST POINT # 13 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935459 | SALAINTP14 |  | TEST POINT # 14 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935460 | SALAINTP15 |  | TEST POINT # 15 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131511 | M400XSP086 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131516 | M400XSP091 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131517 | M400XSP092 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131518 | M400XSP093 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131519 | M400XSP094 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131520 | M400XSP095 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131521 | M400XSP096 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR FOR HVAC ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131523 | M400XSP098 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR FOR OFFICE ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131524 | M400XSP099 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SUB STATION HVAC AIR INTAKE DUCT |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131527 | M400XSP105 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN DOCUMENT ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131591 | M400XHE006 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR FOR 400-NER-001A IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131601 | M400XHE016 | DETECTOR,FIRE PROTECTION, FIXED TEMPERATURE, 24VDC, YES | HEAT DETECTOR AT TRANSFORMER M400-TML001B IN SUB STATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131623 | M400XAC005 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT BATTERY ROOM-PLCR |  | PB_HS-MC | M400FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC005-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 25/09/18 | MFPS-PM07.M3
969131633 | M400XAC023 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT ADMINISTRATION BUILDING |  | PB_HS-MC | M400FACP004 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC023-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969131532 | M400XSP110 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN PRAYER ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131533 | M400XSP111 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN PRAYER ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131534 | M400XSP112 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN HVAC ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131536 | M400XSP114 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN STAFF ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131537 | M400XSP115 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN MANAGER ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131538 | M400XSP117 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN SENIOR MANAGER ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131543 | M400XSP122 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN TOILET OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131544 | M400XSP123 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CORRIDOR OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131545 | M400XSP124 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CORRIDOR OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131547 | M400XSP126 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN HVAC AIR INTAKE DUCT OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131628 | M400XAC014 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT SUB STATION BUILDING |  | PB_HS-MC | M400FACP002 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC014-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 21/10/18 | MFPS-PM07.M3
969131629 | M400XAC015 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT SUB STATION BUILDING |  | PB_HS-MC | M400FACP002 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC015-UFPS | INACTIVE | ELEC | PM | FT | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131630 | M400XAC020 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT OUTSIDE EASTERN LOBBY OF ADMINISTRATION BUILDING |  | PB_HS-MC | M400FACP004 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC020-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969131631 | M400XAC021 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT OUTSIDE NORTHERN LOBBY OF ADMINISTRATION BUILDING |  | PB_HS-MC | M400FACP004 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XAC021-UFPS | ACTIVE | ELEC | PM | FT | 3 | MONTHS | 22/10/18 | MFPS-PM07.M3
969132628 | M400MP216A | MOTOR,ELECTRIC, FEED PUMP-A TO STRIPPER, 0.55 KW, VARIABLE HZ, 415 V, 1375 RPM, 3, 1.52 AMP | MOTOR FOR FEED PUMP-A TO STRIPPER |  | MOTOR | M400P216A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP216A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 15/11/18 | ME-PM-014-M6
969132629 | M400MP216B | MOTOR,ELECTRIC, FEED PUMP-B TO STRIPPER, 0.50 KW, VARIABLE HZ, 415 V, 1375 RPM, 3, 1.52 AMP | MOTOR FOR FEED PUMP-B TO STRIPPER |  | MOTOR | M400P216B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP216B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 16/11/18 | ME-PM-014-M6
IIT59020 | M10TE301 | THERMOCOUPLE, RESISTANCE , 6MM OD , 316 SS , 1/2" MNPT | RTD FOR MULTI PRODUCT INLET METERING SKID | IIF59016 | TEMP_ELE | M10FQRAL301 | 2 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195291 | M410LP022 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP022-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 29/12/18 | ME-PNL1-PM-M6
969195292 | M410LP023 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP023-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 30/12/18 | ME-PNL1-PM-M6
969195293 | M410LP024 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP024-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 02/11/18 | ME-PNL1-PM-M6
969195294 | M410LP031 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP031-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 12/01/19 | ME-PNL1-PM-M6
969195295 | M410LP032 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP032-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 02/11/18 | ME-PNL1-PM-M6
969195296 | M410LP033 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP033-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 12/01/19 | ME-PNL1-PM-M6
969195297 | M410LCS007A | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195298 | M410LCS007B | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195299 | M410LCS007C | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195300 | M410LCS008A | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195301 | M410LCS008B | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195302 | M410LCS009 | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195303 | M410LCS010 | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195304 | M410LCS014A | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195305 | M410LCS014B | Local Motor Control Station | Local Motor Control Station |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195306 | M410SP011 | SOCKET OUTLET PANEL | SOCKET OUTLET PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410SP011-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 06/11/18 | ME-PNL1-PM-M6
969195307 | M410SP012 | SOCKET OUTLET PANEL | SOCKET OUTLET PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410SP012-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 07/11/18 | ME-PNL1-PM-M6
969195308 | M410SP041 | SOCKET OUTLET PANEL | SOCKET OUTLET PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410SP041-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 08/11/18 | ME-PNL1-PM-M6
969195309 | M410SP051 | SOCKET OUTLET PANEL | SOCKET OUTLET PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410SP051-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 09/11/18 | ME-PNL1-PM-M6
969195310 | M410FV450A | Control Valve Globe Actuator | OUTLET OF 410-L-004A | 969175900 | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195311 | M410FV450B | Control Valve Globe Actuator | OUTLET OF 410-L-004A | 969175901 | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195312 | M410FV450C | Control Valve Globe Actuator | OUTLET OF 410-L-004A | 969175902 | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195313 | M410LV451A | Control Valve Globe Actuator | BLOWNDOWN OF 410-L-004A | 969175897 | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195314 | M410LV451B | Control Valve Globe Actuator | BLOWNDOWN OF 410-L-004A | 969175898 | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195315 | M410LV451C | Control Valve Globe Actuator | BLOWNDOWN OF 410-L-004A | 969175899 | CNTR_VLV | M410L004A | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195316 | M410PV357 | Control Valve Actuator | From 410-P-031/032/033 TO 410-T-051/052 | 969175896 | CNTR_VLV | M410FIRE | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195317 | M410BAV2351001 | 1" FBV SS316 150#, RF, LEVER OPERATED | 1" FBV SS316 150#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195318 | M410BAV2351002 | 2" FBV SS316 150#, RF, LEVER OPERATED | 2" FBV SS316 150#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195319 | M410BAV2351003 | 3" FBV SS316 150#, RF, LEVER OPERATED | 3" FBV SS316 150#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195320 | M410BAV2351004 | 4" FBV SS316 150#, RF, LEVER OPERATED | 4" FBV SS316 150#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195321 | M410BAV2351005 | 6" FBV SS316 150#, RF, LEVER OPERATED | 6" FBV SS316 150#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175208 | M410RO738 | WATER SPRAY FOR 410-T-013FROM 410-STR-738 TO 410-PG-738 | WATER SPRAY FOR 410-T-013FROM 410-STR-738 TO 410-PG-738 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175209 | M410RO739 | WATER SPRAY FOR 410-T-013FROM 410-STR-739 TO 410-PG-739 | WATER SPRAY FOR 410-T-013FROM 410-STR-739 TO 410-PG-739 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175210 | M410RO740 | WATER SPRAY FOR 410-T-013FROM 410-STR-740 TO 410-PG-740 | WATER SPRAY FOR 410-T-013FROM 410-STR-740 TO 410-PG-740 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175211 | M410RO741 | WATER SPRAY FOR 410-T-013FROM 410-STR-741 TO 410-PG-741 | WATER SPRAY FOR 410-T-013FROM 410-STR-741 TO 410-PG-741 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175212 | M410RO742 | WATER SPRAY FOR 410-T-013FROM 410-STR-742 TO 410-PG-742 | WATER SPRAY FOR 410-T-013FROM 410-STR-742 TO 410-PG-742 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175213 | M410RO743 | WATER SPRAY FOR 410-T-013FROM 410-STR-743 TO 410-PG-743 | WATER SPRAY FOR 410-T-013FROM 410-STR-743 TO 410-PG-743 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175214 | M410RO744 | WATER SPRAY FOR 410-T-014FROM 410-STR-744 TO 410-PG-744 | WATER SPRAY FOR 410-T-014FROM 410-STR-744 TO 410-PG-744 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175215 | M410RO745 | WATER SPRAY FOR 410-T-014FROM 410-STR-745 TO 410-PG-745 | WATER SPRAY FOR 410-T-014FROM 410-STR-745 TO 410-PG-745 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175216 | M410RO746 | WATER SPRAY FOR 410-T-014FROM 410-STR-746 TO 410-PG-746 | WATER SPRAY FOR 410-T-014FROM 410-STR-746 TO 410-PG-746 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175217 | M410RO747 | WATER SPRAY FOR 410-T-014FROM 410-STR-747 TO 410-PG-747 | WATER SPRAY FOR 410-T-014FROM 410-STR-747 TO 410-PG-747 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175218 | M410RO748 | WATER SPRAY FOR 410-T-014FROM 410-STR-748 TO 410-PG-748 | WATER SPRAY FOR 410-T-014FROM 410-STR-748 TO 410-PG-748 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175219 | M410RO749 | WATER SPRAY FOR 410-T-014FROM 410-STR-749 TO 410-PG-749 | WATER SPRAY FOR 410-T-014FROM 410-STR-749 TO 410-PG-749 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175220 | M410RO750 | WATER SPRAY FOR 410-T-014FROM 410-STR-750 TO 410-PG-750 | WATER SPRAY FOR 410-T-014FROM 410-STR-750 TO 410-PG-750 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175221 | M410RO751 | WATER SPRAY FOR 410-T-014FROM 410-STR-751 TO 410-PG-751 | WATER SPRAY FOR 410-T-014FROM 410-STR-751 TO 410-PG-751 |  | ORIFICE | M410T014 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175222 | M410RO752 | WATER SPRAY FOR 410-T-015FROM 410-STR-752 TO 410-PG-752 | WATER SPRAY FOR 410-T-015FROM 410-STR-752 TO 410-PG-752 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175223 | M410RO753 | WATER SPRAY FOR 410-T-015FROM 410-STR-753 TO 410-PG-753 | WATER SPRAY FOR 410-T-015FROM 410-STR-753 TO 410-PG-753 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175224 | M410RO754 | WATER SPRAY FOR 410-T-015FROM 410-STR-754 TO 410-PG-754 | WATER SPRAY FOR 410-T-015FROM 410-STR-754 TO 410-PG-754 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175225 | M410RO755 | WATER SPRAY FOR 410-T-015FROM 410-STR-755 TO 410-PG-755 | WATER SPRAY FOR 410-T-015FROM 410-STR-755 TO 410-PG-755 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175226 | M410RO756 | WATER SPRAY FOR 410-T-015FROM 410-STR-756 TO 410-PG-756 | WATER SPRAY FOR 410-T-015FROM 410-STR-756 TO 410-PG-756 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175336 | M410PG743 | WATER SPRAY FOR 410-T-013FROM 410-RO-743 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-743 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175337 | M410PG744 | WATER SPRAY FOR 410-T-014FROM 410-RO-744 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-744 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175338 | M410PG745 | WATER SPRAY FOR 410-T-014FROM 410-RO-745 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-745 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175339 | M410PG746 | WATER SPRAY FOR 410-T-014FROM 410-RO-746 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-746 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175340 | M410PG747 | WATER SPRAY FOR 410-T-014FROM 410-RO-747 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-747 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175341 | M410PG748 | WATER SPRAY FOR 410-T-014FROM 410-RO-748 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-748 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175342 | M410PG749 | WATER SPRAY FOR 410-T-014FROM 410-RO-749 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-749 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175343 | M410PG750 | WATER SPRAY FOR 410-T-014FROM 410-RO-750 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-750 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175344 | M410PG751 | WATER SPRAY FOR 410-T-014FROM 410-RO-751 TO RISER PIPE | WATER SPRAY FOR 410-T-014FROM 410-RO-751 TO RISER PIPE |  | INDICATR | M410T014 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175345 | M410PG752 | WATER SPRAY FOR 410-T-015FROM 410-RO-752 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-752 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175227 | M410RO757 | WATER SPRAY FOR 410-T-015FROM 410-STR-757 TO 410-PG-757 | WATER SPRAY FOR 410-T-015FROM 410-STR-757 TO 410-PG-757 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175228 | M410RO758 | WATER SPRAY FOR 410-T-015FROM 410-STR-758 TO 410-PG-758 | WATER SPRAY FOR 410-T-015FROM 410-STR-758 TO 410-PG-758 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175229 | M410RO759 | WATER SPRAY FOR 410-T-015FROM 410-STR-759 TO 410-PG-759 | WATER SPRAY FOR 410-T-015FROM 410-STR-759 TO 410-PG-759 |  | ORIFICE | M410T015 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175230 | M410RO760 | WATER SPRAY FOR 410-T-016FROM 410-STR-760 TO 410-PG-760 | WATER SPRAY FOR 410-T-016FROM 410-STR-760 TO 410-PG-760 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175231 | M410RO761 | WATER SPRAY FOR 410-T-016FROM 410-STR-761 TO 410-PG-761 | WATER SPRAY FOR 410-T-016FROM 410-STR-761 TO 410-PG-761 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175232 | M410RO762 | WATER SPRAY FOR 410-T-016FROM 410-STR-762 TO 410-PG-762 | WATER SPRAY FOR 410-T-016FROM 410-STR-762 TO 410-PG-762 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175233 | M410RO763 | WATER SPRAY FOR 410-T-016FROM 410-STR-763 TO 410-PG-763 | WATER SPRAY FOR 410-T-016FROM 410-STR-763 TO 410-PG-763 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175234 | M410RO764 | WATER SPRAY FOR 410-T-016FROM 410-STR-764 TO 410-PG-764 | WATER SPRAY FOR 410-T-016FROM 410-STR-764 TO 410-PG-764 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175235 | M410RO765 | WATER SPRAY FOR 410-T-016FROM 410-STR-765 TO 410-PG-765 | WATER SPRAY FOR 410-T-016FROM 410-STR-765 TO 410-PG-765 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175236 | M410RO766 | WATER SPRAY FOR 410-T-016FROM 410-STR-766 TO 410-PG-766 | WATER SPRAY FOR 410-T-016FROM 410-STR-766 TO 410-PG-766 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175237 | M410RO767 | WATER SPRAY FOR 410-T-016FROM 410-STR-767 TO 410-PG-767 | WATER SPRAY FOR 410-T-016FROM 410-STR-767 TO 410-PG-767 |  | ORIFICE | M410T016 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195615 | M410GAV2353012 | 3/4" Class 800 Gate Valve, LOCK DEVICE | 3/4" Class 800 Gate Valve, LOCK DEVICE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195616 | M410GAV2353013 | 1" Class 800 Gate Valve, LOCK DEVICE | 1" Class 800 Gate Valve, LOCK DEVICE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195617 | M410GAV2354001 | 2" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# | 2" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195618 | M410GAV2354002 | 3" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# | 3" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195815 | M410FWCP031A | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031A |  | F&G_PNL | M410P031A | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195816 | M410FWCP031B | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031B |  | F&G_PNL | M410P031B | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195817 | M410FWCP031C | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031C |  | F&G_PNL | M410P031C | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195818 | M410FWCP031D | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031D |  | F&G_PNL | M410P031D | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195819 | M410FWCP031E | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031E |  | F&G_PNL | M410P031E | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195820 | M410FWCP031F | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031F |  | F&G_PNL | M410P031F | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195821 | M410FWCP031G | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031G |  | F&G_PNL | M410P031G | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195822 | M410FWCP032A | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-032A |  | F&G_PNL | M410P032A | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195823 | M410FWCP032B | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-032B |  | F&G_PNL | M410P032B | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195824 | M410FWCP033A | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-033A |  | F&G_PNL | M410P033A | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195825 | M410FWCP033B | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-033B |  | F&G_PNL | M410P033B | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195619 | M410GAV2354003 | 4" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# | 4" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195620 | M410GAV2354004 | 6" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# | 6" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195826 | M410FWCP034 | CONTROL PANEL | CONTROL PANEL FOR FIRE WATER PUMP 410-P-034 |  | F&G_PNL | M410P034 | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Non Critical | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195621 | M410GAV2354005 | 2" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# | 2" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195622 | M410GAV2354006 | 20" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# | 20" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195623 | M410GAV2354007 | 4" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# | 4" CAST STEEL GATE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195624 | M410GAV2354008 | 2" CAST STEEL GATE VALVES RF, OS&Y, BB, 300# | 2" CAST STEEL GATE VALVES RF, OS&Y, BB, 300# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195625 | M410GLV2353001 | 3/4" Class 800 GLOBE Valve | 3/4" Class 800 GLOBE Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195626 | M410GLV2354001 | 2" CAST STEEL GLOBE VALVES RF, OS&Y, BB, 150# | 2" CAST STEEL GLOBE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195627 | M410GLV2354002 | 3" CAST STEEL GLOBE VALVES RF, OS&Y, BB, 150# | 3" CAST STEEL GLOBE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195628 | M410GLV2354003 | 8" CAST STEEL GLOBE VALVES RF, OS&Y, BB, 150# | 8" CAST STEEL GLOBE VALVES RF, OS&Y, BB, 150# |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195629 | M410INS001 | SUBSTATION BUILDING INERGEN SYSTEM | SUBSTATION BUILDING INERGEN SYSTEM |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195630 | M410INS002 | SIS INERGEN SYSTEM | SIS INERGEN SYSTEM |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195631 | M410INS003 | EXTENSION CONTROL BLDG INERGEN SYSTEM | EXTENSION CONTROL BLDG INERGEN SYSTEM |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195632 | M410NC001 | SIS-001 NETWORK CABINET | SIS-001 NETWORK CABINET |  |  | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195711 | M410FG078 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195712 | M410FG079 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184857 | M410MS0013A | 3.3KV Switchgear Panel | PANEL FOR MUS-ALN GAS OIL MAINLINE PUMP-A(410-MP-004A)-950KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0013A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184858 | M410MS0014A | 3.3KV Switchgear Panel | PANEL FOR MUS-ADIA JET A1 MAINLINE PUMP-A(410-MP-006A)-500KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0014A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184859 | M410MS0015A | 3.3KV Switchgear Panel | PANEL FOR MUS-ADIA JET A1 MAINLINE PUMP-C(410-MP-006C)-500KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0015A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184860 | M410MS0016A | 3.3KV Switchgear Panel | PANEL FOR MUS-ALD JET A1 PUMP-A(410-MP-024A)-160KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0016A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184861 | M410MS0017A | 3.3KV Switchgear Panel | DUMMY PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410MS0017A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184862 | M410MS0018A | 3.3KV Switchgear Panel | PANEL FOR MUS-ADIA JET A1 BOOSTER PUMP-A(410-MP-005A)-250KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0018A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184863 | M410MS0019A | 3.3KV Switchgear Panel | PANEL FOR MUS-ADIA JET A1 BOOSTER PUMP-C(410-MP-005C)-250KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0019A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184864 | M410MS00110A | 3.3KV Switchgear Panel | PANEL FOR ULG 91/95 INTER-TANK TRANSFER PUMP-A(410-MP-007A)-150KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410MS00110A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184865 | M410MS00111A | 3.3KV Switchgear Panel | PANEL FOR ULG 91/95 INTER-TANK TRANSFER PUMP-C(410-MP-007C)-150KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00111A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184866 | M410MS00112A | 3.3KV Switchgear Panel | PANEL FOR GAS OIL INTER-TANK TRANSFER PUMP-A(410-MP-008A)-200KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00112A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184867 | M410MS00113A | 3.3KV Switchgear Panel | PANEL FOR JET A1 INTER-TANK TRANSFER PUMP-A(410-MP-014A)-200KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00113A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184868 | M410MS00114A | 3.3KV Switchgear Panel | DUMMY PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410MS00114A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184869 | M410MS00115A | 3.3KV Switchgear Panel | PANEL FOR FIRE WATER PUMP MOTOR DRIVEN-A(410-FWCP-032A) 450KW |  | SWBOARD | M410SCB | 1 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MS00115A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184870 | M410MS00116A | 3.3KV Switchgear Panel | PANEL FOR 3.3KV POWER CAPACITOR BANK-A(410-PFI-001A) |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00116A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969265861 | PL100ACBATT001A | BATTERY,BANK | Battery for 100-UPS-AC-001A |  | BATTERY | PL100BATT | 3 | BATTERY | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281346 | M410P004B | VIBRATION MONITORING SYSTEM, SUB-ASSY OF 410-P-004B | AL AIN GAS OIL MAIN LINE PUMP | 969269216 | EMERSDD | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265904 | PL100LT150 | LEVEL TRANSMITTER(GUIDE WAVE RADAR) | LEVEL TRANSMITTER(GUIDE WAVE RADAR) |  | LVL_TX | PL100LEVEL | 3 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265905 | PL100LT151 | LEVEL TRANSMITTER(GUIDE WAVE RADAR) | LEVEL TRANSMITTER(GUIDE WAVE RADAR) |  | LVL_TX | PL100LEVEL | 3 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265906 | PL100MOV400 | MOTOR OPERATED VALVE | MOV (RUWAIS) SHEWIHAT RECIVING STATION. |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265933 | PL100PG407 | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265935 | PL100PG409 | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265936 | PL100PG410 | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265937 | PL100PG411 | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265938 | PL100PG412 | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281627 | M410PG641 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281628 | M410PG642 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281629 | M410PG643 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281630 | M410PG644 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281631 | M410PG645 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281632 | M410PG646 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281633 | M410PG651 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281634 | M410PG652 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281635 | M410PG653 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281636 | M410PG654 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281637 | M410PG655 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265939 | PL100PG413 | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265940 | PL100PG414 | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~10kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270735 | M410PV002 | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, UTILITY AIR FROM COMPRESSOR PACKAGE | 969269246 | CNTR_VLV | M410V006 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270736 | M410PV245 | ACTUATOR FOR 12X8" GLOBE VALVE, CLASS 300 | 12X8" GLOBE VALVE, CLASS 300, TO MUSSAFAH-AIDA JET A1 PIPELINE | 969269247 | CNTR_VLV | M410P006A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270737 | M410PV277 | ACTUATOR FOR 8X6" GLOBE VALVE, CLASS 900 | 8X6" GLOBE VALVE, CLASS 900, TO MUSSAFAH AIN ULG PIPELINE | 969269248 | CNTR_VLV | M410P002B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270738 | M410PV300 | ACTUATOR FOR 8X6" GLOBE VALVE, CLASS 900 | 8X6" GLOBE VALVE, CLASS 900, TO MUSSAFAH-AL AIN AS OIL PIPELINE | 969269249 | CNTR_VLV | M410P004B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270739 | M410PV402 | ACTUATOR FOR 16" GLOBE VALVE, CLASS 300 | 16" GLOBE VALVE, CLASS 300, TO JET A1 METERING | 969269250 | CNTR_VLV | M410PLR001 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270740 | M410PV413 | ACTUATOR FOR 24X20" GLOBE VALVE, CLASS 600 | 24X20" GLOBE VALVE, CLASS 600, GAS OIL TO METERING | 969269251 | CNTR_VLV | M410PT412 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270741 | M410PV462 | ACTUATOR FOR 6" GLOBE VALVE, CLASS 300 | 6" GLOBE VALVE, CLASS 300, FROM MUSSAFAH AL-DHAFRA MAIN LINE PUMPS | 969269252 | CNTR_VLV | M410PLR007 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175968 | M410PKG2306001 | Water Spray Nozzle | Water Spray Nozzle |  | VESSEL | M410MISC | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269769 | M410DAFHK1 | DAF HOOK LIFT VEHICLE #1 RED A/D31622-5. BIG FLOW SYSTEM. | AD 31622-5 DAF HOOKLIFT TRUCK #1 BIG FLOW PACKAGE. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 5 | 10 | 1 | 5 | 4.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270744 | M410LDS001 | LDS SYSTEM CABINET | LDS SYSTEM CABINET |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37145 | UTOYOTA52394 | 12 / 52394 - TOYOTA HILUX PICK-UP | TOYOTA HILUX PICK-UP 12 / 52394 |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA52394UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 04/08/18 | MM-PM-029-M1
IAS59127 | M50PSH155F | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-105 | TNK56585 | PRES_SWT | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH155F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/06/19 | MC-PM-009-Y1
IAS59128 | M50PSL135F | SWITCH, PRESSURE, DIAPHRAGM , 5A @ 110/250VAC & 2A @ 30 VDC , 0-10 BAR , SPDT , | FOAM LOW PRESSURE SWITCH FOR TANK T-105 | TNK56585 | PRES_SWT | M10T105 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL135F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/06/19 | MC-PM-009-Y1
IAS59129 | M50PSH155W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-105 | TNK56585 | PRES_SWT | M10T105 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH155W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/06/19 | MC-PM-009-Y1
IAS59130 | M50PSL135W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-105 | TNK56585 | PRES_SWT | M10T105 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL135W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/06/19 | MC-PM-009-Y1
IAS59140 | M10LZALL062 | SWITCH, LEVEL FLOAT, RF FLANGE , SPDT , ANSI 150 , 2" , SIDE/SIDE , 40 DEG C WOR | LEVEL SWITCH (FLOAT+CAGE) FOR TANK T-106 | TNK56600 | LVL_SWT | M10T106 | 1 | LVL_SWT | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | M10LZALL062-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/10/18 | MC-PM-024-M6
IAS59147 | M50PSH156F | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-106 | TNK56600 | PRES_SWT | M10T106 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH156F-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/06/19 | MC-PM-009-Y1
IAS59149 | M50PSH156W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | FIRE FIGHTING HIGH PRESSURE SWITCH FOR TANK T-106 | TNK56600 | PRES_SWT | M10T106 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSH156W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/06/19 | MC-PM-009-Y1
IAS59150 | M50PSL136W | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 0-10 BAR , SPDT , IP55 , | WATER SPRAY LOW PRESSURE SWITCH FOR TANK T-106 | TNK56600 | PRES_SWT | M10T106 | 1 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M50PSL136W-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/06/19 | MC-PM-009-Y1
969274290 | M400VDR900 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 117 | 939610 | VALCH | M400T117 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271728 | M410STR002B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271729 | M410STR003A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271734 | M410STR005B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271737 | M410STR006B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271738 | M410STR006C | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271739 | M410STR023A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271740 | M410STR023B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275202 | M410MOV232 | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269977 | CONTHNDV | M410L008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275203 | M410MOV233 | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269978 | CONTHNDV | M410L009A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275204 | M410MOV234 | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269979 | CONTHNDV | M410L009B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275205 | M410MOV235 | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269980 | CONTHNDV | M410L009A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275206 | M410MOV236 | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269981 | CONTHNDV | M410L009B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275207 | M410MOV300A | Valve, Ball. 16", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269982 | CONTHNDV | M410P003A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275208 | M410MOV300B | Valve, Ball. 16", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269983 | CONTHNDV | M410P003B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275209 | M410MOV301A | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269984 | CONTHNDV | M410P003A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275210 | M410MOV301B | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269985 | CONTHNDV | M410P003B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275211 | M410MOV302A | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269986 | CONTHNDV | M410P024A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275212 | M410MOV302B | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269987 | CONTHNDV | M410P024B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275213 | M410MOV302C | Valve, Ball. 8", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269988 | CONTHNDV | M410P024C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275214 | M410MOV303A | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269989 | CONTHNDV | M410P024A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275215 | M410MOV303B | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269990 | CONTHNDV | M410P024B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275216 | M410MOV303C | Valve, Ball. 6", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269991 | CONTHNDV | M410P024C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275217 | M410MOV400 | Valve, Ball. 28", 300#, FB, Body ASTM A 105, Trim SS316, MOTOR OPERATED | JET A1 PIG LAUNCHER MOTOR OPERATED VALVE | 969270052 | CONTHNDV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275218 | M410MOV400AA | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | JET A1 MOTOR OPERATED VALVE | 969269992 | CONTHNDV | M410FT400A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275219 | M410MOV400BA | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | JET A1 MOTOR OPERATED VALVE | 969269993 | CONTHNDV | M410FT400B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275220 | M410MOV400CA | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | JET A1 MOTOR OPERATED VALVE | 969269994 | CONTHNDV | M410FT400C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275221 | M410MOV401AA | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269995 | CONTHNDV | M410FT401A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275222 | M410MOV401BA | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269996 | CONTHNDV | M410FT401B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275223 | M410MOV401CA | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269997 | CONTHNDV | M410FT401C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275224 | M410MOV402 | Valve, Ball. 28", 300#, BW + RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269998 | CONTHNDV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275225 | M410MOV403 | Valve, Ball. 28", 300#, BW + RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969269999 | CONTHNDV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275226 | M410MOV406A | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270000 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275227 | M410MOV406B | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270001 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275228 | M410MOV406C | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270002 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275229 | M410MOV406D | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270003 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275230 | M410MOV406E | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270004 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275231 | M410MOV407A | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270005 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275232 | M410MOV407B | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270006 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275233 | M410MOV407C | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270007 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275234 | M410MOV407D | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270008 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 3 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275235 | M410MOV407E | Valve, Ball. 12", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270009 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275236 | M410MOV408 | Valve, Ball. 28", 600#, FB, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270051 | CONTHNDV | M410PLR002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275237 | M410MOV410 | Valve, Ball. 28", 600#, BW + RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270010 | CONTHNDV | M410PT412 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275238 | M410MOV413 | Valve, Ball. 28", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270011 | CONTHNDV | M410L006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275239 | M410MOV414 | Valve, Ball. 28", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270012 | CONTHNDV | M410L006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275240 | M410MOV415 | Valve, Ball. 28", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270013 | CONTHNDV | M410L006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275241 | M410MOV416 | Valve, Ball. 28", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270014 | CONTHNDV | M410L006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275242 | M410MOV417 | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270015 | CONTHNDV | M410PLR005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275243 | M410MOV419 | Valve, Ball. 12", 900#, FB, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270050 | CONTHNDV | M410PLR005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275244 | M410MOV420 | Valve, Ball. 20", 300#, BW + RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270016 | CONTHNDV | M410PT412 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275245 | M410MOV421A | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270017 | CONTHNDV | M410P004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275246 | M410MOV421B | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270018 | CONTHNDV | M410P004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275247 | M410MOV422A | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270019 | CONTHNDV | M410P004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275248 | M410MOV422B | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270020 | CONTHNDV | M410P004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275249 | M410MOV423 | Valve, Ball. 12", 600#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270021 | CONTHNDV | M410PLR006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275250 | M410MOV425 | Valve, Ball. 12", 600#, FB, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270053 | CONTHNDV | M410PLR006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275251 | M410MOV426 | Valve, Ball. 12", 600#, RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270022 | CONTHNDV | M410PLR006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275252 | M410MOV427A | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270023 | CONTHNDV | M410L001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275253 | M410MOV427B | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270024 | CONTHNDV | M410L001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275254 | M410MOV427C | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270025 | CONTHNDV | M410L001C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275255 | M410MOV427D | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270026 | CONTHNDV | M410L001D | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275256 | M410MOV428A | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270027 | CONTHNDV | M410L001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275257 | M410MOV428B | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270028 | CONTHNDV | M410L001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275258 | M410MOV428C | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270029 | CONTHNDV | M410L001C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275259 | M410MOV428D | Valve, Ball. 12", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270030 | CONTHNDV | M410L001D | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275260 | M410MOV429 | Valve, Ball. 20", 300#, RF + BW, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270031 | CONTHNDV | M410PLR003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275261 | M410MOV430 | Valve, Ball. 20", 300#, FB, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270054 | CONTHNDV | M410PLR003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275262 | M410MOV431 | Valve, Ball. 20", 300#, RF + BW, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270032 | CONTHNDV | M410PLR003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275263 | M410MOV438A | Valve, Ball. 10", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270033 | CONTHNDV | M410L011A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275264 | M410MOV438B | Valve, Ball. 10", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270034 | CONTHNDV | M410L011B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275265 | M410MOV439A | Valve, Ball. 10", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270035 | CONTHNDV | M410L011A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275266 | M410MOV439B | Valve, Ball. 10", 150#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270036 | CONTHNDV | M410L011B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281604 | M410CCTVP004 | CCTV CABINET | L&D CCTV CABINET MCR, PIPELINE SURVEILLANCE. |  | BLDGS | M410CCTV | 3 | CCTV_SYS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267920 | PL100BAV21242009 | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267921 | PL100BAV21242010 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267922 | PL100BAV21242011 | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267923 | PL100BAV21242012 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56527 | M50WOV131B | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-101 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-101 |  | VALVE | M10T101 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269680 | M410DOM1 | #1 DOMINATOR WITH DUAL PUMPS 5K GPM EACH -BIG FLOW SYSTEM. | #1 DOMINATOR WITH DUAL PUMPS 5K GPM EACH -BIG FLOW SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Non Critical | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56529 | M50J101A | FIRE FIGHTING FOAM GENERATOR FOR T-101 | FIRE FIGHTING FOAM GENERATOR FOR T-101 |  | VESSEL | M10T101 | 1 | FG_DET | 617101-310510 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56530 | M50J101B | FIRE FIGHTING FOAM GENERATOR FOR T-101 | FIRE FIGHTING FOAM GENERATOR FOR T-101 |  | F_MIXR | M10T101 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56541 | M50PIPE102 | PIPELINE POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-102 |  | PIPING | M10T102 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56542 | M50WOV132A | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-102 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-102 |  | VALVE | M10T102 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56543 | M50WOV132B | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-102 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-102 |  | VALVE | M10T102 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56557 | M50PIPE103 | PIPELINE POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-103 |  | PIPING | M10T103 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56558 | M50T183A | FIRE FIGHTING FOAM BAG TANK FOR TANK T101,T-103,T103 | FIRE FIGHTING FOAM BAG TANK T101,T102,T103 |  | TK | M10TANKS | 1 | TK | 617101-310510 | MTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56559 | M50T183B | FIRE FIGHTING FOAM BAG TANK FOR TANK T101,T-103,T103 | FIRE FIGHTING FOAM BAG TANK T101,T-102,T103 |  | TK | M10TANKS | 1 | TK | 617101-310510 | MTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56560 | M50WOV133A | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-103 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-103 |  | VALVE | M10T103 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935659 | SMLPGTP14 | CP TEST POINT | TEST POINT # 14 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935660 | SMLPGTP15 | CP TEST POINT | TEST POINT # 15 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935661 | SMLPGTP16 | CP TEST POINT | TEST POINT # 16 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56561 | M50WOV133B | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-103 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-103 |  | VALVE | M10T103 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56573 | M50PIPE104 | PIPELINE POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-104 |  | PIPING | M10T104 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56574 | M50T184 | FIRE FIGHTING FOAM BAG TANK FOR TANK T104 | FIRE FIGHTING FOAM BAG TANK FOR TANK T104 |  | TK | M10T104 | 1 | TK | 617101-310510 | MTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56575 | M50WOV134W | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-104 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-104 |  | VALVE | M10T104 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56576 | M50WOV134F | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-104 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-104 |  | VALVE | M10T104 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56589 | M50PIPE105 | PIPELINE, POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-105 |  | PIPING | M10T105 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56590 | M50T185 | FOAM | FIRE FIGHTING FOAM BAG TANK FOR TANK T105 |  |  | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56591 | M50WOV135W | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-105 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-105 |  | VALVE | M10T105 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56592 | M50WOV135F | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-105 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-105 |  | VALVE | M10T105 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56606 | M50PIPE106 | PIPELINE POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-106 |  | PIPING | M10T106 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56607 | M50T186 | FIRE FIGHTING FOAM BAG TANK FOR TANK T105 | FIRE FIGHTING FOAM BAG TANK FOR TANK T105 |  | TK | M10T106 | 1 | TK | 617101-310510 | MTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56608 | M60WOV136W | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-106 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-106 |  | VALVE | M10T106 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56609 | M60WOV136F | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-106 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-106 |  | VALVE | M10T106 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56624 | M50PIPE107 | PIPELINE POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-107 |  | PIPING | M10T107 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56625 | M50T187 | FIRE FIGHTING FOAM BAG TANK FOR TANK T-107 | FIRE FIGHTING FOAM BAG TANK FOR TANK T-107 |  | TK | M10T107 | 1 | TK | 617101-310510 | MTERMINAL | OPERATING | 50 | 1 | 50 | 10 | 1 | 1 | 4.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56626 | M50WOV137W | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-107 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-107 |  | VALVE | M10T107 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56627 | M50WOV137F | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-107 (DELUGE VALVE) | FIRE FIGHTING WATER OPERATED VALVE FOR TANK T-107 |  | VALVE | M10T107 | 1 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56642 | M50PIPE108 | PIPELINE POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-108 |  | PIPING | M10T108 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56653 | M50PIPE109 | PIPELINE POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-109 |  | PIPING | M10T109 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX56664 | M50PIPE110 | PIPELINE, POTABLE WATER | FIRE FIGHTING PIPELINES FOR TANK T-110 |  | PIPING | M10T110 | 1 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935675 | SMLPGTP30 | CP TEST POINT | TEST POINT # 30 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935676 | SMLPGTP31 | CP TEST POINT | TEST POINT # 31 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935677 | SMLPGTP32 | CP TEST POINT | TEST POINT # 32 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935690 | SMLPGTP45 | CP TEST POINT | TEST POINT # 45 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935691 | SMLPGTP46 | CP TEST POINT | TEST POINT # 46 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935692 | SMLPGTP47 | CP TEST POINT | TEST POINT # 47 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935481 | SALAINTP33 |  | TEST POINT # 33 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935482 | SALAINTP34 |  | TEST POINT # 34 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935483 | SALAINTP35 |  | TEST POINT # 35 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935497 | SALAINTP49 |  | TEST POINT # 49 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935498 | SALAINTP50 |  | TEST POINT # 50 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935499 | SALAINCP3GB1 |  | GROUN BED (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935515 | SALAINTP61 |  | TEST POINT # 61 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935516 | SALAINTP62 |  | TEST POINT # 62 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935517 | SALAINTP63 |  | TEST POINT # 63 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935644 | SMTP46 | ??????????????? | TEST POINT# 46 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935645 | SMTP47 | ?????????????? | TEST POINT# 47 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935646 | SMLPGTP1 | CP TEST POINT | TEST POINT # 1 AT MUSSAFAH LPG TRANSFER P.L. |  |  | SMLPGTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512476 | A-MSFH-ANWAR | DELL OPTIPLEX 9020 | Anwer Ibrahim Al Ali |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512477 | SD-MSFH-AUDIT | Dell Optiplex 9020 | Auditoruim |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512480 | A-MSFH-TANNAF | Lenovo - M2999-A34 | Mohammed Tannaf Al Kabbi |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512481 | SDABDULLA | HP PRO DESK 600 G1 | Abdulla Ahmed |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512657 | A-R32-AUHOOD | HP Prodesk 600 G1 | AUHOOD IBRAHIM |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512661 | SDPLANCONT | HP Prodesk 600 G1 | TANZEEL UR REHMAN |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512663 | A-MSFH-OMER | Dell Optiplex 760 | DELL OPTIPLEX 760 |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512664 | SD-MSFH-HAMED | HP Prodesk 600 G1 | HAMED AHMED AL HAMMADI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281338 | M410L050BB | DUPLEX FILTER FOR 410-P-002A/B | DUPLEX FILTER FOR 410-P-002A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281339 | M410L051AA | DUPLEX FILTER FOR 410-P-004A/B | DUPLEX FILTER FOR 410-P-004A/B |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175726 | M410MOV1510 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1510-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/11/18 | ME-PM-002-M6
969175727 | M410MOV1601 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1601-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/11/18 | ME-PM-002-M6
969175728 | M410MOV1602 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1602-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969175729 | M410MOV1603 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1603-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969175730 | M410MOV1604 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1604-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/11/18 | ME-PM-002-M6
969175731 | M410MOV1605 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1605-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/11/18 | ME-PM-002-M6
969175732 | M410MOV1606 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1606-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/11/18 | ME-PM-002-M6
969175733 | M410MOV1607 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1607-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969175734 | M410MOV1608 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1608-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969175735 | M410MOV1609 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1609-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/11/18 | ME-PM-002-M6
969175736 | M410MOV1610 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-016 |  | MOV | M410T016 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1610-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/11/18 | ME-PM-002-M6
969175737 | M410MOV450A | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004A | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004A |  | MOV | M410L004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV450A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/12/18 | ME-PM-002-M6
969175738 | M410MOV450B | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004B | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004B |  | MOV | M410L004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV450B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969175739 | M410MOV450C | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004C | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004C |  | MOV | M410L004C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV450C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969175740 | M410MOV451A | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004A | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004A |  | MOV | M410L004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV451A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969175741 | M410MOV451B | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004B | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004B |  | MOV | M410L004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 3 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV451B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969175742 | M410MOV451C | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004C | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004C |  | MOV | M410L004C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV451C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/12/18 | ME-PM-002-M6
969175743 | M410MOV751A | SUCTION Motor Operated Valve(Ball) OF 410-P007A | SUCTION Motor Operated Valve(Ball) OF 410-P-007A |  | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV751A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175744 | M410MOV752A | SUCTION Motor Operated Valve(Ball) OF 410-P007A | SUCTION Motor Operated Valve(Ball) OF 410-P-007A |  | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV752A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175745 | M410MOV753A | DISCHARGE Motor Operated Valve(Ball) OF 410-P007A | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007A |  | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV753A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175746 | M410MOV754A | DISCHARGE Motor Operated Valve(Ball) OF 410-P007A | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007A |  | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV754A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175747 | M410MOV755B | SUCTION Motor Operated Valve(Ball) OF 410-P007B | SUCTION Motor Operated Valve(Ball) OF 410-P-007B |  | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV755B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175748 | M410MOV756B | SUCTION Motor Operated Valve(Ball) OF 410-P007B | SUCTION Motor Operated Valve(Ball) OF 410-P-007B |  | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV756B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175749 | M410MOV757B | DISCHARGE Motor Operated Valve(Ball) OF 410-P007B | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007B |  | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV757B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175750 | M410MOV758B | DISCHARGE Motor Operated Valve(Ball) OF 410-P007B | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007B |  | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV758B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175751 | M410MOV759C | SUCTION Motor Operated Valve(Ball) OF 410-P007C | SUCTION Motor Operated Valve(Ball) OF 410-P-007C |  | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV759C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175752 | M410MOV760C | SUCTION Motor Operated Valve(Ball) OF 410-P007C | SUCTION Motor Operated Valve(Ball) OF 410-P-007C |  | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV760C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175753 | M410MOV761C | DISCHARGE Motor Operated Valve(Ball) OF 410-P007C | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007C |  | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV761C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175754 | M410MOV762C | DISCHARGE Motor Operated Valve(Ball) OF 410-P007C | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007C |  | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV762C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969175755 | M410MOV763 | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV763-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969175756 | M410MOV764 | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV764-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969175757 | M410MOV765 | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV765-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/12/18 | ME-PM-002-M6
969175758 | M410MOV766 | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV766-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/12/18 | ME-PM-002-M6
969175759 | M410MOV767 | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV767-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969175760 | M410MOV768 | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV768-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969175761 | M410MOV769A | INLET Motor Operated Valve(Ball) TO FILTER | INLET Motor Operated Valve(Ball) TO FILTER |  | MOV | M410L007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV769A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
969175762 | M410MOV769B | INLET Motor Operated Valve(Ball) TO FILTER | INLET Motor Operated Valve(Ball) TO FILTER |  | MOV | M410L007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV769B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969175763 | M410MOV770A | OUTLET Motor Operated Valve(Ball) TO FILTER | OUTLET Motor Operated Valve(Ball) TO FILTER |  | MOV | M410L007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV770A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
969175764 | M410MOV770B | OUTLET Motor Operated Valve(Ball) TO FILTER | OUTLET Motor Operated Valve(Ball) TO FILTER |  | MOV | M410L007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV770B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969175765 | M410MOV851A | SUCTION Motor Operated Valve(Ball) | SUCTION Motor Operated Valve(Ball) |  | MOV | M410P008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV851A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969175766 | M410MOV852A | DISCHARGE Motor Operated Valve(Ball) | DISCHARGE Motor Operated Valve(Ball) |  | MOV | M410P008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV852A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/12/18 | ME-PM-002-M6
969175767 | M410MOV853B | SUCTION Motor Operated Valve(Ball) | SUCTION Motor Operated Valve(Ball) |  | MOV | M410P008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV853B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/12/18 | ME-PM-002-M6
969175768 | M410MOV854B | DISCHARGE Motor Operated Valve(Ball) | DISCHARGE Motor Operated Valve(Ball) |  | MOV | M410P008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV854B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/12/18 | ME-PM-002-M6
969175769 | M410MOV855 | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV855-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969175770 | M410MOV856 | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV856-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969175771 | M410MOV857 | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV857-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/12/18 | ME-PM-002-M6
969195498 | M410FU403 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195481 | M410FU326 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195482 | M410FU327 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195483 | M410FU328 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195484 | M410FU329 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175778 | M410PSV091 | Gas Oil Inter-Tank Transfer Basket Filters | Gas Oil Inter-Tank Transfer Basket Filters |  | PSV | M410L007A | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175779 | M410PSV092 | Gas Oil Inter-Tank Transfer Basket Filters | Gas Oil Inter-Tank Transfer Basket Filters |  | PSV | M410L007B | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175780 | M410TSV001 | ULG 91 TANK 410-T-001 INLET MANIFOLD | ULG 91 TANK 410-T-001 INLET MANIFOLD |  | PSV | M410T001 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175781 | M410TSV002 | ULG 91 TANK 410-T-001 INLET MANIFOLD | ULG 91 TANK 410-T-001 INLET MANIFOLD |  | PSV | M410T001 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175782 | M410TSV003 | ULG 91 TANK 410-T-001 OUTLET MANIFOLD | ULG 91 TANK 410-T-001 OUTLET MANIFOLD |  | PSV | M410T001 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175783 | M410TSV004 | ULG 91 TANK 410-T-001 OUTLET MANIFOLD | ULG 91 TANK 410-T-001 OUTLET MANIFOLD |  | PSV | M410T001 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175784 | M410TSV005 | ULG 91 TANK 410-T-002 INLET MANIFOLD | ULG 91 TANK 410-T-002 INLET MANIFOLD |  | PSV | M410T002 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132780 | M400WWTPAC1 | HVAC, SPLIT, 24000 BTU/HR, 24,000.0 BTU/HR, 230.0 V, S246GC, 230.0 V | SPLIT A/C UNIT NO.1 AT WWTP MCC ROOM |  | HVAC | M400WWTPAC | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132781 | M400WWTPAC2 | HVAC, SPLIT, 2.5 TON, 30,000.0 BTU/HR, 230.0 V, LVNC 608LLA1 | SPLIT A/C UNIT NO.2 AT WWTP |  | HVAC | M400WWTPAC | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132782 | M400WWTPAC3 | HVAC, SPLIT, 2.5 TON, 30,000.0 BTU/HR, 230.0 V, LVNG 608 LLA1 | SPLIT A/C UNIT NO.3 AT WWTP |  | HVAC | M400WWTPAC | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132783 | M400WWTPAC4 | HVAC, SPLIT, 2.5 TON, 30,000.0 BTU/HR, LVNG608 LLA1 | SPLIT A/C UNIT NO.4 AT WWTP |  | HVAC | M400WWTPAC | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132784 | M400WWTPAC5 | HVAC, SPLIT, 2.5 TON, 30,000.0 BTU/HR, LVNG 608 LLA1 | SPLIT A/C UNIT NO.5 AT WWTP |  | HVAC | M400WWTPAC | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935493 | SALAINTP45 |  | TEST POINT # 45 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935494 | SALAINTP46 |  | TEST POINT # 46 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935495 | SALAINTP47 |  | TEST POINT # 47 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935511 | SALAINTP57 |  | TEST POINT # 57 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935512 | SALAINTP58 |  | TEST POINT # 58 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935513 | SALAINTP59 |  | TEST POINT # 59 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935527 | SALAINTP72 |  | TEST POINT # 72 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935528 | SALAINTP73 |  | TEST POINT # 73 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935480 | SALAINTP32 |  | TEST POINT # 32 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935496 | SALAINTP48 |  | TEST POINT # 48 (C.P.STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935514 | SALAINTP60 |  | TEST POINT # 60 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935529 | SALAINTP74 |  | TEST POINT # 74 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935548 | SALAINTP90 |  | TEST POINT # 90 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935564 | SALAINTP104 |  | TEST POINT # 104 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935581 | SADIATP12 |  | TEST POINT# 12 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935598 | SMCP1IJ1 |  | INSULATING JOINT 1 AT KM 0 (MUSSAFAH PROD.) |  |  | SMPIPE | 1 | PIPING | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 5 | 1 | 1 | 5 | 3.0969 | Low | Low | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935613 | SMTP14 |  | TEST POINT# 14 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131972 | MQ600MCCB001A | BREAKER,CIRCUIT, MCCB, 2 P, YES | MCCB FOR 600-BATT-001A |  | BREAKER | MQ600BATT001A | 3 | BREAKER | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131980 | MQ600TCP001 | CATHODIC PROTECTION, C.P. FOR BURRIED PIPELINES, 240 VOLT, 50 HZ, 1, 10 VOLT, 100 AMPERES, AIR, BS 148, 190 LITERS | CATHODIC PROTECTION RECTIFIER FOR PIPELINES |  | CATHPRO | MQ600SCB | 3 | CATHPRO | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132052 | MQ600XGC201 | GAS FLAMMABLE GAS DETECTOR | FLAMMABLE GAS DETECTOR PIGGING AREA |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XGC201-MFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM02.M3
969131121 | M400LP006R102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET. |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131122 | M400LP006Y102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET. |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131123 | M400LP006B102 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET. |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131124 | M400LP008R301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131125 | M400LP008Y301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131126 | M400LP008B301 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131127 | M400LP008R302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131129 | M400LP008B302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131130 | M400LP008Y302 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR SOUTH SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131131 | M400LP008R401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131132 | M400LP008Y401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131134 | M400LP008B401 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131135 | M400LP008R402 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131136 | M400LP008Y402 | LIGHT, WHITE, 240VAC 50HZ | STREET LIGHT POLE FOR WEST SIDE STREET |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969165720 | M410MP007C | ULG 91/97 INTER-TANK TRANSFER PUMP MOTOR | MOTOR FOR ULG 91/95 INTER-TANK TRANSFER PUMP 7-C |  | MOTOR | M410P007C | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP007C-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 30/11/18 | ME-PM-HT1-6M
969165721 | M410MP008A | GAS OIL INTER-TANK TRANSFER PUMP MOTOR | GAS OIL INTER-TANK TRANSFER PUMP MOTOR |  | MOTOR | M410P008A | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP008A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-HT1-6M
969165722 | M410MP008B | GAS OIL INTER-TANK TRANSFER PUMP MOTOR | GAS OIL INTER-TANK TRANSFER PUMP MOTOR |  | MOTOR | M410P008B | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP008B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-HT1-6M
969270261 | M410PG107B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410ME107 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270262 | M410PG108A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410ME108 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270263 | M410PG108B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410ME108 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270264 | M410PG701 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270265 | M410PG702 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270266 | M410PG703 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270267 | M410PG704 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270268 | M410PG711 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270269 | M410PG712 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270270 | M410PG713 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270271 | M410PG714 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M400ME003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270272 | M410PG739A | PRESSURE GAUGES | ANTI-STATIC PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270444 | M410PT426A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR005 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT426A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270445 | M410PT426B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR005 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT426B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270446 | M410PT426C | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR005 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT426C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270447 | M410PT432 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT432-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270448 | M410PT433A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT433A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270449 | M410PT433B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT433B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270450 | M410PT433C | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT433C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270451 | M410PT434 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR006 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT434-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270452 | M410PT441 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR003 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT441-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270453 | M410PT442A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR003 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT442A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270454 | M410PT442B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR003 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT442B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270455 | M410PT442C | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR003 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT442C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270456 | M410PT443 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR003 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT443-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270457 | M410PT459 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR007 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT459-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270458 | M410PT460A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR007 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT460A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270459 | M410PT460B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR007 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT460B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270460 | M410PT460C | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR007 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT460C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270461 | M410PT461 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR007 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT461-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270462 | M410PT462A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P024A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT462A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270463 | M410PT462B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR007 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT462B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270464 | M410PT500 | PRESSURE TRANSMITTERS | ANTI-STATIC PRESSURE TRANSMITTERS |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT500-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270465 | M410PT501 | PRESSURE TRANSMITTERS | ANTI-STATIC PRESSURE TRANSMITTERS |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT501-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270466 | M410RMCS001 | REMOTE MONITORING CONTROL SYSTEM CABINET FOR CATHODIC PROTECTION | REMOTE MONITORING CONTROL SYSTEM CABINET FOR CATHODIC PROTECTION |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269217 | M410P005A | ADIA NORTH JET A1 BOOSTER CENTRIFUGAL PUMP. | ADIA NORTH JET A1 BOOSTER PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269218 | M410P005B | ADIA NORTH JET A1 BOOSTER CENTRIFUGAL PUMP. | ADIA NORTH JET A1 BOOSTER PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269219 | M410P005C | ADIA NORTH JET A1 BOOSTER CENTRIFUGAL PUMP. | ADIA NORTH JET A1 BOOSTER PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269220 | M410P006A | ADIA NORTH JET A1 MAIN LINE CENTRIFUGAL PUMP. | ADIA NORTH JET A1 MAIN LINE PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269221 | M410P006B | ADIA NORTH JET A1 MAIN LINE CENTRIFUGAL PUMP. | ADIA NORTH JET A1 MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269222 | M410P006C | ADIA NORTH JET A1 MAIN LINE PUMP. | ADIA NORTH JET A1 MAIN LINE PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269223 | M410P024A | DHAFRA JP-8 MAIN LINE CENTRIFUGAL PUMP. | AL DHAFRA JP-8 MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269224 | M410P024B | DHAFRA JP-8 MAIN LINE CENTRIFUGAL PUMP. | AL DHAFRA JP-8 MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269225 | M410P024C | DHAFRA JP-8 MAIN LINE CENTRIFUGAL PUMP. | AL DHAFRA JP-8 MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270467 | M410FFE2101305 | Safety Cabinet | Safety Cabinet |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270468 | M410PSV751A | SAFETY VALVE FOR COMPRESSOR | SAFETY VALVE FOR COMPRESSOR |  | PSV | M410K001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270469 | M410PSV751B | SAFETY VALVE FOR COMPRESSOR | SAFETY VALVE FOR COMPRESSOR |  | PSV | M410K001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270470 | M410SCADA001 | SCADA SYSTEM CABINET | SCADA SYSTEM CABINET |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270471 | M410SCADA003 | SCADA APPSCABINET | SCADA APPSCABINET |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270472 | M410SCADA002 | SCADA NETWORKCABINET | SCADA NETWORKCABINET |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270473 | M410PLR003 | Scraper LAUNCHER MUSSAFAH-ADIA NORTH JET A1 PIPLINE | Scraper LAUNCHER MUSSAFAH-ADIA NORTH JET A1 PIPLINE |  | PIPING | M410MISC | 3 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270474 | M410PLR006 | Scraper LAUNCHER MUSSAFAH-ALAINGAS OIL PIPLINE | Scraper LAUNCHER MUSSAFAH-ALAINGAS OIL PIPLINE |  | PIPING | M410MISC | 3 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270475 | M410PLR007 | Scraper LAUNCHER MUSSAFAH-ALDHAFRA JP-8 PIPLINE | Scraper LAUNCHER MUSSAFAH-ALDHAFRA JP-8 PIPLINE |  | PIPING | M410MISC | 3 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270476 | M410PLR005 | Scraper Launcher ULG Pipeline(From Mussafah to AlAin) | Scraper Launcher ULG Pipeline(From Mussafah to AlAin) |  | PIPING | M410MISC | 3 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270477 | M410PLR002 | Scraper RECEIVER RUWAIS-MUSSAFAH GAS OIL PIPLINE | Scraper RECEIVER RUWAIS-MUSSAFAH GAS OIL PIPLINE |  | PIPING | M410MISC | 3 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270478 | M410PLR001 | Scraper RECEIVER RUWAIS-MUSSAFAH JET A1 PIPLINE | Scraper RECEIVER RUWAIS-MUSSAFAH JET A1 PIPLINE |  | PIPING | M410MISC | 3 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270479 | M410YYIS400 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR001 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270480 | M410YYIS401 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR001 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270481 | M410YYIS402 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR002 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270482 | M410YYIS403 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR002 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270483 | M410YYIS404 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR005 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270484 | M410YYIS405 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR005 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270485 | M410YYIS406 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR006 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270486 | M410YYIS407 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR006 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270487 | M410YYIS408 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR003 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270488 | M410YYIS409 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR003 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270489 | M410YYIS412 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR007 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270490 | M410YYIS413 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | M410PLR007 | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270491 | M410P003A | SEAL FLUSHING SYSTEM | AL AIN GAS OIL BOOSTER PUMP | 969269204 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270492 | M410P003B | SEAL FLUSHING SYSTEM | AL AIN GAS OIL BOOSTER PUMP | 969269205 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270493 | M410P023A | SEAL FLUSHING SYSTEM | AL DHAFRA JP-8 BOOSTER PUMP. | 969269206 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270494 | M410P023B | SEAL FLUSHING SYSTEM | AL DHAFRA JP-8 BOOSTER PUMP. | 969269207 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270495 | M410P023C | SEAL FLUSHING SYSTEM | AL DHAFRA JP-8 BOOSTER PUMP. | 969269208 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270496 | M410P040A | SEAL FLUSHING SYSTEM | ANTI FREEZE CHEMICAL OFFLOADING PUMP-A | 969269209 | SYSTEM | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P040A-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969270497 | M410P040B | SEAL FLUSHING SYSTEM | ANTI FREEZE CHEMICAL OFFLOADING PUMP-B | 969269210 | SYSTEM | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P040B-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969270498 | M410P001A | SEAL FLUSHING SYSTEM | AL AIN ULG BOOSTER PUMP | 969269211 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270499 | M410P001B | SEAL FLUSHING SYSTEM | AL AIN ULG BOOSTER PUMP | 969269212 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270500 | M410P002A | SEAL SYSTEM(DE) FOR 410-P-002A | AL AIN ULG MAIN LINE PUMP | 969269213 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270501 | M410P002B | SEAL SYSTEM(DE) FOR 410-P-002B | AL AIN ULG MAIN LINE PUMP | 969269214 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270502 | M410P004A | SEAL SYSTEM(DE) FOR 410-P-004A | AL AIN GAS OIL MAIN LINE PUMP | 969269215 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270503 | M410P004B | SEAL SYSTEM(DE) FOR 410-P-004B | AL AIN GAS OIL MAIN LINE PUMP | 969269216 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270504 | M410P005A | SEAL SYSTEM(DE) FOR 410-P-005A | ADIA NORTH JET A1 BOOSTER PUMP. | 969269217 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270505 | M410P005B | SEAL SYSTEM(DE) FOR 410-P-005A | ADIA NORTH JET A1 BOOSTER PUMP. | 969269218 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270506 | M410P005C | SEAL SYSTEM(DE) FOR 410-P-005C | ADIA NORTH JET A1 BOOSTER PUMP. | 969269219 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270507 | M410P006A | SEAL SYSTEM(DE) FOR 410-P-006A | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269220 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270508 | M410P006B | SEAL SYSTEM(DE) FOR 410-P-006A | ADIA NORTH JET A1 MAIN LINE PUMP | 969269221 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270509 | M410P006C | SEAL SYSTEM(DE) FOR 410-P-006C | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269222 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270510 | M410P024A | SEAL SYSTEM(DE) FOR 410-P-024A | AL DHAFRA JP-8 MAIN LINE PUMP | 969269223 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270511 | M410P024B | SEAL SYSTEM(DE) FOR 410-P-024B | AL DHAFRA JP-8 MAIN LINE PUMP | 969269224 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270512 | M410P024C | SEAL SYSTEM(DE) FOR 410-P-024C | AL DHAFRA JP-8 MAIN LINE PUMP | 969269225 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270513 | M410P002A | SEAL SYSTEM(NDE) FOR 410-P-002A | AL AIN ULG MAIN LINE PUMP | 969269213 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270514 | M410P002B | SEAL SYSTEM(NDE) FOR 410-P-002B | AL AIN ULG MAIN LINE PUMP | 969269214 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270515 | M410P004A | SEAL SYSTEM(NDE) FOR 410-P-004A | AL AIN GAS OIL MAIN LINE PUMP | 969269215 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270516 | M410P004B | SEAL SYSTEM(NDE) FOR 410-P-004B | AL AIN GAS OIL MAIN LINE PUMP | 969269216 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270517 | M410P005A | SEAL SYSTEM(NDE) FOR 410-P-005A | ADIA NORTH JET A1 BOOSTER PUMP. | 969269217 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270518 | M410P005B | SEAL SYSTEM(NDE) FOR 410-P-005A | ADIA NORTH JET A1 BOOSTER PUMP. | 969269218 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205046 | M410MOV0101 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175550 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0101-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205047 | M410MOV0102 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175551 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0102-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205048 | M410MOV0103 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175552 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0103-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205049 | M410MOV0104 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175553 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0104-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205050 | M410MOV0105 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175554 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0105-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205051 | M410MOV0106 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175555 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0106-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205052 | M410MOV0107 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175556 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0107-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205053 | M410MOV0108 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175557 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0108-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
VHC37111 | UTOYOTA57204 | 6 / 57204 TOYOTA HILUX PICK-UP (MAINT. DEPT). | TOYOTA HILUX PICK-UP 6 / 57204 (MAINT. DEPT). |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA57204-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 01/08/18 | MM-PM-029-M1
VHC37114 | UTOYOTA51163 | 6 / 51163 TOYOTA HILUX PICK-UP (MM1 / MP1 - MECH. SUPVR.). | TOYOTA HILUX PICK-UP 6 / 51163 (MP1 / MM1 - MECH. SUPVR.). |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA51163-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 08/08/18 | MM-PM-029-M1
969270403 | M410PT306 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P004B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT306-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270404 | M410PT313 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P005A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT313-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270405 | M410PT314 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P005A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT314-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270406 | M410PT315 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P005B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT315-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270407 | M410PT316 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P005B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT316-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270408 | M410PT325 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT325-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270409 | M410PT326 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT326-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270410 | M410PT327 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT327-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270411 | M410PT328 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT328-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270412 | M410PT336 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P023A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT336-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270413 | M410PT337 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P023A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT337-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270414 | M410PT338 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P023B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT338-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270415 | M410PT339 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P023B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT339-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270416 | M410PT340 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P023C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT340-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270417 | M410PT341 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P023C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT341-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270418 | M410PT372 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P024A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT372-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270419 | M410PT373 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P024A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT373-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270420 | M410PT374 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P024B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT374-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270421 | M410PT375 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P024B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT375-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270422 | M410PT376 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P024C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT376-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270423 | M410PT377 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P024C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT377-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270424 | M410PT394 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT394-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270425 | M410PT395 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P006C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT395-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270426 | M410PT397 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P005C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT397-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270427 | M410PT398 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410P005C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT398-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270428 | M410PT400 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT400-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270429 | M410PT401 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT401-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270430 | M410PT402A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT402A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270431 | M410PT402B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT402B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270432 | M410PT404A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT404A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270433 | M410PT404B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT404B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270434 | M410PT404C | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT404C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270435 | M410PT412 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT412-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270436 | M410PT413A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PT412 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT413A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270437 | M410PT413B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PT412 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT413B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270438 | M410PT414 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PT412 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT414-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270439 | M410PT416A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PT412 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT416A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270440 | M410PT416B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PT412 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT416B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270441 | M410PT416C | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PT412 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT416C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270442 | M410PT424 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR005 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT424-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969271722 | M410JAR001 | GLASS JAR, ASME 150LB | GLASS JAR, ASME 150LB |  | LAB_EQP | M410LAB | 3 | LAB_EQP | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271723 | M410JAR002 | GLASS JAR, ASME 150LB | GLASS JAR, ASME 150LB |  | LAB_EQP | M410LAB | 3 | LAB_EQP | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271724 | M410JAR003 | GLASS JAR, ASME 150LB | GLASS JAR, ASME 150LB |  | LAB_EQP | M410LAB | 3 | LAB_EQP | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271725 | M410STR001A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271726 | M410STR001B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271727 | M410STR002A | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175922 | M410LT023A | ULG 91 TANK 410-T-002 | SAAB ROSEMOUNT ULG 91 TANK 410-T-002 |  | LVL_TX | M410T002 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935719 | M400DCP001 | PANEL CONTROL | IPCS, CUBICAL |  | PA_SYS | M400SYS | 1 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935720 | M400DCP002 | PANEL, CONTROL, 230VAC | IPCS, COMMUNICATION BOX |  | PA_SYS | M400SYS | 1 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935721 | M400DCP003 | PANEL CONTROL | IPCS, CUBICAL |  | PA_SYS | M400SYS | 1 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935722 | M400MMS001 | SWITCHGEAR | SWITCHGEAR, 11000 VOLT |  | SWBOARD | M400SCB | 2 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935723 | M400MS001 | SWITCHGEAR | SWITCHGEAR, 11000 VOLT |  | SWBOARD | M400SCB | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936065 | M400P016A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 4.500/4.750" , SILICON CARBIDE , 316 SS , F | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP | 935826 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 04/10/18 | MM-PM-002-M6
936066 | M400P016A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 4.500/4.750" , SILICON CARBIDE , 316 SS , F | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP | 935826 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 04/10/18 | MM-PM-002-M6
936067 | M400P018B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.125"/3.375" , CARBON , 316 SS , FLUOROELA | JET A1 MAIN LINE PUMP-B TO ADIA. | 935829 | PUMPS | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | M400P018BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/11/18 | MM-PM-005-M6
936068 | M400P018A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.125/3.375" , SILICON CARBIDE , 316 SS , F | JET A1 MAIN LINE PUMP-A TO ADIA. | 935828 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P018AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-005-M6
936069 | M400P018A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.125/3.375" , SILICON CARBIDE , 316 SS , F | JET A1 MAIN LINE PUMP-A TO ADIA. | 935828 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P018AMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-005-M6
936070 | M400P016B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 4.500/4.750" , SILICON CARBIDE , 316 SS , F | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP | 935827 | PUMPS | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-002-M6
936071 | M400P016B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 4.500/4.750" , SILICON CARBIDE , 316 SS , F | ULG95/ULG98/GAS OIL/JET A1/KEROSENE MAIN LINE PUMP | 935827 | PUMPS | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P016BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-002-M6
936072 | M400P018B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.125/3.375" , SILICON CARBIDE , 316 SS , F | JET A1 MAIN LINE PUMP-B TO ADIA. | 935829 | PUMPS | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | M400P018BMM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/11/18 | MM-PM-005-M6
936073 | M400P019 | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 5.000/5.250" , SILICON CARBIDE , 316 SS , F | OFF SPEC JET A1 MAIN LINE PUMP TO RUWAIS. | 935830 | PUMPS | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P019MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-001-M6
936074 | M400P019 | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 5.000/5.250" , SILICON CARBIDE , 316 SS , F | OFF SPEC JET A1 MAIN LINE PUMP TO RUWAIS. | 935830 | PUMPS | M400PUMP | 3 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P019MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-001-M6
969147466 | M410P031A | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) |  | PUCE | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 1 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P031A-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147467 | M410P031B | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) |  | PUCE | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 1 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P031B-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147468 | M410P031C | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) |  | PUCE | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 1 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P031C-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147469 | M410P031D | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) |  | PUCE | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P031D-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147470 | M410P031E | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) |  | PUCE | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P031E-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147471 | M410P031F | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) |  | PUCE | M410PUMP | 3 | CEDEFF | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P031F-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147472 | M410P031G | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) |  | PUCE | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P031G-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147473 | M410P032A | FIRE WATER PUMP- MOTOR DRIVEN (2 DUTY) | FIRE WATER PUMP- MOTOR DRIVEN(2 DUTY) |  | PUCE | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P032A-MM1 | ACTIVE | MECH | PM | FT | 2 | WEEKS | 05/08/18 | MM-PM-026-W1
969147474 | M410P032B | FIRE WATER PUMP- MOTOR DRIVEN (2 DUTY) | FIRE WATER PUMP- MOTOR DRIVEN(2 DUTY) |  | PUCE | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P032B-MM1 | ACTIVE | MECH | PM | FT | 2 | WEEKS | 05/08/18 | MM-PM-026-W1
969147475 | M410P033A | FIRE WATER JOCKEY CENTRIFUGAL PUMP. | JOCKEY PUMP ELECTRIC MOTOR DRIVEN |  | PUCE | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P033A-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 25/11/18 | MC-PM-02-M6
969147476 | M410P033B | FIRE WATER JOCKEY CENTRIFUGAL PUMP. | JOCKEY PUMP ELECTRIC MOTOR DRIVEN |  | PUCE | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M410P033B-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 28/11/18 | MC-PM-02-M6
969175401 | M410EPB001 | IRP-2 Emergency Generator | Emergency Generator |  | GENRATOR | M410MOTOR | 1 | GENRATOR | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 50 | 50 | 50 | 10 | 10 | 9.0969 | Very High | High | High | y | High Critical | Y | 0 | 12 | m | 0 | y | y | 0 | 0 | 0 | M410EPB001-ME1 | ACTIVE | ELEC | PM | EDS | 1 | WEEKS | 05/08/18 | ME-PM-006-W1
969269467 | M410COM1 | #1 IRON MAN DOMINATOR / MONITOR 10K GPM COMBO UNIT. BIG FLOW SYSTEM. | #1 IRON MAN COMBO UNIT DOMINATOR / MONITOR WITH BOOSTER PUMP-10K GPM. BIG FLOW SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269453 | M410HOS1 | #1 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. BIG FLOW SYSTEM. | #1 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL PODS 1/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269454 | M410HOS2 | #2 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. BIG FLOW SYSTEM. | #2 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL PODS 2/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485991 | M410FLP2 | FLOATING PUMP#2 FOR NEPTUNE #1, 5K GPM FROM THE SEA. BIG FLOW SYSTEM. | HYDRAULIC DRIVE FLOATING PUMP #2, USED WITH THE NEPTUNE UNITS, BIG FLOW FIRE FIGHTING SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936422 | M400POV537 | VALVE, SEQUENTIAL CONTROL / ESD, 10" X 600 | ESD VALVE AT NAPHTHA/REFORMATE P/L TO 400-L-003A/B |  |  | M400VALVE | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936423 | M400POV571 | ACTUATOR FOR SEQUENCIAL CONTROL/ESD VALVE | ESD VALVE -NAPHTHA/REFORMATE P/L (OFF SPEC JET A1) |  |  | M400VALVE | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175834 | M410TSV062 | JET A1 TANK 410-T-014 INLET MANIFOLD | JET A1 TANK 410-T-014 INLET MANIFOLD |  | PSV | M410T014 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175835 | M410TSV063 | JET A1 TANK 410-T-014 INLET MANIFOLD | JET A1 TANK 410-T-014 INLET MANIFOLD |  | PSV | M410T014 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175836 | M410TSV064 | JET A1 TANK 410-T-014 OUTLET MANIFOLD | JET A1 TANK 410-T-014 OUTLET MANIFOLD |  | PSV | M410T014 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175837 | M410TSV065 | JET A1 TANK 410-T-014 OUTLET MANIFOLD | JET A1 TANK 410-T-014 OUTLET MANIFOLD |  | PSV | M410T014 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175838 | M410TSV066 | JET A1 TANK 410-T-015 INLET MANIFOLD | JET A1 TANK 410-T-015 INLET MANIFOLD |  | PSV | M410T015 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175839 | M410TSV067 | JET A1 TANK 410-T-015 INLET MANIFOLD | JET A1 TANK 410-T-015 INLET MANIFOLD |  | PSV | M410T015 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175840 | M410TSV068 | JET A1 TANK 410-T-015 OUTLET MANIFOLD | JET A1 TANK 410-T-015 OUTLET MANIFOLD |  | PSV | M410T015 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175841 | M410TSV069 | JET A1 TANK 410-T-015 OUTLET MANIFOLD | JET A1 TANK 410-T-015 OUTLET MANIFOLD |  | PSV | M410T015 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175842 | M410TSV070 | JET A1 TANK 410-T-016 INLET MANIFOLD | JET A1 TANK 410-T-016 INLET MANIFOLD |  | PSV | M410T016 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175843 | M410TSV071 | JET A1 TANK 410-T-016 INLET MANIFOLD | JET A1 TANK 410-T-016 INLET MANIFOLD |  | PSV | M410T016 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175844 | M410TSV072 | JET A1 TANK 410-T-016 OUTLET MANIFOLD | JET A1 TANK 410-T-016 OUTLET MANIFOLD |  | PSV | M410T016 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175845 | M410TSV073 | JET A1 TANK 410-T-016 OUTLET MANIFOLD | JET A1 TANK 410-T-016 OUTLET MANIFOLD SOUTH OF 400T116. |  | PSV | M410T016 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175846 | M410TSV074 | ULG 91 TANK 410-T-001 INLET MANIFOLD | ULG 91 TANK 410-T-001 INLET MANIFOLD |  | PSV | M410T001 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175847 | M410TSV075 | ULG 91 TANK 410-T-002 INLET MANIFOLD | ULG 91 TANK 410-T-002 INLET MANIFOLD |  | PSV | M410T002 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175848 | M410TSV076 | ULG 91 TANK 410-T-003 INLET MANIFOLD | ULG 91 TANK 410-T-003 INLET MANIFOLD |  | PSV | M410T003 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175849 | M410TSV077 | ULG 91 TANK 410-T-004 INLET MANIFOLD | ULG 91 TANK 410-T-004 INLET MANIFOLD |  | PSV | M410T004 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175850 | M410TSV078 | ULG 91 TANK 410-T-005 INLET MANIFOLD | ULG 91 TANK 410-T-005 INLET MANIFOLD |  | PSV | M410T005 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175851 | M410TSV079 | ULG 91 TANK 410-T-006 INLET MANIFOLD | ULG 91 TANK 410-T-006 INLET MANIFOLD |  | PSV | M410T006 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175852 | M410TSV080 | ULG 91 TANK 410-T-007 INLET MANIFOLD | ULG 91 TANK 410-T-007 INLET MANIFOLD |  | PSV | M410T007 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175853 | M410TSV081 | ULG 91 TANK 410-T-008 INLET MANIFOLD | ULG 91 TANK 410-T-008 INLET MANIFOLD |  | PSV | M410T008 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175854 | M410TSV082 | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175855 | M410TSV083 | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C SUCTION HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175856 | M410TSV084 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A PUMP SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A PUMP SUCTION HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175857 | M410TSV085 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B PUMP SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B PUMP SUCTION HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175858 | M410TSV086 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C PUMP SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C PUMP SUCTION HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175859 | M410TSV087 | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175860 | M410TSV088 | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER | ULG 91/95 INTER-TANK TRANSFER PUMPS 410-P-007A/B/C DISCHARGE HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175861 | M410TSV093 | ULG 91/95 TIE-IN'S FROM EXISTING MULTI PRODUCT MANIFOLD | ULG 91/95 TIE-IN'S FROM EXISTING MULTI PRODUCT MANIFOLD |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175862 | M410TSV094 | ULG 91/95 TIE-IN'S FROM EXISTING MULTI PRODUCT MANIFOLD | ULG 91/95 TIE-IN'S FROM EXISTING MULTI PRODUCT MANIFOLD |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175863 | M410TSV095 | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008A PUMP SUCTION HEADER | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008A PUMP SUCTION HEADER NORTH OF 400T114. |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175864 | M410TSV096 | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008B PUMP SUCTION HEADER | GAS OIL INTER-TANK TRANSFER PUMPS 410-P-008B PUMP SUCTION HEADER |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175865 | M410TSV097 | VALVE,SAFETY RELIEF, CONVENTIONAL, JET A1, 3/4" X 1", 4.5 KG/CM2, ATM, ANSI150RF, ASTMA216GR WCB, ASTMA182GR F316, SWPA (AL META) | JET A1 INTER-TANK TRANSFER PUMPS 410-P-014A PUMP SUCTION HEADER |  | PSV | M410T014 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175866 | M410TSV098 | JET A1 INTER-TANK TRANSFER PUMPS 410-P-014B PUMP SUCTION HEADER | JET A1 INTER-TANK TRANSFER PUMPS 410-P-014B PUMP SUCTION HEADER |  | PSV | M410T014 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175867 | M410TSV100 | ULG 95 TANKS 410-T-005 TO 410-T-008 | ULG 95 TANKS 410-T-005 TO 410-T-008 |  | PSV | M410T008 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 |  | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175868 | M410TSV101 | ULG 91 TANKS 410-T-001 TO 410-T-004 | ULG 91 TANKS 410-T-001 TO 410-T-004 |  | PSV | M410T008 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175869 | M410TSV103 | JET A1 TANKS 410-T-011 TO 410-T-016 | JET A1 TANKS 410-T-011 TO 410-T-016 |  | PSV | M410T016 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175870 | M410TSV104 | GAS OIL TANKS 410-T-009/010 | GAS OIL TANKS 410-T-009/010 |  | PSV | M410T009 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175871 | M410TSV105 | JET A1 TANKS 410-T-011 TO 410-T-016 | JET A1 TANKS 410-T-011 TO 410-T-016 |  | PSV | M410T011 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175872 | M410TSV106 | JET A1 ADIA BOOSTER PUMPS 410-P-005A/B | JET A1 ADIA BOOSTER PUMPS 410-P-005A/B |  | PUCE | M410VALVE | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281263 | M410TEL001 | SDH/ACS SHARED CABINET | Telephone (Outdoor) | 969195420 | BLDGS | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278559 | M400DCSMC005 | CABINET | PLCR DCS MARSHALLING CABINET | 969195553 | DCS_PNL | M400SYS | 3 | DCS_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278562 | M410ASP0011 | PANEL | Substation Alarm Annunciator Panel | 969195406 | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278574 | PL312CCTV001 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278575 | PL312CCTV002 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278576 | PL312CCTV003 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278577 | PL312CCTV004 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278578 | PL312CCTV005 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278579 | PL312CCTV006 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278580 | PL312CCTV007 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278581 | PL312CCTV009 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278582 | PL312CCTV010 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278583 | PL312CCTV011 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278584 | PL312CCTV012 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278585 | PL312CCTV013 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278586 | PL312CCTV014 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278587 | PL312CCTV015 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278588 | PL312CCTV016 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278589 | PL312CCTV017 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278590 | PL312CCTV018 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278560 | M400DCSSRC001 | CABINET | PLCR NETWORK/SERVER CABINET | 969195555 |  | M400SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278563 | M410ASP0012 | PANEL | Substation Alarm Annunciator Panel | 969195407 | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278564 | M410PDB001 | CABINET | POWER DISTRIBUTION BOARD CABINET FOR SIS-001DCSSYSTEM | 969195633 | SWBOARD | M410SCB | 3 | SWBOARD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PDB001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 20/10/18 | ME-PNL1-PM-M6
969278573 | PL100TEL001 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL100MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265962 | PL100TSV401 | THERMAL RELIEF VALVE, 3/4" 300# X 1" 150# RF, SET PR:31KG/CM2G | THERMAL RELIEF VALVE |  | PSV | PL100VALVE | 3 | PSV | 616101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265963 | PL100TSV402 | THERMAL RELIEF VALVE, 3/4" 300# X 1" 150# RF, SET PR:31KG/CM2G | THERMAL RELIEF VALVE |  | PSV | PL100VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265964 | PL100TSV403 | THERMAL RELIEF VALVE, 3/4" 300# X 1" 150# RF, SET PR:31KG/CM2G | THERMAL RELIEF VALVE |  | PSV | PL100VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265965 | PL100TSV404 | THERMAL RELIEF VALVE, 3/4" 300# X 1" 150# RF, SET PR:10KG/CM2G | THERMAL RELIEF VALVE |  | PSV | PL100VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265966 | PL100TSV405A | THERMAL RELIEF VALVE, 3/4" 300# X 1" 150# RF, SET PR:18KG/CM2G | THERMAL RELIEF VALVE |  | PSV | PL100VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265967 | PL100TSV405B | THERMAL RELIEF VALVE, 3/4" 300# X 1" 150# RF, SET PR:18KG/CM2G | THERMAL RELIEF VALVE |  | PSV | PL100VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265969 | PL100TT400 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL100TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265970 | PL100TT400A | Temperature Transemitter | Temperature Transemitter |  | TEMP_TX | PL100TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265971 | PL100TT400B | Temperature Transemitter | Temperature Transemitter |  | TEMP_TX | PL100TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265972 | PL100TT401 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL100TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265973 | PL100UPSAC001A | 240V AC UPS-1A | 240V AC UPS-1A |  | INVRT_UP | PL100BATT | 3 | INVRT_UP | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265974 | PL100UPSAC001B | 240V AC UPS-1B | 240V AC UPS-1B |  | INVRT_UP | PL100BATT | 3 | INVRT_UP | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265975 | PL100UPSACPDB001 | PDB for 240V AC UPS | PDB for 240V AC UPS |  | SWBOARD | PL100SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265976 | PL100V001 | GAS OIL SUMP VESSEL | GAS OIL SUMP VESSEL |  | VESSEL | PL100VESSEL | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265977 | PL100XA620 | AUDIBLE HAZARD ALARM | AUDIBLE HAZARD ALARM |  | ALARMANC | PL100ALRM | 3 | ALARMANC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265978 | PL100XAC620 | MANUAL ALARM CALL POINT-Field | MANUAL ALARM CALL POINT-Field |  | PA_SYS | PL100TELM | 3 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265979 | PL100XGH630 | GAS DETECTORS | GAS DETECTORS |  | FG_DET | PL100GD | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265980 | PL100XHE630 | HEAT DETECTOR | HEAT DETECTOR |  | FG_DET | PL100GD | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265981 | PL100XLF620 | RED FLASHING BEACON | RED FLASHING BEACON |  | ALARMANC | PL100ALRM | 3 | ALARMANC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265982 | PL100XLG620 | BLU FLASHING BEACON | BLU FLASHING BEACON |  | ALARMANC | PL100ALRM | 3 | ALARMANC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265983 | PL100XSP630 | SSH DETECTORr level) (SSH photo sensor 4098-9714) | SSH DETECTORr level) (SSH photo sensor 4098-9714) |  | FG_DET | PL100GD | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265984 | PL100XSP641A | REMOTE ALARM INDICATOR | REMOTE ALARM INDICATOR |  | ALARMANC | PL100ALRM | 3 | ALARMANC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265985 | PL100YYIS400 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | PL100MISC | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265986 | PL100YYIS401 | SCRAPER SIGNALLER | SCRAPER SIGNALLER |  | PIPING | PL100MISC | 2 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 100 | 5 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265987 | PL311CCTV001 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Explosion Proof PTZ | CAMERA OF CCTV (SHOWEIHAT) Explosion Proof PTZ |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265988 | PL311CCTV002 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Explosion Proof PTZ | CAMERA OF CCTV (SHOWEIHAT) Explosion Proof PTZ |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265989 | PL311CCTV003 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (25mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (25mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265990 | PL311CCTV004 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (50mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265991 | PL311CCTV005 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265992 | PL311CCTV006 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265993 | PL311CCTV007 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265994 | PL311CCTV008 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (25mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (25mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265995 | PL311CCTV009 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265996 | PL311CCTV010 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265997 | PL311CCTV011 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265998 | PL311CCTV012 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265999 | PL311CCTV013 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266000 | PL311CCTV014 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (50mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266001 | PL311CCTV015 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (50mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266002 | PL311CCTV016 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (50mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266003 | PL311CCTV017 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA OF CCTV (SHOWEIHAT) Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266004 | PL311CCTV018 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (50mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266005 | PL311CCTV019 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (50mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266006 | PL311CCTV020 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (25mm) | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (25mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266007 | PL311CCTV021 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA OF CCTV (SHOWEIHAT) Short range Thermal Fixed (50mm) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266008 | PL311CCTV022 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Explosion Proof PTZ | CAMERA OF CCTV (SHOWEIHAT) Explosion Proof PTZ |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969266009 | PL311CCTV023 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Explosion Proof PTZ | CAMERA OF CCTV (SHOWEIHAT) Explosion Proof PTZ |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278591 | PL312CCTV019 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265883 | PL100BPD2001 | BLAST DRAFT DAMPER | BLAST DRAFT DAMPER |  | PACKAGE | PL100MISC | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265858 | PL100EOV403 | VALVE,CONTROL, BALL, 16", CLASS 300, RF FLG 16 in CL300, A216 WCB, A564 Tp. 630 - H1150D, SS316+GRAPHITE PACKING, ElectroHydraulic, 990.8 mm | ELECTRO HYDRAULIC VALVE, GAS OIL TO BASKET FILTERS & METERING |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | SHWEIHAT TERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265884 | PL100EOV403 | Actuator for ELECTRO HYDRAULIC VALVE | ELECTRO HYDRAULIC VALVE, GAS OIL TO BASKET FILTERS & METERING | 969265858 | CNTR_VLV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | SHWEIHAT TERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265859 | PL100ESD001 | ESD SYSTEM CABINET | ESD SYSTEM CABINET |  | BLDGS | PL100MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265887 | PL100FACP620 | FIRE ALARM PANEL | FIRE ALARM PANEL |  | F&G_PNL | PL100MISC | 3 | F&G_PNL | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265888 | PL100FD620 | FLAME DETECTOR UV/IR type | FLAME DETECTOR UV/IR type |  | FGBFFD | PL100GD | 3 | FGBFFD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265889 | PL100FHL2150 | FIXTURE HID LIGHT | FIXTURE HID LIGHT |  | LIGHT | PL100SCB | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265890 | PL100FS2031 | PRESSURE SWITCH (EX-PROOF) | PRESSURE SWITCH (EX-PROOF) |  | PRES_SWT | PL100PRESS | 3 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265891 | PL100FS2032 | PRESSURE SWITCH (EX-PROOF) | PRESSURE SWITCH (EX-PROOF) |  | PRES_SWT | PL100PRESS | 3 | PRES_SWT | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265893 | PL100FT400A | Custody Transfer Metering System (Flow Meter) | Custody Transfer Metering System (Flow Meter) |  | FL_MTR | PL100FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265894 | PL100FT400B | Custody Transfer Metering System(Flow Meter) | Custody Transfer Metering System(Flow Meter) |  | FL_MTR | PL100FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969527927 | M410FD675 | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR AIR ELIMINITOR 410-FT-400 |  | FGBFFD | M410FGSC001 | [12 empty] | Non Critical |  | High Critical | Y | High Critical | Y |  | 6 | g
969512659 | SD-MSFH-PI1 | HP Prodesk 600 G1 | PRODUCTION PLANNING |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512660 | SCD-DANILO | HP Prodesk 600 G1 | DANILO ACERO UMBINA |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512695 | SD-MSFH-KHALID | HP Prodesk 600 G1 | MILIND NAVSALKAR |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512696 | A-PROD-PLANNING | HP Prodesk 600 G1 | Production Planing |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512697 | SDHASAN1 | HP Prodesk 600 G1 | HASSAN M.AL JAHWARI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512698 | SD-MSFH-P12 | Lenovo - M5498-PS4 | Planing - Hasan Al Jahwari |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512699 | A-MSFH-SIVA | Lenovo - M7491 | IBM LENOVO |  |  | P&T_WAREHOUSE | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512700 | A-MSH-POOL100 | Dell - Optiplex 755 | Control - Warehouse |  |  | P&T_WAREHOUSE | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512701 | A-MSH-WPOOL | Dell - Optiplex 755 | VENKETESWARA |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512708 | SDCONF1 | Lenovo - M2999-A34 | MAJED AHMED AL WAHEDIT |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512712 | A-MSFH-INSP | Lenovo - M2999-A34 | AFTAB FAKHRUDDIN KHAN |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512720 | A-MSFH-FS | Dell Optiplex 9020 | P&T SAFTY SUPERVISOR |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175238 | M410RO768 | WATER SPRAY FOR 410-T-005FROM 410-STR-768 TO 410-PG-768 | WATER SPRAY FOR 410-T-005FROM 410-STR-768 TO 410-PG-768 |  | ORIFICE | M410T005 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175239 | M410RO769 | WATER SPRAY FOR 410-T-005FROM 410-STR-769 TO 410-PG-769 | WATER SPRAY FOR 410-T-005FROM 410-STR-769 TO 410-PG-769 |  | ORIFICE | M410T005 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175240 | M410RO770 | WATER SPRAY FOR 410-T-005FROM 410-STR-770 TO 410-PG-770 | WATER SPRAY FOR 410-T-005FROM 410-STR-770 TO 410-PG-770 |  | ORIFICE | M410T005 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175241 | M410RO771 | WATER SPRAY FOR 410-T-005FROM 410-STR-771 TO 410-PG-771 | WATER SPRAY FOR 410-T-005FROM 410-STR-771 TO 410-PG-771 |  | ORIFICE | M410T005 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175242 | M410RO772 | WATER SPRAY FOR 410-T-006FROM 410-STR-772 TO 410-PG-772 | WATER SPRAY FOR 410-T-006FROM 410-STR-772 TO 410-PG-772 |  | ORIFICE | M410T006 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175243 | M410RO773 | WATER SPRAY FOR 410-T-006FROM 410-STR-773 TO 410-PG-773 | WATER SPRAY FOR 410-T-006FROM 410-STR-773 TO 410-PG-773 |  | ORIFICE | M410T006 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175244 | M410RO774 | WATER SPRAY FOR 410-T-006FROM 410-STR-774 TO 410-PG-774 | WATER SPRAY FOR 410-T-006FROM 410-STR-774 TO 410-PG-774 |  | ORIFICE | M410T006 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175245 | M410RO775 | WATER SPRAY FOR 410-T-006FROM 410-STR-775 TO 410-PG-775 | WATER SPRAY FOR 410-T-006FROM 410-STR-775 TO 410-PG-775 |  | ORIFICE | M410T006 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175246 | M410RO776 | WATER SPRAY FOR 410-T-007FROM 410-STR-776 TO 410-PG-776 | WATER SPRAY FOR 410-T-007FROM 410-STR-776 TO 410-PG-776 |  | ORIFICE | M410T007 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175247 | M410RO777 | WATER SPRAY FOR 410-T-007FROM 410-STR-777 TO 410-PG-777 | WATER SPRAY FOR 410-T-007FROM 410-STR-777 TO 410-PG-777 |  | ORIFICE | M410T007 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175248 | M410RO778 | WATER SPRAY FOR 410-T-007FROM 410-STR-778 TO 410-PG-778 | WATER SPRAY FOR 410-T-007FROM 410-STR-778 TO 410-PG-778 |  | ORIFICE | M410T007 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175249 | M410RO779 | WATER SPRAY FOR 410-T-007FROM 410-STR-779 TO 410-PG-779 | WATER SPRAY FOR 410-T-007FROM 410-STR-779 TO 410-PG-779 |  | ORIFICE | M410T007 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175250 | M410RO780 | WATER SPRAY FOR 410-T-008FROM 410-STR-780 TO 410-PG-780 | WATER SPRAY FOR 410-T-008FROM 410-STR-780 TO 410-PG-780 |  | ORIFICE | M410T008 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175251 | M410RO781 | WATER SPRAY FOR 410-T-008FROM 410-STR-781 TO 410-PG-781 | WATER SPRAY FOR 410-T-008FROM 410-STR-781 TO 410-PG-781 |  | ORIFICE | M410T008 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175252 | M410RO782 | WATER SPRAY FOR 410-T-008FROM 410-STR-782 TO 410-PG-782 | WATER SPRAY FOR 410-T-008FROM 410-STR-782 TO 410-PG-782 |  | ORIFICE | M410T008 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175253 | M410RO783 | WATER SPRAY FOR 410-T-008FROM 410-STR-783 TO 410-PG-783 | WATER SPRAY FOR 410-T-008FROM 410-STR-783 TO 410-PG-783 |  | ORIFICE | M410T008 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175254 | M410RO784 | WATER SPRAY FOR 410-T-001FROM 410-STR-784 TO 410-PG-784 | WATER SPRAY FOR 410-T-001FROM 410-STR-784 TO 410-PG-784 |  | ORIFICE | M410T001 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175255 | M410RO785 | WATER SPRAY FOR 410-T-001FROM 410-STR-785 TO 410-PG-785 | WATER SPRAY FOR 410-T-001FROM 410-STR-785 TO 410-PG-785 |  | ORIFICE | M410T001 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175256 | M410RO786 | WATER SPRAY FOR 410-T-001FROM 410-STR-786 TO 410-PG-786 | WATER SPRAY FOR 410-T-001FROM 410-STR-786 TO 410-PG-786 |  | ORIFICE | M410T001 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175257 | M410RO787 | WATER SPRAY FOR 410-T-001FROM 410-STR-787 TO 410-PG-787 | WATER SPRAY FOR 410-T-001FROM 410-STR-787 TO 410-PG-787 |  | ORIFICE | M410T001 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175258 | M410RO788 | WATER SPRAY FOR 410-T-002FROM 410-STR-788 TO 410-PG-788 | WATER SPRAY FOR 410-T-002FROM 410-STR-788 TO 410-PG-788 |  | ORIFICE | M410T002 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175259 | M410RO789 | WATER SPRAY FOR 410-T-002FROM 410-STR-789 TO 410-PG-789 | WATER SPRAY FOR 410-T-002FROM 410-STR-789 TO 410-PG-789 |  | ORIFICE | M410T002 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175260 | M410RO790 | WATER SPRAY FOR 410-T-002FROM 410-STR-790 TO 410-PG-790 | WATER SPRAY FOR 410-T-002FROM 410-STR-790 TO 410-PG-790 |  | ORIFICE | M410T002 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175261 | M410RO791 | WATER SPRAY FOR 410-T-002FROM 410-STR-791 TO 410-PG-791 | WATER SPRAY FOR 410-T-002FROM 410-STR-791 TO 410-PG-791 |  | ORIFICE | M410T002 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175262 | M410RO792 | WATER SPRAY FOR 410-T-003FROM 410-STR-792 TO 410-PG-792 | WATER SPRAY FOR 410-T-003FROM 410-STR-792 TO 410-PG-792 |  | ORIFICE | M410T003 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175263 | M410RO793 | WATER SPRAY FOR 410-T-003FROM 410-STR-793 TO 410-PG-793 | WATER SPRAY FOR 410-T-003FROM 410-STR-793 TO 410-PG-793 |  | ORIFICE | M410T003 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175264 | M410RO794 | WATER SPRAY FOR 410-T-003FROM 410-STR-794 TO 410-PG-794 | WATER SPRAY FOR 410-T-003FROM 410-STR-794 TO 410-PG-794 |  | ORIFICE | M410T003 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175265 | M410RO795 | WATER SPRAY FOR 410-T-003FROM 410-STR-795 TO 410-PG-795 | WATER SPRAY FOR 410-T-003FROM 410-STR-795 TO 410-PG-795 |  | ORIFICE | M410T003 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175266 | M410RO796 | WATER SPRAY FOR 410-T-004FROM 410-STR-796 TO 410-PG-796 | WATER SPRAY FOR 410-T-004FROM 410-STR-796 TO 410-PG-796 |  | ORIFICE | M410T004 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175267 | M410RO797 | WATER SPRAY FOR 410-T-004FROM 410-STR-797 TO 410-PG-797 | WATER SPRAY FOR 410-T-004FROM 410-STR-797 TO 410-PG-797 |  | ORIFICE | M410T004 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175268 | M410RO798 | WATER SPRAY FOR 410-T-004FROM 410-STR-798 TO 410-PG-798 | WATER SPRAY FOR 410-T-004FROM 410-STR-798 TO 410-PG-798 |  | ORIFICE | M410T004 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175269 | M410RO799 | WATER SPRAY FOR 410-T-004FROM 410-STR-799 TO 410-PG-799 | WATER SPRAY FOR 410-T-004FROM 410-STR-799 TO 410-PG-799 |  | ORIFICE | M410T004 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175270 | M410RO800 | WATER SPRAY FOR 410-T-009FROM 410-STR-800 TO 410-PG-800 | WATER SPRAY FOR 410-T-009FROM 410-STR-800 TO 410-PG-800 |  | ORIFICE | M410T009 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175271 | M410RO801 | WATER SPRAY FOR 410-T-009FROM 410-STR-801 TO 410-PG-801 | WATER SPRAY FOR 410-T-009FROM 410-STR-801 TO 410-PG-801 |  | ORIFICE | M410T009 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175272 | M410RO802 | WATER SPRAY FOR 410-T-009FROM 410-STR-802 TO 410-PG-802 | WATER SPRAY FOR 410-T-009FROM 410-STR-802 TO 410-PG-802 |  | ORIFICE | M410T009 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175273 | M410RO803 | WATER SPRAY FOR 410-T-009FROM 410-STR-803 TO 410-PG-803 | WATER SPRAY FOR 410-T-009FROM 410-STR-803 TO 410-PG-803 |  | ORIFICE | M410T009 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175274 | M410RO804 | WATER SPRAY FOR 410-T-010FROM 410-STR-804 TO 410-PG-804 | WATER SPRAY FOR 410-T-010FROM 410-STR-804 TO 410-PG-804 |  | ORIFICE | M410T010 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175275 | M410RO805 | WATER SPRAY FOR 410-T-010FROM 410-STR-805 TO 410-PG-805 | WATER SPRAY FOR 410-T-010FROM 410-STR-805 TO 410-PG-805 |  | ORIFICE | M410T010 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175276 | M410RO806 | WATER SPRAY FOR 410-T-010FROM 410-STR-806 TO 410-PG-806 | WATER SPRAY FOR 410-T-010FROM 410-STR-806 TO 410-PG-806 |  | ORIFICE | M410T010 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353287 | M410MCC001B1 | INTERPOSING RELAY PANEL | INTERPOSING RELAY PANEL |  | SWBOARD | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410MCC001B1-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969353288 | M410MCC001A1 | INTERPOSING RELAY PANEL | INTERPOSING RELAY PANEL |  | SWBOARD | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410MCC001A1-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969351157 | M410K001A | GEAR ASSEMBLY FOR AIR COMPRESSOR | AIR COMPRESSOR | 969269355 | COMPRS | M410COMP | 3 | COMPRS | 617101-310600 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 2 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351158 | M410K001B | GEAR ASSEMBLY FOR AIR COMPRESSOR | AIR COMPRESSOR | 969269356 | COMPRS | M410COMP | 3 | COMPRS | 617101-310600 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 50 | 4.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351159 | M410AT761A | INSTRUMENT AIR DEW POINT TEMPERATURE METER | INSTRUMENT AIR DEW POINT TEMPERATURE ANALYSER. |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351160 | M410AT761B | INSTRUMENT AIR DEW POINT TEMPERATURE METER | INSTRUMENT AIR DEW POINT TEMPERATURE ANALYSER. |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351161 | M410PG663 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351162 | M410PG664 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351163 | M410XSOV761B | DOUBLE ACTING SOLENOID VALVE | DOUBLE ACTING SOLENOID VALVE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351164 | M410XSOV761A | DOUBLE ACTING SOLENOID VALVE | DOUBLE ACTING SOLENOID VALVE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351165 | M410XSOV762A | SINGLE ACTING SOLENOID VALVE | SINGLE ACTING SOLENOID VALVE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351166 | M410XSOV762B | SINGLE ACTING SOLENOID VALVE | SINGLE ACTING SOLENOID VALVE |  | SOL_VLV | M410CNTRVL | 3 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351167 | M410FV751A | CAPACITY CONTROL VALVE | CAPACITY CONTROL VALVE |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351168 | M410FV751B | CAPACITY CONTROL VALVE | CAPACITY CONTROL VALVE |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351171 | M410CV751A | 2-1/2" CHECK VALVE | 2-1/2" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351172 | M410CV752A | 1/2" CHECK VALVE | 1/2" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351173 | M410CV753A | 1" CHECK VALVE | 1" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351174 | M410CV754A | 1" CHECK VALVE | 1" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351175 | M410CV755A | 1/2" CHECK VALVE | 1/2" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351176 | M410CV751B | 2-1/2" CHECK VALVE | 2-1/2" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351177 | M410CV752B | 1/2" CHECK VALVE | 1/2" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351178 | M410CV753B | 1" CHECK VALVE | 1" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351179 | M410CV754B | 1" CHECK VALVE | 1" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351180 | M410CV755B | 1/2" CHECK VALVE | 1/2" CHECK VALVE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351181 | M410K091A | Rotor Assembly for 1st STAGE OF COMPRESSOR | 1ST STAGE OF COMPRESSOR FOR 410-K-001A AIR COMPRESSOR UNIT | 969269289 | COMPRS | M410K001A | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351182 | M410K091B | Rotor Assembly for 1st STAGE OF COMPRESSOR | 1ST STAGE OF COMPRESSOR FOR 410-K-001B AIR COMPRESSOR UNIT | 969269290 | COMPRS | M410K001B | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195334 | M410BAV2351018 | 16" TBV SS316 300#, RF, GEAR OPERATED | 16" TBV SS316 300#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195335 | M410BAV2351019 | 28" TBV SS316 300#, RF, GEAR OPERATED | 28" TBV SS316 300#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195336 | M410LI012 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195337 | M410LI022 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195338 | M410LI032 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195339 | M410LI042 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195340 | M410LI052 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195341 | M410LI062 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195342 | M410LI072 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195343 | M410LI082 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195344 | M410LI092 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195345 | M410LI102 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195346 | M410LI112 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195347 | M410LI122 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195348 | M410LI132 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195349 | M410LI142 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195350 | M410LI152 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195351 | M410LI162 | Local Level Indicator(Radar) | Local Level Indicator(Radar) |  | INDICATR | M410LEVEL | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195352 | M410PT011 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT011 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT011-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195353 | M410PT021 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT021 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT021-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195354 | M410PT031 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT031 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT031-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195355 | M410PT041 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT041 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT041-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195356 | M410PT051 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT051 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT051-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195357 | M410PT061 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT061 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT061-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195358 | M410PT071 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT071 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT071-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195359 | M410PT081 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT081 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT081-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195360 | M410PT091 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT091 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT091-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195361 | M410PT101 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT101 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT101-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195362 | M410PT111 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT111 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT111-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195363 | M410PT121 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT121 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT121-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195364 | M410PT131 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT131 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT131-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195365 | M410PT141 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT141 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT141-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195366 | M410PT151 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT151 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT151-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195367 | M410PT161 | Pressure Transmitter | Pressure Transmitter |  | PRES_TX | M410LT161 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT161-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969195368 | M410TE011 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT011 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195369 | M410TE021 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT021 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195370 | M410TE031 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT031 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195371 | M410TE041 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT041 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195372 | M410TE051 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT051 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195373 | M410TE061 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT061 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195374 | M410TE071 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT071 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195375 | M410TE081 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT081 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195376 | M410TE091 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT091 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195377 | M410TE101 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT101 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195378 | M410TE111 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT111 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195379 | M410TE121 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT121 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195380 | M410TE131 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT131 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195381 | M410TE141 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT141 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195382 | M410TE151 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT151 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195383 | M410TE161 | Temperature Element | Temperature Element |  | TEMP_ELE | M410LT161 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195384 | M410ARV004A | Air Release Valve | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-004A INTERNAL TRANSFER IRP2 TO IRP1. |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195385 | M410ARV004B | Air Release Valve | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-004B INTERNAL TRANSFER IRP2 TO IRP1. |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195386 | M410ARV004C | Air Release Valve | AIR RELEASE VALVE 2", JET A1 FILTER COALESCERS 410-L-004C INTERNAL TRANSFER IRP2 TO IRP1. |  | PSV | M410VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195387 | M410STR007A | Strainer, 18" T-TYPE | Strainer |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195388 | M410STR379 | Strainer, 4", Y -TYPE | Strainer |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195389 | M410STR383 | Strainer, 20" T TYPE | Strainer |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195390 | M410STR720 | Strainer, 8" , Y TYPE | Strainer |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195391 | M410STR721 | Strainer, 6", Y-TYPE | Strainer |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195392 | M410STR900 | Strainer, 12", T TYPE | Strainer |  | TRST | M410FILTER | 3 | TRST | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195393 | M410FA003A | 6" Flame Arrester, 150#, RF | 6" Flame Arrester, 150#, RF |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 5 | 50 | 5 | 5 | 6.4949 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195394 | M410FA003B | 6" Flame Arrester, 150#, RF | 6" Flame Arrester, 150#, RF |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 5 | 50 | 5 | 5 | 6.4949 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195395 | M410FA004A | 6" Flame Arrester, 150#, RF | 6" Flame Arrester, 150#, RF |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 5 | 50 | 5 | 5 | 6.4949 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195396 | M410FA004B | 6" Flame Arrester, 150#, RF | 6" Flame Arrester, 150#, RF |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 5 | 50 | 5 | 5 | 6.4949 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195397 | M410BAV2358001 | 1" Non Ferrous Ball Valve, #150, FF | 1" Non Ferrous Ball Valve, #150, FF |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195398 | M410BAV2358002 | 2" Non Ferrous Ball Valve, #150, FF | 2" Non Ferrous Ball Valve, #150, FF |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195399 | M410BAV2358003 | 3" Non Ferrous Ball Valve, #150, FF | 3" Non Ferrous Ball Valve, #150, FF |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195400 | M410BAV2358004 | 1/2" Non Ferrous Ball Valve, PN25, FTE | 1/2" Non Ferrous Ball Valve, PN25, FTE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195401 | M410BAV2358005 | 3/4" Non Ferrous Ball Valve, PN25, FTE | 3/4" Non Ferrous Ball Valve, PN25, FTE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195402 | M410BAV2358006 | 1" Non Ferrous Ball Valve, PN25, FTE | 1" Non Ferrous Ball Valve, PN25, FTE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195403 | M410BAV2358007 | 2" Non Ferrous Ball Valve, PN25, FTE | 2" Non Ferrous Ball Valve, PN25, FTE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195404 | M410BAV2358008 | 3" Non Ferrous Ball Valve, PN25, FTE | 3" Non Ferrous Ball Valve, PN25, FTE |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195405 | M410CHV2358001 | 1" Non Ferrous Check Valve, #150, FF | 1" Non Ferrous Check Valve, #150, FF |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195406 | M410ASP0011 | Substation Alarm Annunciator Panel | Substation Alarm Annunciator Panel |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195407 | M410ASP0012 | Substation Alarm Annunciator Panel | Substation Alarm Annunciator Panel |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195408 | M410BD001A | 415V BUSBAR TRUNKING for 410-TML-001A | Bus Bar Trunking for 410-TML-001A |  | SWBOARD | M410TML001A | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195409 | M410BD001B | 415V BUSBAR TRUNKING for 410-TML-001B | Bus Bar Trunking for 410-TML-001B |  | SWBOARD | M410TML001B | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281330 | M410EA050BB | AIR BLAST COOLER FOR 410-P-002A/B | AIR BLAST COOLER FOR 410-P-002A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA050BB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969281331 | M410EA051AA | AIR BLAST COOLER FOR 410-P-004A/B | AIR BLAST COOLER FOR 410-P-004A/B |  | HEATEXHR | M410EXCH | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA051AA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
932795 | M400BD11011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932796 | M400BD11111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932797 | M400BD11211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935737 | M400TMM001BB | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935741 | M400MSBC | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935742 | M400MSBR | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935743 | M400MMSBC001 | SWITCHGEAR | H.V. SWITCHGEAR 11KV |  | SWBOARD | M400MS001 | 2 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935744 | M400MMSBR001 | SWITCHGEAR | H.V. SWITCHGEAR 11KV |  | SWBOARD | M400MS001 | 2 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935745 | M400MMSIC001 | SWITCHGEAR | H.V. SWITCHGEAR 11KV |  | SWBOARD | M400MS001 | 2 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935746 | M400MMSIC002 | SWITCHGEAR | H.V. SWITCHGEAR 11KV |  | SWBOARD | M400MS001 | 2 | BREAKER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935747 | M400FWF001 | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935751 | M400PM016A | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935752 | M400PM016B | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935753 | M400PM018SPARE | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935754 | M400PM018A | SWITCHGEAR | M.V. SWITCHGEAR 3.3KV |  | SWBOARD | M400MS001 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937392 | M20MP227A | MOTOR, ELECTRIC, JET A1 TANKER LOADING , 37KW , 50HZ , 415V , IP55 , 6312M/C3 , | MOTOR JET A1 ROAD LOADING PUMP |  | MOTOR | M20P227A | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937393 | M20MP227B | MOTOR, ELECTRIC, JET A1 TANKER LOADING , 37KW , 50HZ , 415V , IP55 , 6312M/C3 , | MOTOR JET A1 ROAD LOADING PUMP |  | MOTOR | M20P227B | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937394 | M400MP021A | MOTOR,ELECTRIC, ULG-95/98 INTER TANK TRANSFER, IP55, 55KW, 50HZ, 415V, S1, IP55, M3GP 280SMA 4V1, 6316M/C3, 6316M/C3, VERTICAL MOUNTING, 1483 RPM, 3, DELTA, 94A, F, EExnAII T3, 625 KG, T3, AS PER DATA SHEET | VERTICAL MOTOR, ELECTRIC, ULG 95/98 TRASFER PUMP, IP55 |  | MOTOR | M400P021A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP021A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 02/12/18 | ME-PM-014-M6
937395 | M400MP021B | MOTOR,ELECTRIC, ULG-95/98 INTER TANK TRANSFER, IP55, 55KW, 50HZ, 415V, S1, Ex d, M3GP 280SMA 4V1, 6316M/C3, 6316M/C3, VERTCAL MOUNTING, 1483 RPM, 3, STAR, 94A, F, EExnAII T3, 625 KG, T3 | VERTICAL MOTOR, ULG95/ULG98/ INTER TANK TRANSFER PUMP |  | MOTOR | M400P021B | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP021B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/01/19 | ME-PM-014-M6
937397 | M20P227A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.75" , SILICON CARBIDE , 5U4X/5U4X , FLUOR | JET A1 ROAD LOADING PUMPS | 934049 | PUMPS | M20PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937398 | M20P227B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 3.75" , SILICON CARBIDE , 5U4X/5U4X , FLUOR | JET A1 ROAD LOADING PUMPS | 934050 | PUMPS | M20PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937401 | M400P024B | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 2" , SILICON CARBIDE , 5U4X/5U4X , FLUOROEL | SLOP TRANSFER PUMPS | 934057 | PUMPS | M400PUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P024B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-007-M6
937402 | M400P024A | SEAL, MECHANICAL, DOUBLE CARTRIDGE , 2" , SILICON CARBIDE , 5U4X/5U4X , FLUOROEL | SLOP TRANSFER PUMP-A. | 934056 | PUMPS | M400PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P024A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/12/18 | MM-PM-007-M6
939039 | M400TE408B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing CE For Pump 400-P-016A |  | TEMP_ELE | M400TI408B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939040 | M400TE409A | ELEMENT, TEMPERATURE, SINGLE RTD THERMOMETER , PT100, 3 WIRE, SINGLE , 0-200 DEG | Pump Radial Bearing D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI409A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939041 | M400TE409B | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100 , 100 OHM @ 0 DEG C , PLATINUM | Pump Radial Bearing D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI409B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939042 | M400TE410A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100, 3 WIRE, SINGLE , 0-200 | Casing For Pump 400-P-016A |  | TEMP_ELE | M400TI410A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939043 | M400TE411A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Pump Radial Bearing N.D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI411A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939044 | M400TE411B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Pump Radial Bearing N.D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI411B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939045 | M400TE412A | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C | Thrust Bearing D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI412A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939046 | M400TE412B | ELEMENT, TEMPERATURE, THERMORESISTANCE , PT100, 3 WIRE, SINGLE , 100 OHM @ 0 DEG | Thrust Bearing D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI412B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939047 | M400TE413A | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C | Thrust Bearing N.D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI413A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939048 | M400TE413B | ELEMENT, TEMPERATURE, SINGLE RTD THERMOMETER , PT100 , 100 OHM @ 0 DEG C , PLATI | Thrust Bearing N.D.E. For Pump 400-P-016A |  | TEMP_ELE | M400TI413B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939049 | M400TE414C | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Lube Oil Header Temp. For Pump 400-P-016A |  | TEMP_ELE | M400TI414C | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939050 | M400TE416 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'U' Winding For Pump 400-P-016B | 939154 | TEMP_ELE | M400TI416 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939051 | M400TE417 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'U' Winding For Pump 400-P-016B | 939155 | TEMP_ELE | M400TI417 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939052 | M400TE418 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'V' Winding For Pump 400-P-016B | 939156 | TEMP_ELE | M400TI418 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939053 | M400TE418C | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'U' Winding For Pump 400-P-016B | 939157 | TEMP_ELE | M400TI418C | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939054 | M400TE419 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'V' Winding For Pump 400-P-016B | 939158 | TEMP_ELE | M400TI419 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939055 | M400TE420 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'W' Winding For Pump 400-P-016B | 939159 | TEMP_ELE | M400TI420 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939056 | M400TE421 | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR 'W' Winding For Pump 400-P-016B | 939160 | TEMP_ELE | M400TI421 | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939057 | M400TE422A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing NCE For Pump 400-P-016 | 939161 | TEMP_ELE | M400TI422A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939058 | M400TE422B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing NCE For Pump 400-P-016 | 939162 | TEMP_ELE | M400TI422B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939059 | M400TE423A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing CE For Pump 400-P-016B | 939163 | TEMP_ELE | M400TI423A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939060 | M400TE423B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 100 OHM @ 0 DEG C , PL | Main E-MOTOR Radial Bearing CE For Pump 400-P-016B | 939164 | TEMP_ELE | M400TI423B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939061 | M400TE424A | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C | Pump Radial Bearing D.E. For Pump 400-P-016B | 939165 | TEMP_ELE | M400TI424A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939062 | M400TE424B | ELEMENT, TEMPERATURE, THERMORESISTANCE , SINGLE RTD, 3 WIRES , 100 OHM @ 0 DEG C | Pump Radial Bearing D.E. For Pump 400-P-016B | 939166 | TEMP_ELE | M400TI424B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV19793 | U51MOV115 | ACTUATOR, ELECTRIC MOTOR, LPG TO MUSSAFAH , LIMITORQUE , L120-10 , 415 V, 3 , 50 | MOV FOR LPG TO MUSSAFAH LINE |  | MOV | U5101R01 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV19801 | U51MOV104 | ACTUATOR, ELECTRIC MOTOR, LPG TO MUSSAFAH , LIMITORQUE , L120-10 , 415 V, 3 , 50 | MOV FOR LPG LINE |  | MOV | U5101R01 | 2 | MOV | 623101-610202 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV19802 | U51MOV105 | ACTUATOR, ELECTRIC MOTOR, LPG LINE , LIMITORQUE , L120-10 , 415 V, 3 , 50 HZ, 14 | MOV FOR LPG TO MUSSAFAH LINE |  | MOV | U5101R01 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV19803 | U51MOV106 | ACTUATOR,ELECTRIC MOTOR, LPG LINE, LIMITORQUE, L120-10, 415 V, 3, 50 HZ, 1417 RPM, 1.7 AMP, 15 MIN, 8" X 6", D N/A, RF X 300LB, D N/A, D N/A, D N/A, D N/A, D N/A, D N/A, D N/A, D N/A, D N/A, D N/A, D N/A, ELECTRIC, D N/A, GREASE, L120-10, D N/A, EExd IIB T4, D N/A | MOV FOR LPG LINE |  | MOV | U5101R01 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275944 | PL100FG111 | Sight Glass | Sight Glass |  | INDICATR | PL100FLOW | 3 | INDICATR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275420 | PL312EOV31204 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-04 | ELECTRO HYDRAULIC VALVE, SV STATION-4 | 969275349 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275350 | PL312EOV31205 | ELECTRO HYDRAULIC VALVE, SV STATION-5 | ELECTRO HYDRAULIC VALVE, SV STATION-5 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275421 | PL312EOV31205 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-05 | ELECTRO HYDRAULIC VALVE, SV STATION-5 | 969275350 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275351 | PL312EOV31206 | ELECTRO HYDRAULIC VALVE, SV STATION-6 | ELECTRO HYDRAULIC VALVE, SV STATION-6 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275422 | PL312EOV31206 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-06 | ELECTRO HYDRAULIC VALVE, SV STATION-6 | 969275351 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275352 | PL312EOV31301 | ELECTRO HYDRAULIC VALVE, SV STATION-1 | ELECTRO HYDRAULIC VALVE, SV STATION-1 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275423 | PL312EOV31301 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-01 | ELECTRO HYDRAULIC VALVE, SV STATION-1 | 969275352 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275353 | PL312EOV31302 | ELECTRO HYDRAULIC VALVE, SV STATION-2 | ELECTRO HYDRAULIC VALVE, SV STATION-2 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275424 | PL312EOV31302 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-02 | ELECTRO HYDRAULIC VALVE, SV STATION-2 | 969275353 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275354 | PL312EOV31303 | ELECTRO HYDRAULIC VALVE, SV STATION-3 | ELECTRO HYDRAULIC VALVE, SV STATION-3 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275425 | PL312EOV31303 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-03 | ELECTRO HYDRAULIC VALVE, SV STATION-3 | 969275354 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275355 | PL312EOV31304 | ELECTRO HYDRAULIC VALVE, SV STATION-4 | ELECTRO HYDRAULIC VALVE, SV STATION-4 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275426 | PL312EOV31304 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-04 | ELECTRO HYDRAULIC VALVE, SV STATION-4 | 969275355 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275356 | PL312EOV31305 | ELECTRO HYDRAULIC VALVE, SV STATION-5 | ELECTRO HYDRAULIC VALVE, SV STATION-5 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275427 | PL312EOV31305 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-05 | ELECTRO HYDRAULIC VALVE, SV STATION-5 | 969275356 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275357 | PL312EOV31306 | ELECTRO HYDRAULIC VALVE, SV STATION-6 | ELECTRO HYDRAULIC VALVE, SV STATION-6 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275428 | PL312EOV31306 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-06 | ELECTRO HYDRAULIC VALVE, SV STATION-6 | 969275357 | MOV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275429 | PL312FE001A | FLOW ELEMENT FOR CTS | FLOW ELEMENT FOR CTS |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275430 | PL312FE001B | FLOW ELEMENT FOR CTS | FLOW ELEMENT FOR CTS |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275431 | PL312FE002A | FLOW ELEMENT FOR CTS | FLOW ELEMENT FOR CTS |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275432 | PL312FE002B | FLOW ELEMENT FOR CTS | FLOW ELEMENT FOR CTS |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275433 | PL312FG111 | Sight Glass | Sight Glass |  | INDICATR | PL312FLOW | 4 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275434 | PL312FG211 | Sight Glass | Sight Glass |  | INDICATR | PL312FLOW | 4 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275435 | PL312FMS001 | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, TARIF (312) CONTROL ROOM | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, TARIF (312) CONTROL ROOM |  | BLDGS | PL312SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275436 | PL312FT001 | CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF ULG | CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF ULG |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275437 | PL312FT001A | FLOW TRANSMITTER FOR 312-FT-001 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF ULG | FLOW TRANSMITTER FOR 312-FT-001 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF ULG |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275438 | PL312FT001B | FLOW TRANSMITTER FOR 312-FT-001 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF ULG | FLOW TRANSMITTER FOR 312-FT-001 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF ULG |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275439 | PL312FT002 | CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF GAS OIL | CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF GAS OIL |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275440 | PL312FT002A | FLOW TRANSMITTER FOR 312-FT-002 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF GAS OIL | FLOW TRANSMITTER FOR 312-FT-002 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF GAS OIL |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275441 | PL312FT002B | FLOW TRANSMITTER FOR 312-FT-002 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF GAS OIL | FLOW TRANSMITTER FOR 312-FT-002 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER) TARIF GAS OIL |  | FL_MTR | PL312FLOW | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275442 | PL312GAV21223001 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275443 | PL312GAV21223002 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275444 | PL312GAV21223003 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275445 | PL312GAV21223004 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275446 | PL312GAV21223005 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275447 | PL312GAV21223006 | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275448 | PL312GAV21223007 | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275449 | PL312GAV21223008 | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275450 | PL312GAV21233001 | 2" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275451 | PL312GAV21233002 | 2" Gate Valve, ISO 10434, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275452 | PL312GAV21233003 | 2" Gate Valve, ISO 10434, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Flexible Wedge, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275453 | PL312GDH105 | HC GAS DETECTOR | HC GAS DETECTOR |  | FG_DET | PL312GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275454 | PL312GLV21233001 | 2" Globe Valve, BS 1873, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 | 2" Globe Valve, BS 1873, Class 600, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275455 | PL312GLV21233002 | 3" Globe Valve, BS 1873, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 | 3" Globe Valve, BS 1873, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275456 | PL312GLV21233003 | 2" Globe Valve, BS 1873, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Plug Disc, ASME B16.5 | 2" Globe Valve, BS 1873, Class 1500, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, Plug Disc, ASME B16.5 |  | CONTHNDV | PL312VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365304 | M410XHD605A | LINEAR HEAT DETECTOR FOR TANK-016 | LINEAR HEAT DETECTOR FOR TANK-016 |  | FGBHFD | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275465 | PL312LT001 | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | PL312SYS | 3 | POWER_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275466 | PL312LT002 | LEVEL TRANSMITTER | LEVEL TRANSMITTER |  | POWER_TX | PL312SYS | 3 | POWER_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275467 | PL312MOV001AA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275468 | PL312MOV001AB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275469 | PL312MOV001BA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275470 | PL312MOV001BB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275471 | PL312MOV002AA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275472 | PL312MOV002AB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275473 | PL312MOV002BA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275474 | PL312MOV002BB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | PL312MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275475 | PL312PDT001A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275476 | PL312PDT001B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275477 | PL312PDT002A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275478 | PL312PDT002B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | PL312PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275479 | PL312PG001 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275480 | PL312PG001AA | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275481 | PL312PG001AB | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275482 | PL312PG001BA | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275483 | PL312PG001BB | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275484 | PL312PG002 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275485 | PL312PG002AA | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275486 | PL312PG002AB | Pressure Gauge | Pressure Gauge |  | INDICATR | PL312PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275820 | PL318PT31912B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275821 | PL318RTU001 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275822 | PL318RTU002 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275823 | PL318RTU003 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275824 | PL318RTU004 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275825 | PL318RTU005 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275826 | PL318SCR1001 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL318SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275827 | PL318SCR1101 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL318SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275828 | PL318SCR1201 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL318SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275829 | PL318SCR801 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL318SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275830 | PL318SCR901 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL318SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275831 | PL318SPS1001 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL318SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275832 | PL318SPS1002 | PASSIVE COOLING SHELTER - SV.10 | PASSIVE COOLING SHELTER - SV.10 |  | PACKAGE | PL318PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275833 | PL318SPS1101 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL318SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275834 | PL318SPS1102 | PASSIVE COOLING SHELTER - SV.11 | PASSIVE COOLING SHELTER - SV.11 |  | PACKAGE | PL318PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275835 | PL318SPS1201 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL318SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275836 | PL318SPS1202 | PASSIVE COOLING SHELTER - SV.12 | PASSIVE COOLING SHELTER - SV.12 |  | PACKAGE | PL318PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275837 | PL318SPS801 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL318SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275838 | PL318SPS802 | PASSIVE COOLING SHELTER - SV.8 | PASSIVE COOLING SHELTER - SV.8 |  | PACKAGE | PL318PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275839 | PL318SPS901 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL318SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275840 | PL318SPS902 | PASSIVE COOLING SHELTER - SV.9 | PASSIVE COOLING SHELTER - SV.9 |  | PACKAGE | PL318PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275841 | PL318TE31808A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275842 | PL318TE31808B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935449 | SALAINTP4 |  | TEST POINT # 4 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935465 | SALAINTP17 |  | TEST POINT # 17 (C.P. STATION-2 AT KM 18.5) |  |  | SALAINCPS2 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175099 | M410DET234901 | Leak Detection System | TANKS Leak Detection System |  | PACKAGE | M410TANKS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175140 | M410PDT200 | 410-P-007A SUCTION STRAINER 410-STR-007A | 410P007A SUCTION STRAINER 410-STR-007A |  | PRES_TX | M410P007A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT200-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/11/18 | MC-PM-PT1-M6
969270608 | M410TT002 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410V006 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270609 | M410TT401 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410PLR001 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270610 | M410TT403 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410PT412 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270611 | M410TT405 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410PLR005 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270612 | M410TT406 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410PLR006 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270613 | M410TT408 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410PLR003 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270614 | M410TT412 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410PLR007 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270615 | M410TSV130 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270616 | M410TSV206 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270617 | M410TSV207 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270618 | M410TSV208 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270619 | M410TSV209 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270620 | M410TSV211 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P002B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270621 | M410TSV213 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P002B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270622 | M410TSV214 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P003A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270623 | M410TSV215 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P003B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270624 | M410TSV216 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P003A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270625 | M410TSV217 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P003B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270626 | M410TSV219 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P004B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270627 | M410TSV221 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P004B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270628 | M410TSV222 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P005A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270629 | M410TSV223 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P005A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270630 | M410TSV224 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P005A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270631 | M410TSV225 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P005B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270632 | M410TSV226 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270633 | M410TSV227 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270634 | M410TSV228 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270635 | M410TSV229 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P006B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270636 | M410TSV230 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P023A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270637 | M410TSV231 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P023A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270638 | M410TSV232 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P023A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270639 | M410TSV233 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P023B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270640 | M410TSV234 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270641 | M410TSV235 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270642 | M410TSV236 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P023C | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270643 | M410TSV257 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L008A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270644 | M410TSV258 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L009A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270645 | M410TSV265 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P006C | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270646 | M410TSV266 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P005C | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270647 | M410TSV267 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P024A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270648 | M410TSV268 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P024A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270649 | M410TSV269 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P024A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270650 | M410TSV270 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P024B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270651 | M410TSV271 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410P024C | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270652 | M410TSV411 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270653 | M410TSV412 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270654 | M410TSV413 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270655 | M410TSV414 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270656 | M410TSV415 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270657 | M410TSV416 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270658 | M410TSV417 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270659 | M410TSV418 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270660 | M410TSV420 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410PLR005 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270661 | M410TSV421 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410PLR005 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270662 | M410TSV422 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410PLR005 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270663 | M410TSV435 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L011A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270664 | M410TSV436 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L011A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270665 | M410TSV441 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410PLR005 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270666 | M410TSV448 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410L001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270667 | M410TSV451 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270668 | M410TSV203A | THERMAL RELIEFE VALVE, MUS-ALAIN ULG P/L FLOW | THERMAL RELIEFE VALVE, MUS-ALAIN ULG P/L FLOW |  | PSV | M410FT203 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270669 | M410TSV203B | THERMAL RELIEFE VALVE, MUS-ALAIN ULG P/L FLOW | THERMAL RELIEFE VALVE, MUS-ALAIN ULG P/L FLOW |  | PSV | M410FT203 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270670 | M410TSV206A | THERMAL RELIEFE VALVE, MUS-ALAIN GO P/L FLOW | THERMAL RELIEFE VALVE, MUS-ALAIN GO P/L FLOW |  | PSV | M410FT206 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270671 | M410TSV206B | THERMAL RELIEFE VALVE, MUS-ALAIN GO P/L FLOW | THERMAL RELIEFE VALVE, MUS-ALAIN GO P/L FLOW |  | PSV | M410FT206 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270672 | M410TSV209A | THERMAL RELIEFE VALVE, MUS-ADIA-N JA1 P/L FLOW | THERMAL RELIEFE VALVE, MUS-ADIA-N JA1 P/L FLOW |  | PSV | M410FT209 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270673 | M410TSV209B | THERMAL RELIEFE VALVE, MUS-ADIA-N JA1 P/L FLOW | THERMAL RELIEFE VALVE, MUS-ADIA-N JA1 P/L FLOW |  | PSV | M410FT209 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270674 | M410TSV211A | THERMAL RELIEFE VALVE, MUS-DHAFRA JP8 P/L FLOW | THERMAL RELIEFE VALVE, MUS-DHAFRA JP8 P/L FLOW |  | PSV | M410FT211 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270675 | M410TSV211B | THERMAL RELIEFE VALVE, MUS-DHAFRA JP8 P/L FLOW | THERMAL RELIEFE VALVE, MUS-DHAFRA JP8 P/L FLOW |  | PSV | M410FT211 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270676 | M410TSV400A | THERMAL RELIEFE VALVE, RUW-MUS JA1 P/L FLOW | THERMAL RELIEFE VALVE, RUW-MUS JA1 P/L FLOW |  | PSV | M410FT400 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270677 | M410TSV400B | THERMAL RELIEFE VALVE, RUW-MUS JA1 P/L FLOW | THERMAL RELIEFE VALVE, RUW-MUS JA1 P/L FLOW |  | PSV | M410FT400 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270678 | M410TSV400C | THERMAL RELIEFE VALVE, RUW-MUS JA1 P/L FLOW | THERMAL RELIEFE VALVE, RUW-MUS JA1 P/L FLOW |  | PSV | M410FT400 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270679 | M410TSV401A | THERMAL RELIEFE VALVE, RUW-MUS GO P/L FLOW | THERMAL RELIEFE VALVE, RUW-MUS GO P/L FLOW |  | PSV | M410FT401 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270680 | M410TSV401B | THERMAL RELIEFE VALVE, RUW-MUS GO P/L FLOW | THERMAL RELIEFE VALVE, RUW-MUS GO P/L FLOW |  | PSV | M410FT401 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270681 | M410TSV401C | THERMAL RELIEFE VALVE, RUW-MUS GO P/L FLOW | THERMAL RELIEFE VALVE, RUW-MUS GO P/L FLOW |  | PSV | M410FT401 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270682 | M410TSV405 | PRESSURE SAFETY VALVE | Thermal Reliefe Valve |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270683 | M410TSV751 | THERMAL SAFETY VALVE FOR ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) | THERMAL SAFETY VALVE FOR ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) |  | PSV | M410ME011 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270684 | M410TSV701 | THERMAL SAFETY VALVE FOR ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) | THERMAL SAFETY VALVE FOR ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) |  | PSV | M400ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512478 | A-MSFH-RECEPT | Dell Optiplex 7010 | P&T Reception |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512668 | A-MSFH-AGOPAL | Dell Optiplex 9020 | ARUN GOPAL MADASWAMY |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512676 | SDIBTESAM | HP Prodesk 600 G1 | IBTESAM MOHAMED AL JENAIBI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512677 | A-MSFH-ASMA | HP Prodesk 600 G1 | Asma Abbas Al Blooshi. |  |  | P&T_NEW_ADMIN | [14 empty] | Non Critical | N | Non Critical | N |  |  | d
969512678 | SD-PT-MJM11491 | HP Prodesk 600 G3 | Mohammed Al Shamisi |  |  | P&T_NEW_ADMIN | [14 empty] | Non Critical | N | Non Critical | N |  |  | d
969512679 | A-MSFH-PI | Dell Optiplex 760 | Planning - PI system |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512680 | A-HESHAM | Lenovo - M2999-A34 | No Body using this PC - room 118 |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512681 | SD-MSH-JAMAL | HP Prodesk 600 G1 | Jamal Al Hindi |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512682 | A-GERA45-R30 | HP Prodesk 600 G1 | Jamal - Planing |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512683 | A-MSFH-MGR | Dell Optiplex 9020 | FUJITSU-SIEMENS P3510 |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512684 | A-MSFH-MEERA | Lenovo - M2999-A34 | Meera Al Mansoori. |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512685 | A-MSFH0-SHATERI | Lenovo - M2999-A34 | Ahmed Hasen Al Shateri |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512670 | A-MSFH-FARAJ | Lenovo - M2999-A34 | ABDULLA FARAJ ABDULLAH AL HASAN |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512673 | A-PLANNING-R32 | Dell Optiplex 790. | DELL OPTIPLEX 790 |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512674 | SDSINISH | HP Prodesk 600 G1 | Sinish |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512686 | A-MSFH-MRASHED | Dell Optiplex 9020 | CHRISTIAN QUICHO |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512687 | A-MSFH-VISH | Dell Optiplex 9020 | JAMAL AYEDH SALMEEN |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512688 | A-TSD-SURAJ | Dell Optiplex 790 | Jay-Mar Monjas |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512689 | A-MSFH-ESDMNGR | HP Prodesk 600 G1 | AHMED ALI MUBARAK OBAID |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512690 | A-ABDULAZIZ-R41 | HP Prodesk 600 G1 | AHMED ALI MUBARAK OBAID - Process |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512691 | A-MSFH-VPSEC | HP Prodesk 600 G1 | VP Secretary |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512692 | A-MSFH-VPSD | HP Prodesk 600 G1 | FAREED MOHAMED AL JABERI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512694 | A-FOUSAL-A3 | Dell Optiplex 9020 | Fousal Ameen Khadr |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512468 | SD-PT-ELCHOUM | Hp Prodesk 600 G3 | Hussein El Choum |  |  | P&T_NEW_ADMIN | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | d
969132468 | PL300XAC001/02 | CALL POINT, EEx emd IIT4 or EEx ed IIT6, RED, FIRE ALARM PUSH BUTTON, IP66 & IP 67, YES | MANUAL CALL POINT AT MAIN GATE SV STATION - 2 |  | PB_HS-MC | PL300SVS2 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC001/02-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/10/18 | MFPS-PM07.M3
969132469 | PL300XAC002/02 | CALL POINT, EEx emd IIT4 or EEx ed IIT6, RED, FIRE ALARM PUSH BUTTON, IP66 & IP 67, YES | MANUAL CALL POINT AT EMERGENCY GATE SV STATION - 2 |  | PB_HS-MC | PL300SVS2 | 3 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XAC002/02-UFP | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 08/10/18 | MFPS-PM07.M3
969169667 | MFBAY2EGD | FIRE BUILDING BAY#1 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. | FIRE BUILDING BAY#2 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. |  |  | MFBAY2 | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131365 | M400MON001 | MONITOR | CCTV MONITOR SYSTEM AT PLCR CONSOLE ROOM |  | WS_SYS | M400CCTV | 1 | WS_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MON001-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131506 | M400XSP081 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131508 | M400XSP083 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131513 | M400XSP088 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR SWITCHGEAR ROOM IN SUBSTATION |  | FG_DET | M400FACP002 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131535 | M400XSP113 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN HVAC ROOM OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131539 | M400XSP118 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN RECEPTION / WAITING AREA OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131483 | M400XSP050 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TELECOM ROOM BETWEN FLOOR AND FALSE FLORR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131489 | M400XSP056 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR LOBBY ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131499 | M400XSP066 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR CORRIDOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131502 | M400XSP069 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR HVAC ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131540 | M400XSP119 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN LOBBY AREA OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131541 | M400XSP120 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR FIRE & SAFETY STAFF OFADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131542 | M400XSP121 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN PIPELINE STAFF OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131546 | M400XSP125 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN CORRIDOR OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131548 | M400XSP127 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR IN HVAC AIR INTAKE DUCT OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131467 | M400XSP034 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT UPS ROOM BETWEN CEILING & FALSE CEILING-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131468 | M400XSP035 | DETECTOR,FIRE PROTECTION, YES, 24VDC, OPTICAL SMOKE | SMOKE DETECTOR AT UPS ROOM BETWEN FLOOR & FALSE FLOOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131470 | M400XSP037 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131472 | M400XSP039 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR AT SCADA ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131478 | M400XSP045 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR TELECOM ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131485 | M400XSP052 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR CORRIDOR-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131492 | M400XSP059 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR INCHARGE ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131495 | M400XSP062 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES, 24VDC | SMOKE DETECTOR FOR LOCKER ROOM-PLCR |  | FG_DET | M400FACP001 | 1 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131383 | M400RXTB002 | CONTROL RECEIVER | RECEIVER, ABOVE T-112 , CONTROL THE DATA TO & FROM COMPACT CAMERA |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RXTB002-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131384 | M400RXTB003 | CONTROL RECEIVER | RECEIVER, ABOVE T-106 , CONTROL THE DATA TO & FROM COMPACT CAMERA |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RXTB003-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131385 | M400RXTB004 | CONTROL RECEIVER | RECEIVER, ABOVE T-103 , CONTROL THE DATA TO & FROM COMPACT CAMERA |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RXTB004-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131386 | M400RX002 | COMMUNICATION RECEIVER | RECEIVER-ABOVE T-112, FOR COMMUNICATION WITH CONTROL SYSTEM & CONTROLS THE OTHER FUNCTIONS OF THE CAMERAS |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RX002-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131387 | M400RX003 | COMMUNICATION RECEIVER | RECEIVER-ABOVE T-106, FOR COMMUNICATION WITH CONTROL SYSTEM & CONTROLS THE OTHER FUNCTIONS OF THE CAMERAS |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RX003-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969131388 | M400RX004 | COMMUNICATION RECEIVER | RECEIVER |  | CCTVSEC | M400SYS | 1 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400RX004-UFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM04.M3
969271749 | M410STR903 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271752 | M410STR905 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205434 | M410MP033A | FIRE WATER JOCKY PUMP- MOTOR | FIRE WATER JOCKY PUMP- MOTOR |  | MOTOR | M410P033A | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MP033A-ME1 | ACTIVE | ELEC | PM | FIM | 2 | WEEKS | 05/08/18 | ME-PM-016-W1
969205435 | M410MP033B | FIRE WATER PUMP- MOTOR | FIRE WATER JOCKY PUMP- MOTOR |  | MOTOR | M410P033B | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MP033B-ME1 | ACTIVE | ELEC | PM | FIM | 2 | WEEKS | 05/08/18 | ME-PM-016-W1
969205436 | M410PG364 | Pressure Gauge Discharge water Pump | Pressure Gauge Discharge water Pump |  | INDICATR | M410P031A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205437 | M410PG363 | Pressure Gauge Suction water pump | Pressure Gauge Suction water pump |  | INDICATR | M410P031A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205438 | M410PG377 | Pressure Gauge Discharge water Pump | Pressure Gauge Discharge water Pump |  | INDICATR | M410P033A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205439 | M410PG357 | Pressure Gauge Suction water pump | Pressure Gauge Suction water pump |  | INDICATR | M410P033A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205440 | M410PT31A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410T031A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT31A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 20/11/18 | MC-PM-PT1-M6
969205441 | M410PSV31A | PRESSURE SAFETY VALVE 18KG. | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P031A | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205442 | M410PDI383 | Pressure differential Indicator | Pressure differential Indicator |  | INDICATR | M410P031A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265920 | PL100PDG400A | Pressure Gage | Pressure Gauge |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265921 | PL100PDG400B | Pressure Gage | Pressure Gauge |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59001 | M51PI113 | GAUGE, PRESSURE, 0-25 KG/CM2 , 150MM , 1/2" NPT , 316 SS , 316 SS , BOTTOM , LOC | PRESS. INDICATOR FOR LPG PIG RECEIVER AT MTF | PGR56198 | INDICATR | M5101R02 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59002 | M51PI112 | GAUGE, PRESSURE, 0-25 KG/CM2 , 150MM , 1/2" , 316 SS , 316 SS , BOTTOM , LOCAL , | PRESS. INDICATOR FOR LPG PIG RECEIVER AT MTF | PGR56198 | INDICATR | M5101R02 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59003 | M51PI111 | GAUGE, PRESSURE, 0-25 KG/CM2 , 150MM , 1/2" , 316 SS , 316 SS , BOTTOM , LOCAL , | PRESS. INDICATOR FOR LPG PIG RECEIVER AT MTF | PGR56198 | INDICATR | M5101R02 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59004 | M51PI121 | GAUGE, PRESSURE, 0-60 BAR , 150MM , 1/2" , 316 SS , 316 SS , BOTTOM , LOCAL , +/ | PRESS. INDICATOR FOR LPG PIG RECEIVER AT MTF | PGR56198 | INDICATR | M5101R02 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59005 | M51PI118 | GAUGE, PRESSURE, 0-60 BAR , 150MM , 1/2" , 316 SS , 316 SS , BOTTOM , LOCAL , +/ | PRESS. INDICATOR FOR LPG PIG RECEIVER AT MTF | PGR56198 | INDICATR | M5101R02 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59012 | M15PG180 | GAUGE, PRESSURE, 0-25 KG/CM2 , 150MM , 1/2" NPT , 316 SS , COPPER ALLOY , 316 SS | PRESS. GAUGE AT MULTIPRODUCT PIG RECEIVER |  | INDICATR | M15R04 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59013 | M15PG161 | GAUGE, PRESSURE, 0-25 KG/CM2 , 150MM , 1/2" , 316 SS , COPPER ALLOY , 316 SS , B | PRESS. GAUGE AT MULTIPRODUCT PIG RECEIVER |  | INDICATR | M15R04 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59014 | M15PG103 | GAUGE, PRESSURE, 0-25 KG/CM2 , 150MM , 1/2" , 316 SS , COPPER ALLOY , 316 SS , B | PRESS. GAUGE AT MULTIPRODUCT PIG RECEIVER |  | INDICATR | M15R04 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59047 | M50PI171A | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , GRP PLASTIC , COPPER ALLOY , BRAS | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-101 | TNK56513 | INDICATR | M10T101 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59048 | M50PI171B | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-101 | TNK56513 | INDICATR | M10T101 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59049 | M50PI181A | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-101 | TNK56513 | INDICATR | M10T101 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59050 | M50PI181B | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-101 | TNK56513 | INDICATR | M10T101 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59069 | M50PI172A | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-102 | TNK56531 | INDICATR | M10T102 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59070 | M50PI172B | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" NPT , 1.4301 , COPPER ALLOY , BRASS , BO | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-102 | TNK56531 | INDICATR | M10T102 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59071 | M50PI182A | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" NPT , 1.4301 , COPPER ALLOY , BRASS , BO | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-102 | TNK56531 | INDICATR | M10T102 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59072 | M50PI182B | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" NPT , 1.4301 , COPPER ALLOY , BRASS , BO | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-102 | TNK56531 | INDICATR | M10T102 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59091 | M50PI173A | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" , 1.4301 , COPPER ALLOY , BRASS , BOTTOM | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-103 | TNK56547 | INDICATR | M10T103 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59092 | M50PI173B | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" , 1.4301 , COPPER ALLOY , BRASS , BOTTOM | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-103 | TNK56547 | INDICATR | M10T103 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59093 | M50PI183A | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" , 1.4301 , COPPER ALLOY , BRASS , BOTTOM | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-103 | TNK56547 | INDICATR | M10T103 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59094 | M50PI183B | GAUGE, PRESSURE, 0-25 BAR , 63MM , 1/4" , 1.4301 , COPPER ALLOY , BRASS , BOTTOM | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-103 | TNK56547 | INDICATR | M10T103 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59111 | M50PI174W | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-104 | TNK56565 | INDICATR | M10T104 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59112 | M50PI184W | GAUGE, PRESSURE, 0-16 KG/CM2 , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-104 | TNK56565 | INDICATR | M10T104 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59113 | M50PI200F | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-104 | TNK56565 | INDICATR | M10T104 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59114 | M50PI220F | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-104 | TNK56565 | INDICATR | M10T104 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59131 | M50PI175W | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-105 | TNK56585 | INDICATR | M10T105 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59132 | M50PI185W | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-105 | TNK56585 | INDICATR | M10T105 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGP59133 | M50PI201F | GAUGE, PRESSURE, 0-16 BAR , 63MM , 1/4" MNPT , 1.4301 , COPPER ALLOY , BRASS , B | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-105 | TNK56585 | INDICATR | M10T105 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195485 | M410FU330 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969169669 | MFBAY1WGD | FIRE BUILDING BAY#1 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. | FIRE BUILDING BAY#1 WEST GARAGE DOOR AT MUSSAFAH TERMINAL. |  |  | MFBAY1 | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969169670 | MFBAY2WGD | FIRE BUILDING BAY#1 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. | FIRE BUILDING BAY#2 WEST GARAGE DOOR AT MUSSAFAH TERMINAL. |  |  | MFBAY2 | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969169671 | MFBAY3WGD | FIRE BUILDING BAY#1 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. | FIRE BUILDING BAY#3 WEST GARAGE DOOR AT MUSSAFAH TERMINAL. |  |  | MFBAY3 | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175204 | M410RO734 | WATER SPRAY FOR 410-T-012FROM 410-STR-734 TO 410-PG-734 | WATER SPRAY FOR 410-T-012FROM 410-STR-734 TO 410-PG-734 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175205 | M410RO735 | WATER SPRAY FOR 410-T-012FROM 410-STR-735 TO 410-PG-735 | WATER SPRAY FOR 410-T-012FROM 410-STR-735 TO 410-PG-735 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175206 | M410RO736 | WATER SPRAY FOR 410-T-013FROM 410-STR-736 TO 410-PG-736 | WATER SPRAY FOR 410-T-013FROM 410-STR-736 TO 410-PG-736 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175207 | M410RO737 | WATER SPRAY FOR 410-T-013FROM 410-STR-737 TO 410-PG-737 | WATER SPRAY FOR 410-T-013FROM 410-STR-737 TO 410-PG-737 |  | ORIFICE | M410T013 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275096 | M410CHV21263008 | 6" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 6" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275097 | M410CHV21263009 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 300, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 300, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275098 | M410CHV21263010 | 20" Dual Plate Double-Flanged Check Valve, API 594, Class 300, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 20" Dual Plate Double-Flanged Check Valve, API 594, Class 300, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275099 | M410CHV21263011 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 600, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 600, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275100 | M410CHV21263012 | 16" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 16" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275101 | M410CHV21263013 | 18" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 18" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275102 | M410CHV21263014 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 900, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 900, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275076 | M410BAV21273007 | 0.5" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe | 0.5" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275077 | M410BAV21273008 | 1.5" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe | 1.5" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275078 | M410CHV21223001 | 1" Lift Check Valve Piston Type, ISO 15761, Class 800, Socket Weld End, Bolted Cover, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc | 1" Lift Check Valve Piston Type, ISO 15761, Class 800, Socket Weld End, Bolted Cover, ASTM A182 Grade F316L, Trim 316LSS w/Stellite Seats & Disc |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275079 | M410CHV21233001 | 12" Swing Check Valve, BS 1868, Class 900, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, ASME B16.5 | 12" Swing Check Valve, BS 1868, Class 900, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr w/Stellite Seats & Disc, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275080 | M410CHV21233002 | 4" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A351 Grade CF8M, Trim 316LSS w/Stellite Seats & Disc, ASME B16.5 | 4" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A351 Grade CF8M, Trim 316LSS w/Stellite Seats & Disc, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275081 | M410CHV21233003 | 2" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 2" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275082 | M410CHV21233004 | 3" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 3" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275083 | M410CHV21233005 | 12" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 12" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275084 | M410CHV21233006 | 16" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 16" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275085 | M410CHV21233007 | 8" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 8" Swing Check Valve, BS 1868, Class 150, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275086 | M410CHV21233008 | 10" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 10" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275087 | M410CHV21233009 | 16" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 16" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275088 | M410CHV21233010 | 6" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 6" Swing Check Valve, BS 1868, Class 300, Raised Face, Bolted Cover, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275089 | M410CHV21263001 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275090 | M410CHV21263002 | 6" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 6" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275091 | M410CHV21263003 | 8" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 8" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275092 | M410CHV21263004 | 14" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 14" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275093 | M410CHV21263005 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 10" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275094 | M410CHV21263006 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 12" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275095 | M410CHV21263007 | 14" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 14" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Flat Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270011 | M410MOV413 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270012 | M410MOV414 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270013 | M410MOV415 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270014 | M410MOV416 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270015 | M410MOV417 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270016 | M410MOV420 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PT412 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270017 | M410MOV421A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270018 | M410MOV421B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270019 | M410MOV422A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270020 | M410MOV422B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270021 | M410MOV423 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270022 | M410MOV426 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270023 | M410MOV427A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270024 | M410MOV427B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270025 | M410MOV427C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270026 | M410MOV427D | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001D | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270027 | M410MOV428A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270028 | M410MOV428B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270029 | M410MOV428C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270030 | M410MOV428D | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L001D | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270031 | M410MOV429 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270032 | M410MOV431 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270033 | M410MOV438A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L011A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270034 | M410MOV438B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L011B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270035 | M410MOV439A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L011A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270036 | M410MOV439B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L011B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270037 | M410MOV440 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270038 | M410MOV442 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270039 | M410MOV443 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270040 | M410MOV444 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PT412 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270041 | M410MOV600A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270042 | M410MOV600B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270043 | M410MOV600C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P006C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270044 | M410MOV601A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270045 | M410MOV601B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270046 | M410MOV601C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P006C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270047 | M410MOV660 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270048 | M410MOV661 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270049 | M410MOV662 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270050 | M410MOV419 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270051 | M410MOV408 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270052 | M410MOV400 | MOTOR OPERATED VALVE | JET A1 PIG LAUNCHER MOTOR OPERATED VALVE |  | MOV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270053 | M410MOV425 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270054 | M410MOV430 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270055 | M410MOV441 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270056 | M410MP005A | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR FOR MUS-ADIA JET A1 BOOSTER PUMP 5-A |  | MOTOR | M410P005A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP005A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969270057 | M410MP006A | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR OF MUS-ADIA JET A1 BOOSTER PUMP 6-A |  | MOTOR | M410P006A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP006A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270058 | M410MP005B | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR FOR MUS-ADIA JET A1 BOOSTER PUMP 5-B |  | MOTOR | M410P005B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP005B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969270059 | M410MP006B | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR OF MUS-ADIA JET A1 BOOSTER PUMP 6-B |  | MOTOR | M410P006B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP006B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270060 | M410MP005C | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR FOR MUS-ADIA JET A1 BOOSTER PUMP 5-C |  | MOTOR | M410P005C | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP005C-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969270061 | M410MP006C | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR OF MUS-ADIA JET A1 BOOSTER PUMP 6-C |  | MOTOR | M410P006C | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP006C-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270062 | M410MP024A | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR OF DHAFRA JP8 MAIN LINE PUMP-A |  | MOTOR | M410P024A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP024A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969270063 | M410MP024B | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR OF DHAFRA JP8 MAIN LINE PUMP-B |  | MOTOR | M410P024B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP024B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969270064 | M410MP024C | Electric Motor HV Cage-Induction - Hazardous Area | MOTOR OF DHAFRA JP8 MAIN LINE PUMP-C |  | MOTOR | M410P024C | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP024C-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969269211 | M410P001A | ALAIN ULG BOOSTER CENTRIFUGAL PUMP. | AL AIN ULG BOOSTER PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269212 | M410P001B | ALAIN ULG BOOSTER CENTRIFUGAL PUMP. | AL AIN ULG BOOSTER PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270065 | M410MP023A | Electric Motor LV Cage-Induction - Hazardous Area | MOTOR OF MUSSAFAH-ALDHAFRA JP-8 BOSSTER PUMP-A |  | MOTOR | M410P023A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP023A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270066 | M410MP023B | Electric Motor LV Cage-Induction - Hazardous Area | MOTOR OF MUSSAFAH-ALDHAFRA JP-8 BOSSTER PUMP-B |  | MOTOR | M410P023B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP023B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270067 | M410MP023C | Electric Motor LV Cage-Induction - Hazardous Area | MOTOR OF MUSSAFAH-ALDHAFRA JP-8 BOSSTER PUMP-C |  | MOTOR | M410P023C | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP023C-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270068 | M410P045A | ANTI-STATIC DOSING RECIPROCATING PUMP. | ANTI-STATIC CHEMICAL DOSING PUMP 410ME002. |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270069 | M410P045B | ANTI-STATIC DOSING RECIPROCATING PUMP. | ANTI-STATIC CHEMICAL DOSING PUMP |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270070 | M410P046A | ANTI-STATIC DILUENT RECIPROCATING PUMP. | ANTI-STATIC DILUENT PUMPS |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270071 | M410P046B | ANTI-STATIC DILUENT RECIPROCATING PUMP. | ANTI-STATIC DILUENT PUMPS |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270072 | M410T023 | NEAT CORROSION INHIBITOR CHEMICAL SRORAGE TANK | NEAT CORROSION INHIBITOR CHEMICAL SRORAGE TANK |  | VESSEL | M410ME010 | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270073 | M410MP013A | MOTOR FOR NEAT DYE (BLUE) INJECTION PUMPS 410-P-013A | MOTOR FOR NEAT DYE (BLUE) INJECTION PUMPS 410-P-013A |  | MOTOR | M410ME001 | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP013A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270074 | M410MP013B | MOTOR FOR NEAT DYE (BLUE) INJECTION PUMPS 410-P-013B | MOTOR FOR NEAT DYE (BLUE) INJECTION PUMPS 410-P-013B |  | MOTOR | M410ME001 | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP013B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270075 | M410P013A | BLUE DYE INJECTION RECIPROCATING PUMP. | BLUE DYE INJECTION PUMP 410ME001. |  | PURE | M410ME001 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270076 | M410P013B | BLUE DYE INJECTION RECIPROCATING PUMP. | BLUE DYE INJECTION PUMP 410ME001. |  | PURE | M410ME001 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484409 | M410DAFHK2 | DAF HOOK LIFT TRUCK # 2, BIG FLOW FIRE | AD 79465-12 DAF HOOKLIFT TRUCK #2 BIG FLOW PACKAGE. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 5 | 10 | 1 | 5 | 4.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270078 | M410TML001C | OFF CIRCULT TAP CHANGER | OFF CIRCULT TAP CHANGER |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TML001C-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-009-M6
969270079 | M410TML001D | OFF CIRCULT TAP CHANGER | OFF CIRCULT TAP CHANGER |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TML001D-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-009-M6
969270080 | M410EA093A | OIL COOLER FOR COMPRESSOR | OIL COOLER FOR COMPRESSOR |  | HEATEXHR | M410K001A | 3 | HEATEXHR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA093A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270081 | M410EA093B | OIL COOLER FOR COMPRESSOR | OIL COOLER FOR COMPRESSOR |  | HEATEXHR | M410K001B | 3 | HEATEXHR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA093B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270082 | M410PDT752A | Oil Filter Diff. pressure Transmitter | Oil Filter Diff. pressure Transmitter |  | PRES_TX | M410K001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT752A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270083 | M410PDT752B | Oil Filter Diff. pressure Transmitter | Oil Filter Diff. pressure Transmitter |  | PRES_TX | M410K001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT752B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270086 | M410L092A | OIL FILTER FOR COMPRESSOR | OIL FILTER FOR COMPRESSOR |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270087 | M410L092B | OIL FILTER FOR COMPRESSOR | OIL FILTER FOR COMPRESSOR |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270088 | M410LT751A | OIL LEVEL TRANSMITTER | OIL LEVEL TRANSMITTER |  | LVL_TX | M410K001A | 3 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270089 | M410LT751B | OIL LEVEL TRANSMITTER | OIL LEVEL TRANSMITTER |  | LVL_TX | M410K001B | 3 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270090 | M410P091A | LUB OIL PUMP FOR 410K001A. | OIL PUMP FOR COMPRESSOR |  | PUCEOH | M410K001A | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P091A-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969270091 | M410P091B | LUB OIL PUMP FOR 410K001B. | OIL PUMP FOR COMPRESSOR |  | PUCEOH | M410K001B | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P091B-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969270092 | M410P092A | LUB OIL PUMP FOR 410K001A. | OIL PUMP FOR COMPRESSOR |  | PUCEOH | M410K001A | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P092A-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969270093 | M410P092B | LUB OIL PUMP FOR 410K001B. | OIL PUMP FOR COMPRESSOR |  | PUCEOH | M410K001B | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P092B-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969270094 | M410MK001AOP | OIL PUMP MOTOR FOR COMPRESSOR | OIL PUMP MOTOR FOR COMPRESSOR |  | MOTOR | M410P092A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MK001AOP-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969270095 | M410MK001BOP | OIL PUMP MOTOR FOR COMPRESSOR | OIL PUMP MOTOR FOR COMPRESSOR |  | PUMPS | M410P092B | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270273 | M410PG739B | PRESSURE GAUGES | ANTI-STATIC PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270274 | M410PG740A | PRESSURE GAUGES | ANTI-STATIC PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270275 | M410PG740B | PRESSURE GAUGES | ANTI-STATIC PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270276 | M410PSV001B | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410V006 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270277 | M410PSV200 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L008A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270278 | M410PSV201 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L008B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270279 | M410PSV202 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L009A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270280 | M410PSV203 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L009B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270281 | M410PSV400A | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L005A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270282 | M410PSV400B | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L005B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270283 | M410PSV400C | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L005C | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270284 | M410PSV400D | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L005D | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270285 | M410PSV400E | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L005E | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270286 | M410PSV401 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L006A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270287 | M410PSV402 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L006B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278863 | PL318CCTV072 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278864 | PL318CCTV073 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278865 | PL318CCTV074 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278866 | PL318CCTV075 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278867 | PL318CCTV076 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278868 | PL318CCTV077 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278869 | PL318CCTV078 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278870 | PL318CCTV079 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278871 | PL318CCTV080 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278872 | PL318CCTV081 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278873 | PL318CCTV082 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278874 | PL318CCTV083 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278875 | PL318CCTV084 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278876 | PL318CCTV085 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278877 | PL318CCTV086 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278878 | PL318CCTV087 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278879 | PL318CCTV088 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278880 | PL318CCTV089 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278881 | PL318CCTV090 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278882 | PL318CCTV091 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278883 | PL318CCTV092 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278884 | PL318CCTV093 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278885 | PL318CCTV094 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278886 | PL318CCTV095 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278887 | PL318CCTV096 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278888 | PL318CCTV097 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278889 | PL318CCTV098 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278890 | PL318CCTV099 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278891 | PL318CCTV100 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278892 | PL318CCTV101 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278893 | PL318CCTV102 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278894 | PL318CCTV103 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278895 | PL318CCTV104 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278896 | PL318CCTV105 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278897 | PL318CCTV106 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278898 | PL318CCTV107 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278899 | PL318CCTV108 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278900 | PL318CCTV109 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278901 | PL318CCTV110 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278902 | PL318CCTV111 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278903 | PL318CCTV112 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278904 | PL318CCTV113 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278905 | PL318CCTV114 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278906 | PL318CCTV115 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278907 | PL318CCTV116 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278908 | PL318CCTV117 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278909 | PL318CCTV118 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278910 | PL318CCTV119 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278911 | PL318CCTV120 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278912 | PL318CCTV121 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278913 | PL318CCTV122 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278914 | PL318CCTV123 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278915 | PL318CCTV124 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278916 | PL318CCTV125 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278917 | PL318CCTV126 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278918 | PL318CCTV127 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278919 | PL318CCTV128 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278920 | PL318CCTV129 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278921 | PL318CCTV130 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278922 | PL318CCTV131 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278923 | PL318CCTV132 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278924 | PL318CCTV133 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278925 | PL318CCTV134 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278926 | PL318CCTV135 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278927 | PL318CCTV136 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278928 | PL318CCTV137 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 1 | CCTVSEC | 0 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278929 | PL318CCTV138 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278930 | PL318CCTV139 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278931 | PL318CCTV140 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278932 | PL318CCTV141 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269300 | M410BAV21243051 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37147 | UTOYOTA52336 | 12 / 52336 - TOYOTA AUXION. | TOYOTA AUXION 12 / 52336 (MAINT. S/H). |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA52336UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 06/08/18 | MM-PM-029-M1
969175419 | M410CCTV005 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera SW of Tank 6 |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175420 | M410CCTV006 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera East of ITTP House |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175421 | M410CCTV007 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera North of Tank 1. |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175422 | M410CCTV008 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera North of Tank 10. |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175423 | M410CCTV009 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera South of evaporation pond IRP2. |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175424 | M410CCTV010 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera East of Pump House 4. |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175425 | M410CCTV011 | Indoor CCTV Camera | CCTV Camera Switch Gear Room IRP2 Sub Station Bldng |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175426 | M410CCTV012 | Indoor Camera (Fixed Dome) | CCTV PAN/TILT Camera Rack Room SIS BLDG. |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175427 | M410FOSR001 | Fiber Optical Subrack | Fiber Optical Subrack |  | CCTV_SYS | M410TEL | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175428 | M410FOSR002 | Fiber Optical Subrack | Fiber Optical Subrack |  | CCTV_SYS | M410TEL | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175429 | M410LS001 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-004 NE SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175430 | M410LS002 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-002 WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175431 | M410LS003 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-002 WS SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175432 | M410LS004 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-007 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175433 | M410LS005 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-005 NW SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175434 | M410LS006 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-006 WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175435 | M410LS007 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-010 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175436 | M410LS008 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-010 NW SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175437 | M410LS009 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-009 WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175438 | M410LS010 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-009 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175439 | M410LS013 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-ON THE POLE- SOUTH OF TANK-016 |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175440 | M410LS014 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK016-NORTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175441 | M410LS015 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK012-NORTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175442 | M410LS016 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK012-POND EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175443 | M410LS017 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK OIL NEAR POND SW ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175444 | M410LS018 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK013 WS SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175445 | M410LS019 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK015 SOUTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175446 | M410LS025 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ROOF-NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175447 | M410LS026 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING NEAR DIESEL GENERATOR-EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175448 | M410LS027 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ON ROOF-SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175449 | M410LS028 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ROOF-WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175450 | M410LS029 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS BUILDING ON ROOF-NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175451 | M410LS030 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS BUILDING ON ROOF-WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175452 | M410LS034 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-MAIN CONTROL BUILDING ON ROOF WEST SIDE ON WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175453 | M410LS035 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-MAIN CONTROL BUILDING ON ROOF EAST SIDE ON WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175454 | M410LS039 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ON ROOF EAST SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175455 | M410LS040 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ON ROOF EAST SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175456 | M410LS044 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-GUARD HOUSE(EXISTING SECURITY ROOM) |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175457 | M410LS047 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-SECURITY SUPERVISOR OFFICE-SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175458 | M410LS049 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR AT FIRE STATION BUILDING ON ROOF-EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175459 | M410LS050 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR AT FIRE STATION BUILDING ON ROOF-NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175460 | M410LS054 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-MAIN CONTROL BUILDING ON ROOF SOUTH SIDE SIDE ON WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175461 | M410LS100 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ON ROOF-EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175462 | M410LS106 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS BUILDING ON ROOF-SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175463 | M410LS107 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS BUILDING ON ROOF-EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175464 | M410LS116 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ON ROOF SOUTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175465 | M410LS117 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING ON ROOF NORTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175466 | M410LS126 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-FIRE STATION BUILDING ON ROOF WEST SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175467 | M410LS127 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-FIRE STATION BUILDING ON ROOF WEST SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175468 | M410LS131 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT MAIN CONTROL BUILDING ON ROOF NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175469 | M410LS132 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT RACK ROOM NEAR VESDA PANEL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175470 | M410LS136 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE BUILDING ON ROOF-WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175471 | M410LS137 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE BUILDING ON ROOF-WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175472 | M410LS141 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE BUILDING ON ROOF SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175473 | M410LS142 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE BUILDING ON ROOF EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175474 | M410LS146 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-ADMN BUILDING ON ROOF-NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175475 | M410LS147 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-ADMN BUILDING ON ROOF-EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175476 | M410LS153 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT ADMN BUILDING ON ROOF-NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175477 | M410LS154 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT ADMN BUILDING ON ROOF-WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175478 | M410LS160 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-116 WS SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175479 | M410LS161 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR- NEAR TANK-111 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175480 | M410LS162 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-115 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175481 | M410LS163 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-113 WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175482 | M410LS164 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-120 WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175483 | M410LS165 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-117 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175484 | M410LS166 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR FIRE WATER TANK WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175485 | M410LS167 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR NEW ADMIN BUILDING EAST SIDE EXIT DOOR AT POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175486 | M410LS168 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-105 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175487 | M410LS169 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-106 WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175488 | M410LS170 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-104 WEST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175489 | M410LS171 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK 104 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175490 | M410LS172 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR ADNOC TANK-101 EAST SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175491 | M410LS173 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK 101 SOUTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175492 | M410LS174 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-103 SOUTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175493 | M410LS175 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-103 SOUTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175494 | M410LS176 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-118 NORTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175495 | M410LS177 | Loud Speaker with J/B-Outdoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR TANK-119 NORTH SIDE ON POLE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175496 | M410LS031 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR NEAR 410-FACP-001 NORTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175497 | M410LS032 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS ROOM EAST SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175498 | M410LS033 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS AC ROOM, NEAR ELECTRICAL PANEL NORTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175499 | M410LS036 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT HVAC ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175500 | M410LS037 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT HALLWAY NEAR PTW COORDINATION BOARD |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175501 | M410LS038 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT LOBBY NEAR TELECOM ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175502 | M410LS041 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-OFFICE DOCUMENT ROOM WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175503 | M410LS042 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR EMERGENCY DOOR SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175504 | M410LS043 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SUBSTATION MAIN DOOR |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175505 | M410LS046 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SECURITY OFFICE-SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175506 | M410LS051 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-HALFWAY FIRST FLOOR FIRE STATION BUILFING |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175507 | M410LS052 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-HALFWAY NEAR PANTRY AT FIRE STATION BUILDING |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175508 | M410LS053 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-WORKSHOP LAB ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175509 | M410LS101 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SWGR ROOM NEAR 410-FACP-002-EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175510 | M410LS102 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-MCM ROOM-WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175511 | M410LS103 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SWGR ROOM NEAR FU006 ICP EAST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175512 | M410LS104 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SWGR ROOM NEAR 410-SP-011 ELECTRICAL PANEL WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175513 | M410LS105 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SWGR ROOM NEAR EMERGENCY DOOR WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175514 | M410LS108 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS RACK ROOM-SOUTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175628 | M410MOV0707 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0707-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969175967 | M410CHV2304001 | Check Valve | Check Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485971 | M410FLPOD1 | FLOATING PUMPS STORAGE & TRANSPORTER POD. BIG FLOW FIRE FIGHTING SYSTEM. | FLOATING PUMPS STORAGE & TRANSPORTER POD, BIG FLOW FIRE FIGHTING SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175969 | M410HYD2306001 | 4-WAY HYDRANT | 4-WAY HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175970 | M410HYD2306002 | 4-WAY HYDRANT W/ WATER MONITOR | 4-WAY HYDRANT W/ WATER MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175971 | M410FOM738 | 23,000 LITRE SEMI FIXED STORAGE FOAM TANKS BIG FLOW SYSTEM. | 23000 L FOAM TANKS BIG FLOW SEMI FIXED STORAGE TANK (NORTH). |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175972 | M410FFE2306002 | CO2 EXTINGUISHER(5KG) | CO2 EXTINGUISHER(5KG) |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175973 | M410FFE2306003 | CO2 EXTINGUISHER(6KG) | CO2 EXTINGUISHER(6KG) |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175974 | M410FFE2306004 | CO2 EXTINGUISHER(9KG) | CO2 EXTINGUISHER(9KG) |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175975 | M410FFE2306005 | CO2 EXTINGUISHER(50KG) | CO2 EXTINGUISHER(50KG) |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175976 | M410FFE2307001 | First Aid Rim Seal Protection System | First Aid Rim Seal Protection System |  |  | M410SYS | 1 | F&G_RST | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Low | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175629 | M410MOV0708 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0708-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/12/18 | ME-PM-002-M6
969175977 | M410INS2308001 | INERGEN GAS SYSTEM | INERGEN GAS SYSTEM |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Low | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175978 | M410HVAC2309001 | HVAC SYSTEM | HVAC SYSTEM |  | HVAC_FLT | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175979 | M410FU001 | FOAM STORAGE FACILITY | FOAM STORAGE FACILITY |  |  | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184837 | M410TML001B | Transformer and NER | Transformer and NER |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TML001B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 04/09/18 | ME-PM-009-M6
969184838 | M410MMS0011A | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0011A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184839 | M410MMS001A | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS001A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184840 | M410MMS0012A | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0012A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184841 | M410MMS0013A | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0013A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184842 | M410MMS0014A | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0014A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184843 | M410MMS0015A | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0015A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184844 | M410MMS0016A | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0016A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184845 | M410MMS001AB | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS001AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184846 | M410MMS0011AB | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0011AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184847 | M410MMS0011B | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0011B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184848 | M410MMS001B | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS001B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184849 | M410MMS0012B | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0012B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184850 | M410MMS0013B | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0013B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184851 | M410MMS0014B | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0014B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184852 | M410MMS0015B | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0015B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184853 | M410MMS0016B | Panel for 11KV Switchgear | 11KV Switchgear |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MMS0016B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184854 | M410MS0011A | 3.3KV Switchgear Panel | MAIN INCOMING PANEL-A |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0011A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184855 | M410MS001A | 3.3KV Switchgear Panel | BUS-A VT PANEL(3.3KV/SQRT3/110/SQRT3) |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS001A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184856 | M410MS0012A | 3.3KV Switchgear Panel | PANEL FOR MUS-ALAIN ULG MAINLINE PUMP-A(410-MP-002A)-950KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0012A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969195511 | M410FU416 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195512 | M410FU417 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195513 | M410FU418 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195514 | M410FU419 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195515 | M410FU420 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195516 | M410FU421 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195517 | M410FU422 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267911 | PL100PLR002 | Scraper Receiver Gas Oil Pipeline | Scraper Receiver Gas Oil Pipeline |  | PIPING | PL100MISC | 3 | PIPING | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267912 | PL100BAV21242001 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267913 | PL100BAV21242002 | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267914 | PL100BAV21242003 | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267915 | PL100BAV21242004 | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267916 | PL100BAV21242005 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267917 | PL100BAV21242006 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267918 | PL100BAV21242007 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969267919 | PL100BAV21242008 | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275267 | M410MOV440 | Valve, Ball. 10", 300#, RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270037 | CONTHNDV | M410PLR007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275268 | M410MOV441 | Valve, Ball. 10", 300#, FB, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270055 | CONTHNDV | M410PLR007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275269 | M410MOV442 | Valve, Ball. 10", 300#, RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270038 | CONTHNDV | M410PLR007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275270 | M410MOV443 | Valve, Ball. 2", 300#, RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270039 | CONTHNDV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275271 | M410MOV444 | Valve, Ball. 2", 600#, RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270040 | CONTHNDV | M410PT412 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275069 | M410MOV445 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275272 | M410MOV445 | Valve, Ball. 12", 900#, RF, Body ASTM A 105, Trim SS316L, MOTOR OPERATED | MOTOR OPERATED VALVE | 969275069 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275273 | M410MOV600A | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270041 | CONTHNDV | M410P006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275274 | M410MOV600B | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270042 | CONTHNDV | M410P006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275275 | M410MOV600C | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270043 | CONTHNDV | M410P006C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275276 | M410MOV601A | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270044 | CONTHNDV | M410P006A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275277 | M410MOV601B | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270045 | CONTHNDV | M410P006B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275278 | M410MOV601C | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270046 | CONTHNDV | M410P006C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275279 | M410MOV660 | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270047 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275280 | M410MOV661 | Valve, Ball. 16", 300#, RF, Body ASTM A 105, Trim SS316, MOTOR OPERATED | MOTOR OPERATED VALVE | 969270048 | CONTHNDV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275573 | PL312SPS102 | PASSIVE COOLING SHELTER - SV.1 | PASSIVE COOLING SHELTER - SV.1 |  | PACKAGE | PL312PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275574 | PL312SPS201 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL312SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275575 | PL312SPS202 | PASSIVE COOLING SHELTER - SV.2 | PASSIVE COOLING SHELTER - SV.2 |  | PACKAGE | PL312PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275576 | PL312SPS301 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL312SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275577 | PL312SPS302 | PASSIVE COOLING SHELTER - SV.3 | PASSIVE COOLING SHELTER - SV.3 |  | PACKAGE | PL312PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275578 | PL312SPS401 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL312SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275579 | PL312SPS402 | PASSIVE COOLING SHELTER - SV.4 | PASSIVE COOLING SHELTER - SV.4 |  | PACKAGE | PL312PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275580 | PL312SPS501 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL312SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275581 | PL312SPS502 | PASSIVE COOLING SHELTER - SV.5 | PASSIVE COOLING SHELTER - SV.5 |  | PACKAGE | PL312PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275582 | PL312SPS601 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL312SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275583 | PL312SPS602 | PASSIVE COOLING SHELTER - SV.6 | PASSIVE COOLING SHELTER - SV.6 |  | PACKAGE | PL312PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275584 | PL312TE005 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275585 | PL312TE010 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275586 | PL312TE31201A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275587 | PL312TE31201B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275588 | PL312TE31202A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275589 | PL312TE31202B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275590 | PL312TE31203A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275591 | PL312TE31203B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275592 | PL312TE31204A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275593 | PL312TE31204B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275594 | PL312TE31205A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275595 | PL312TE31205B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275596 | PL312TE31206A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275597 | PL312TE31206B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275598 | PL312TE31301A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275599 | PL312TE31301B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275600 | PL312TE31302A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275601 | PL312TE31302B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275602 | PL312TE31303A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275603 | PL312TE31303B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275604 | PL312TE31304A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275605 | PL312TE31304B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275606 | PL312TE31305A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275607 | PL312TE31305B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275608 | PL312TE31306A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275609 | PL312TE31306B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL312TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275610 | PL312TG001A | Temperature gauge | Temperature gauge |  | INDICATR | PL312MISC | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275611 | PL312TG001B | Temperature gauge | Temperature gauge |  | INDICATR | PL312MISC | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275612 | PL312TG002A | Temperature gauge | Temperature gauge |  | INDICATR | PL312MISC | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275613 | PL312TG002B | Temperature gauge | Temperature gauge |  | INDICATR | PL312MISC | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275614 | PL312TSV001 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275615 | PL312TSV001A | THERMAL RELIEFE VALVE, TARIF, ULG | THERMAL RELIEFE VALVE, TARIF, ULG |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275616 | PL312TSV001B | THERMAL RELIEFE VALVE, TARIF, ULG | THERMAL RELIEFE VALVE, TARIF, ULG |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275617 | PL312TSV002 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275618 | PL312TSV002A | THERMAL RELIEFE VALVE, TARIF GAS OIL | THERMAL RELIEFE VALVE, TARIF GAS OIL |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275619 | PL312TSV002B | THERMAL RELIEFE VALVE, TARIF GAS OIL | THERMAL RELIEFE VALVE, TARIF GAS OIL |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275620 | PL312TSV003 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275621 | PL312TSV006 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275622 | PL312TSV007 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275623 | PL312TSV008 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | PL312VALVE | 1 | PSV | 0 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275624 | PL312TT001A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275625 | PL312TT001B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275626 | PL312TT002A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275627 | PL312TT002B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275628 | PL312TT004 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275629 | PL312TT005 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275630 | PL312TT009 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275631 | PL312TT010 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275632 | PL312TT31201A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275633 | PL312TT31201B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275634 | PL312TT31202A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275635 | PL312TT31202B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275636 | PL312TT31203A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275637 | PL312TT31203B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275638 | PL312TT31204A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275639 | PL312TT31204B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275640 | PL312TT31205A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275641 | PL312TT31205B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275642 | PL312TT31206A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275643 | PL312TT31206B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275644 | PL312TT31301A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275645 | PL312TT31301B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275646 | PL312TT31302A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275647 | PL312TT31302B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275648 | PL312TT31303A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275649 | PL312TT31303B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275650 | PL312TT31304A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275651 | PL312TT31304B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275652 | PL312TT31305A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275653 | PL312TT31305B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275654 | PL312TT31306A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275655 | PL312TT31306B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL312TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935582 | SADIATP13 |  | TEST POINT# 13 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935583 | SADIATP14 |  | TEST POINT# 14 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935584 | SADIATP15 |  | TEST POINT# 15 (C.P. AT A.D. INT'L AIRPORT) |  |  | SADIATP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935599 | SMCP1IJ2 |  | INSULATING JOINT 2 AT KM 16.8 (MUSSAFAH PROD.) |  |  | SMPIPE | 1 | PIPING | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 5 | 1 | 1 | 5 | 3.0969 | Low | Low | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935600 | SMTP1 |  | TEST POINT# 1 ( MUSSAFAH PRODUCT TRANS. P.L.) |  |  | SMTP | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936234 | M400MP016A | DRIVE, YES, VARIABLE FREQUENCY | MOTOR,ELECTRIC, Variable Speed Drive FOR ALAIN MAIN LINE PUMP JET A1, IP55, 1500 KW, 50 HZ, 3300 V, Ex d, ET 710 V2, EFNLB 11-125,EFNLQ 11-125 | 935852 | SWBOARD | M400P016A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP016A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 04/10/18 | ME-PM-013-M6
936235 | M400MP016B | DRIVE, YES, VARIABLE FREQUENCY | MOTOR,ELECTRIC, Variable Speed Drive MOTOR FOR MAIN LINE PUMP AL AIN, IP55, 1500 KW, 50 HZ, 3300 V, Ex d, ET 710 V2, EF NLB | 935853 | SWBOARD | M400P016B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP016B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 03/11/18 | ME-PM-013-M6
936236 | M400TG462 | THERMOMETER, DIAL, 0-120 DEG C , BIMETAL , 100MM , 1/2" NPT , 304 SS , BIMETALLI | LUBE OIL RETURN MAIN E MOTOR BEARING (400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936237 | M400UCP016A | PANEL CONTROL | ULG95/98/GO/JETA1/KEROSE M/LINE PUMP-PANEL |  |  | M400P016A | 1 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936238 | M400UCP016B | PANEL CONTROL | ULG95/98/GO/JETA1/KEROSE M/LINE PUMP-PANEL |  |  | M400P016B | 1 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936239 | M400UCP019 | PANEL CONTROL | OFF SPEC JET A1 MAIN LINE PUMP-PANEL |  |  | M400P019 | 1 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936240 | M400SSP16BR2 | SYSTEM, PUMP MECHANICAL SEAL | ULG95/98/GASOIL/JETA1/KEROSENE M/LINEPUMP SEAL SYS |  |  | M400P016B | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936241 | M400SSP18AR1 | SYSTEM, PUMP MECHANICAL SEAL | JET A1 MAIN LINE PUMP SEAL SYSTEM |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936242 | M400SSP18AR2 | SYSTEM, PUMP MECHANICAL SEAL | JET A1 MAIN LINE PUMP SEAL SYSTEM |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936243 | M400SSP18BR3 | SYSTEM, PUMP MECHANICAL SEAL | JET A1 MAIN LINE PUMP SEAL SYSTEM |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936244 | M400SSP18BR4 | SYSTEM, PUMP MECHANICAL SEAL | JET A1 MAIN LINE PUMP SEAL SYSTEM |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936245 | M400SSP19R1 | SYSTEM, PUMP MECHANICAL SEAL | OFF SPEC JET A1 MAIN LINE PUMP SEAL SYSTEM |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936246 | M400SSP19R2 | SYSTEM, PUMP MECHANICAL SEAL | OFF SPEC JET A1 MAIN LINE PUMP SEAL SYSTEM |  |  | M400SSP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936247 | M400TG406 | THERMOMETER, DIAL, 0-120 DEG C , BIMETAL , 350MM , 100MM , 1/2" NPT , BOTTOM , 3 | PLAN 53 B - TEMPERATURE GAUGE (M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936248 | M400TG407 | THERMOMETER, DIAL, 0-120 DEG C , BIMETAL , 350MM , 100MM , 1/2" NPT , BOTTOM , 3 | PLAN 53 B - TEMPERATURE GAUGE (M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936249 | M400TG421 | THERMOMETER, DIAL, 0-120 DEG C , BIMETAL , 350MM , 100MM , 1/2" NPT , BOTTOM , 3 | PLAN 53 B - TEMPERATURE GAUGE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936250 | M400TG422 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 350MM , 100MM , | PLAN 53 B - TEMPERATURE GAUGE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936251 | M400TG436 | THERMOMETER, DIAL, 0-120 DEG C , 350MM , 100MM , 1/2" MNPT , BOTTOM , 304 SS , B | PLAN 53 B - TEMPERATURE GAUGE (M400P018A) | 935828 |  | M400P018A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936252 | M400TG437 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 350MM , 100MM , | PLAN 53 B - TEMPERATURE GAUGE (M400P018A) | 935828 |  | M400P018A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936253 | M400TG451 | THERMOMETER, DIAL, 0-120 DEG C , 350MM , 100MM , 1/2" MNPT , BOTTOM , 304 SS , B | PLAN 53 B - TEMPERATURE GAUGE (M400P018B) | 935829 |  | M400P018B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936254 | M400TG452 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 350MM , 100MM , | PLAN 53 B - TEMPERATURE GAUGE (M400P018B) | 935829 |  | M400P018B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936255 | M400TG464 | THERMOMETER, DIAL, 0-120 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | LUBE OIL RETURN MAIN MOTOR BEARING DE ( (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936287 | M400PG407 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 G , 100MM , 1/2" NPT , SS , BOTTOM , | PLAN 53 B - PRESSURE GAUGE(M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936288 | M400PG408 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 G , 100MM , 1/2" NPT , SS , BOTTOM , | PLAN 53 B - PRESSURE GAUGE(M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936289 | M400PG422 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 G , 100MM , 1/2" NPT , SS , BOTTOM , | PLAN 53 B - PRESSURE GAUGE(M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936290 | M400PG423 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 G , 100MM , 1/2" NPT , SS , BOTTOM , | PLAN 53 B - PRESSURE GAUGE (M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936291 | M400PG437 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 , 100MM , 1/2" NPT , SS , SS , BOTTO | PLAN 53 B - PRESSURE GAUGE (M400P018A) | 935828 |  | M400P018A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936292 | M400PG438 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 , 100MM , 1/2" NPT , SS , SS , BOTTO | PLAN 53 B - PRESSURE GAUGE (M400P018A) | 935828 |  | M400P018A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936293 | M400PG452 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 , 100MM , 1/2" NPT , SS , SS , BOTTO | PLAN 53 B - PRESSURE GAUGE (M400P018B) | 935829 |  | M400P018B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936294 | M400LMK018B3 | MOTOR,ELECTRIC, SEAL OIL COOLER FAN 'A' FOR M400MP018B, -, II 3 G Eex Na II T3, 0.55KW, 50HZ, 415V, S1, IP55, AMGK-090LB-06A, 6205-2Z C3, IM B3, 945RPM, 3, AMP, OHM, F, 18KG, SAE, ****, V, AMP | SEAL OIL COOLER FAN 'A' FOR 400MP018B,JET A1 MAIN LINE PUMP MOTOR |  | MOTOR | M400P018B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M400LMK018B3-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/11/18 | ME-PM-014-M6
936295 | M400LMK018B4 | MOTOR,ELECTRIC, SEAL OIL COOLER FAN 'B' FOR M400MP018B, -, II 3 G Eex Na II T3, 0.55KW, 50HZ, 415V, S1, IP55, AMGK 090LB 06A, 6205-2Z C3, IM B3, 945RPM, 3, AMP, OHM, F, 18KG, SAE, ****, V, AMP | SEAL OIL COOLER FAN 'B' FOR 400MP018B,, JET A1 MAIN LINE PUMP MOTOR |  | MOTOR | M400P018B | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M400LMK018B4-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/11/18 | ME-PM-014-M6
936296 | M400LMK019A3 | MOTOR, ELECTRIC, - , II 3 G Eex Na II T3 , 0.55KW , 50HZ , 415V , S1 , IP55 , IM | MOTOR FOR SEAL OIL COOLER FAN 'A' FOR 400MP019 |  | MOTOR | M400P019 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK019A3-ME1 | INACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-014-M6
936297 | M400LMK019A4 | MOTOR, ELECTRIC, - , II 3 G Eex Na II T3 , 0.55KW , 50HZ , 415V , S1 , IP55 , IM | MOTOR FOR SEAL OIL COOLER FAN 'B' FOR 400MP019 |  | MOTOR | M400P019 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 1 |  | M400LMK019A4-ME1 | INACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-014-M6
936298 | M400PG453 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 , 100MM , 1/2" NPT , SS , SS , BOTTO | PLAN 53 B - PRESSURE GAUGE (M400P018B) | 935829 |  | M400P018B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936299 | M400PG467 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 G , 100MM , 1/2" NPT , SS , SS , SS | PLAN 53 B - PRESSURE GAUGE (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936300 | M400PG468 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 G , 100MM , 1/2" NPT , SS , SS , SS | PLAN 53 B - PRESSURE GAUGE (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936301 | M400PI421C | LOOP, PRESSURE INDICATOR INSTRUMEN, YOKOGAWA , EBS7N-07DN/KU2/D4/M15 , 0-40 KG | PLAN 53 B - PRESSURE (M400P016B) | 935827 | OPENLOOP | M400P016B | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI421C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 19/10/18 | MC-PM-007-Y1
936302 | M400PT407 | TRANSMITTER, PRESSURE, GAGE , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , 1/2" - | PLAN 53 B - PRESSURE TRANSMITTER (M400P016A) | 935826 | PRES_TX | M400P016A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400PT407-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/09/18 | MC-PM-007-Y1
936303 | M400PT422 | TRANSMITTER, PRESSURE, ELECTRONIC , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , | PLAN 53 B - PRESSURE TRANSMITTER (M400P016B) | 935827 | PRES_TX | M400P016B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400PT422-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/10/18 | MC-PM-007-Y1
936304 | M400PT423 | TRANSMITTER, PRESSURE, ELECTRONIC , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , | PLAN 53 B - PRESSURE TRANSMITTER (M400P016B | 935827 | PRES_TX | M400P016B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400PT423-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 20/10/18 | MC-PM-007-Y1
936504 | U29TT702 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0-100 DEG C , 4-20mA W | TEMP.TR. NAPHTHA REFORMATE/HSGO LINE TO SV STATION | 939568 | TEMP_TX | U29TI702 | 2 | TEMP_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936505 | U29TT703 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0-100 DEG C , 4-20mA W | TEMP.TRANS.2902-L SCRAPER LAUNCHER TO SV STATION-7 | 939569 | TEMP_TX | U29TI703 | 2 | TEMP_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936512 | U29TT710 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0 - 120 , 4-20mA WITH | TEMP.TRANSMTR. SRR MAIN PUMPS 2937JA/B/C TO 2903L | 939576 | TEMP_TX | U29TI710 | 2 | TEMP_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936513 | U29TT711 | TRANSMITTER, TEMPERATURE, TEMPERATURE TRANSMITTER-SMART , 0-100 DEG C , 4-20mA W | TEMP.TRANSMTR. 2903L SCRAPER LAUNCHER-SV STATION-7 | 939579 | TEMP_TX | U29TI711 | 2 | TEMP_TX | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936514 | M30DPT361 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0- | Filter Coal. Sep. 30-L-006 Filter DP | 939656 | DP_TXTR | M30DPI361 | 2 | DP_TXTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936515 | M30DPT362 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIFFERENTIAL PRESSURE TRANSMITTER-SMART , 0- | Filter Coal. Sep. 30-L-007 Filter DP | 939657 | DP_TXTR | M30DPI362 | 2 | DP_TXTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936516 | M30PT262 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 8 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. LOADING BAY FILTER COALESCER INLET |  | PRES_TX | M30PRESS | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936517 | PL300PT30101A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR. NAPHTHA/REFORMATE P/L UPSTREAM PR. PL300EOV30101 |  | PRES_TX | PL300SVS1 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30101A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-021-M2
936518 | PL300PT30101B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM PR.301EOV01 |  | PRES_TX | PL300SVS1 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30101B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-021-M2
936519 | PL300PT30102A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L UPSTREAM PR.301EOV02 |  | TRANS | PL300SVS2 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30102A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-021-M2
936520 | PL300PT30102B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM PR.301EOV02 |  | TRANS | PL300SVS2 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30102B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-021-M2
936521 | PL300PT30103A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L UPSTREAM PR.301EOV03 |  | TRANS | PL300SVS3 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30103A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-021-M2
936522 | PL300PT30103B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM PR.301EOV03 |  | TRANS | PL300SVS3 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30103B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-021-M2
936523 | PL300PT30104A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L UPSTREAM PR.301EOV04 |  | TRANS | PL300SVS4 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30104A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 26/05/19 | MC-PM-021-M2
969275930 | PL100BAV21243002 | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275931 | PL100BAV21243003 | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275932 | PL100BAV21243004 | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275933 | PL100BAV21243005 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275934 | PL100BAV21243006 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275935 | PL100BAV21243007 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195696 | M410FG063 | 4" 150# RF Flow Glass | 4" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195697 | M410FG064 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195698 | M410FG065 | 6" 150# RF Flow Glass | 6" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195699 | M410FG066 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195700 | M410FG067 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195701 | M410FG068 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195702 | M410FG069 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195703 | M410FG070 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195704 | M410FG071 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195705 | M410FG072 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195706 | M410FG073 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195707 | M410FG074 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195708 | M410FG075 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969272766 | M400TSV517 | 400P21A.B.C DISCHARG THERMAL RELIEF VALVE. | 400P21A.B.C DISCHARG THERMAL RELIEF VALVE. |  | VALVE | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207829 | M410DCP001 | PANEL FOR INTEGRATED PROTECTION CONTROL SYSTEM (IPCS) | PANEL FOR INTEGRATED PROTECTION CONTROL SYSTEM (IPCS) |  | SWBOARD | M410SCB | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M410DCP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 02/12/18 | ME-PNL1-PM-M6
969207868 | M410EXP003 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207828 | M410IRP001 | INTERPOSING RELAY PANEL | INTERPOSING RELAY PANEL |  | SWBOARD | M410SCB | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M410IRP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 19/12/18 | ME-PNL1-PM-M6
969207841 | M400POV571 | BALL VALVE 10" x 900LB, FOR MOV (SEQUENCIAL CONTROL/ESD VALVE) | ESD VALVE -NAPHTHA/REFORMATE P/L (OFF SPEC JET A1) | 936423 |  | M400VALVE | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207878 | M410EXP014 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207879 | M410EXP015 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207881 | M410EXP017 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936524 | PL300PT30104B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM PR.301EOV04 |  | TRANS | PL300SVS4 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30104B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/05/19 | MC-PM-021-M2
936525 | PL300PT30105A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L UPSTREAM PR.301EOV05 |  | TRANS | PL300SVS5 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30105A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-021-M2
936526 | PL300PT30105B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM PR.301EOV05 |  | TRANS | PL300SVS5 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30105B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-021-M2
936527 | PL300PT30106A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L UPSTREAM PR.301EOV06 |  | TRANS | PL300SVS6 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30106A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-021-M2
936528 | PL300PT30106B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 100 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM PR.301EOV06 |  | TRANS | PL300SVS6 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30106B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/05/19 | MC-PM-021-M2
936529 | PL300PT30107A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L UPSTREAM PR.301EOV07 |  | TRANS | PL300SVS7 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30107A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-021-M2
936530 | PL300PT30107B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0 - 120 , 4-20mA , 24V DC, 2 | PR.TR.NAPHTHA/REFORMATE P/L DOWNSTREAM PR.301EOV07 |  | TRANS | PL300SVS7 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30107B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/05/19 | MC-PM-021-M2
936531 | PL300PT30201A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. SRR P/L UPSTREAM PRESSURE-302EOV01 |  | TRANS | PL300SVS1 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30201A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-021-M2
936532 | PL300PT30201B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. SRR P/L DOWNSTREAM PRESSURE-302EOV01 |  | TRANS | PL300SVS1 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30201B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 09/02/19 | MC-PM-021-M2
936533 | PL300PT30202A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR. SRR P/L UPSTREAM PRESSURE-302-EOV-02 |  | TRANS | PL300SVS2 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30202A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-021-M2
936534 | PL300PT30202B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR.SRR P/L DOWNSTREAM PRESSURE-302-EOV-02 |  | TRANS | PL300SVS2 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30202B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/05/19 | MC-PM-021-M2
936535 | PL300PT30203A | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR.SRR P/L UPSTREAM PRESSURE-302-EOV-03 |  | TRANS | PL300SVS3 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30203A-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-021-M2
936536 | PL300PT30203B | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 0-100 , 4-20mA , 24V DC, 2 W | PR.TRANSMTR.SRR P/L DOWNSTREAM PRESSURE-302-EOV-03 |  | TRANS | PL300SVS3 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300PT30203B-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 08/04/19 | MC-PM-021-M2
938451 | M30TE261J | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100 , 0-200 DEG C , PLATINUM | Temp. at Loading Bay J |  | TEMP_ELE | M30MISC | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938452 | M400P205A | PUMP, CENTRIFUGAL | EFFLUENT OILY WATER PUMPS |  | PUCE | M400PUMP | 1 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P205A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 06/11/18 | MM-PM-017-M6
938453 | M400P205B | EFFLUENT OILY WATER PUMP | EFFLUENT OILY WATER PUMP |  | PUCE | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P205B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-017-M6
938454 | M400P305 | TRANSFER PUMP FOR PPD | TANK 301 POUR POINT DEPRESSER FILLING PUMP. |  | PUSC | M400PUMP | 3 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | M400P305-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/09/18 | MM-PM-036-M6
938455 | M400P306 | TANK 302 LUBRICITY IMPROVER FILLING PUMP. | TANK 302 LUBRICITY IMPROVER FILLING PUMP. |  | PUSC | M400T302 | 3 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | M400P306-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 22/10/18 | MM-PM-036-M6
938480 | M20P227C | PUMP | JP 8/JET A1 LOADING PUMPS |  | PUCE | M20PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938482 | M20P227D | PUMP | JP 8/JET A1 LOADING PUMPS |  | PUCE | M20PUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275716 | PL315SPS1302 | PASSIVE COOLING SHELTER - SV.13 | PASSIVE COOLING SHELTER - SV.13 |  | PACKAGE | PL315PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275717 | PL315TE31513A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL315TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275718 | PL315TE31513B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL315TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275719 | PL315TE31613A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL315TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275720 | PL315TE31613B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL315TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275721 | PL315TT31513A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL315TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275722 | PL315TT31513B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL315TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275723 | PL315TT31613A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL315TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275724 | PL315TT31613B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL315TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275725 | PL315XGH1301 | H2 GAS DETECTOR | H2 GAS DETECTOR |  | FG_DET | PL315GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275726 | PL315YYIS31513A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL315MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275727 | PL315YYIS31513B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL315MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275728 | PL315YYIS31613A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL315MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275729 | PL315YYIS31613B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL315MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275732 | PL318BAV21243001 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275733 | PL318BAV21243002 | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275734 | PL318BAV21243003 | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 4" S-80, Ball Valve Long Pattern Reduced Bore, API 6D, Class 900, Bevel End x Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275735 | PL318BAV21243004 | 12" 8.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe | 12" 8.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End x Raised Face, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, ASME B16.5, Fire Safe |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275736 | PL318BAV21243005 | 12" 8.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe | 12" 8.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 900, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/Devlon V, Fire Safe |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275737 | PL318BAV21243006 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275738 | PL318BB1001 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL318BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275739 | PL318BB1101 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL318BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275740 | PL318BB1201 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL318BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275741 | PL318BB1202 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL318BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275742 | PL318BB801 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL318BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275743 | PL318BB901 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL318BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275370 | PL325EOV32507 | ELECTRO HYDRAULIC VALVE, SV STATION-07 | ELECTRO HYDRAULIC VALVE, SV STATION-07 |  | TELECOM | PL325TELM | 2 | TELECOM | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275907 | PL325EOV32507 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 325-EOV-325-07 | ELECTRO HYDRAULIC VALVE, SV STATION-07 | 969275370 | MOV | PL325TELM | 2 | TELECOM | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275908 | PL325GAV21223001 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL325VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275909 | PL325GAV21223002 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL325VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275910 | PL325GDH701 | HC GAS DETECTOR | HC GAS DETECTOR |  | FG_DET | PL325GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275913 | PL325PG32507A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL325PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275914 | PL325PG32507B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL325PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275915 | PL325PT32507A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL325PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275916 | PL325PT32507B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL325PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275917 | PL325RTU001 | RTU Cabinet | RTU Cabinet |  | BLDGS | PL325MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275918 | PL325SCR701 | SOLAR POWER SYSTEM CONTROL PANEL | SOLAR POWER SYSTEM CONTROL PANEL |  | BLDGS | PL325SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275919 | PL325SPS701 | SOLAR POWER PANEL | SOLAR POWER PANEL |  |  | PL325SYS | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275920 | PL325SPS702 | PASSIVE COOLING SHELTER - SV.7 | PASSIVE COOLING SHELTER - SV.7 |  | PACKAGE | PL325PKG | [12 empty] | Non Critical |  | Low | N | Low | Y |  | 6 | p
969275921 | PL325TE32507A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL325TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275922 | PL325TE32507B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL325TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275923 | PL325TT32507A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL325TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275924 | PL325TT32507B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL325TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275925 | PL325XGH701 | H2 GAS DETECTOR | H2 GAS DETECTOR |  | FG_DET | PL325GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275926 | PL325YYIS32507A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL325MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275927 | PL325YYIS32507B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL325MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275945 | PL100FG211 | Sight Glass | Sight Glass |  | INDICATR | PL100FLOW | 3 | INDICATR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275946 | PL100FG311 | Sight Glass | Sight Glass |  | INDICATR | PL100FLOW | 3 | INDICATR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275947 | PL100FG411 | Sight Glass | Sight Glass |  | INDICATR | PL100FLOW | 3 | INDICATR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275948 | PL100TE400 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL100TEMP | 3 | TEMP_ELE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275949 | PL100MOV400 | Valve, Ball. 16", 300#, BW, Body ASTM A105, Trim SS316, MOTOR OPERATED | MOV (RUWAIS) SHEWIHAT RECIVING STATION. | 969265906 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275950 | PL100MOV400AA | Valve, Ball. 10", 150#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | MOV (RUWAIS) SHEWIHAT RECIVING STATION.(100-FT-400 METERING SKID) | 969265907 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400AA-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275951 | PL100MOV400AB | Valve, Ball. 8", 300#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | MOV (RUWAIS) SHEWIHAT RECIVING STATION. (100-FT-400 METERING SKID) | 969265908 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400AB-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275952 | PL100MOV400BA | Valve, Ball. 10", 150#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | MOV (RUWAIS) SHEWIHAT RECIVING STATION. (100-FT-400 METERING SKID) | 969265909 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400BA-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275953 | PL100MOV400BB | Valve, Ball. 10", 150#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | MOV (RUWAIS) SHEWIHAT RECIVING STATION. (100-FT-400 METERING SKID) | 969265910 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400BB-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275954 | PL100MOV401 | Valve, Ball. 16", 300#, BW+RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316L, MOTOR OPERATED | Ruwais Shweihat Gas oil Scrapper Receiver 100-PL-002 | 969265911 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV401-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275955 | PL100MOV402 | Valve, Ball. 16", 300#, BW+RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316L, MOTOR OPERATED | Ruwais Shweihat Gas oil Scrapper Receiver 100-PL-002 | 969265912 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV402-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275956 | PL100MOV403A | Valve, Ball. 16", 150#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | Gas oil P/L From Scrapper Receiver 100-V-001A Inlet | 969265913 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV403A-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275957 | PL100MOV403B | Valve, Ball. 16", 150#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | Gas oil P/L From Scrapper Receiver 100-V-001B Inlet | 969265914 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV403B-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275958 | PL100MOV404A | Valve, Ball. 16", 150#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | Gas oil P/L From Scrapper Receiver 100-V-001A Outlet | 969265915 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV404A-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275959 | PL100MOV404B | Valve, Ball. 16", 150#, RF, Body ASTM A 105/A216 Gr. WCB, Trim SS316, MOTOR OPERATED | Gas oil P/L From Scrapper Receiver 100-V-001B Outlet | 969265916 | CONTHNDV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV404B-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969275960 | PL100FLX001 | Flexible Hose, 3", 316SS | Flexible Hose, 3", 316SS |  | PACKAGE | PL100MISC | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | m
969275961 | PL100CPL002 | Quick Coupling, 3" 316SS | Quick Coupling, 3" 316SS |  | PACKAGE | PL100MISC | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | m
969275962 | PL100GAV21222002 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275963 | PL100GAV21222003 | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.75" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275964 | PL100GAV21232001 | 2" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 150, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275965 | PL100GAV21232002 | 2" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 | 2" Gate Valve, ISO 10434, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Flexible Wedge, ASME B16.5 |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275982 | M400VDR904 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 120 | 939613 | VALCH | M400T120 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484435 | M410NEP2 | #2 NEPTUNE 10K GPM SOURCE PUMP BIG FLOW SYSTEM. | #2 NEPTUNE UNIT 10K GPM BIG FLOW SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484436 | M410COM2 | #2 IRON MAN COMBO UNIT DOMINATOR / MONITOR WITH BOOSTER PUMP-10K GPM. BIG FLOW SYSTEM. | #2 IRON MAN COMBO UNIT DOMINATOR / MONITOR WITH BOOSTER PUMP-10K GPM. BIG FLOW SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484437 | M410DOM2 | #2 DOMINATOR WITH DUAL PUMPS 5K GPM EACH -BIG FLOW SYSTEM. | #2 DOMINATOR WITH DUAL PUMPS 5K GPM EACH -BIG FLOW SYSTEM. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969484414 | M410HOS3 | #3 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #3 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL PODS 3/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205044 | M410T031A | Level transmitter Fuel tank level | DIESEL DAY TANK (FIREWATER PUMP) | 969147435 | LVL_TX | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205045 | M410FWCP031A | PRESSURE TRANSDUCER | CONTROL PANEL FOR FIRE WATER PUMP 410-P-031A | 969195815 |  | M410P031A | 1 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275966 | PL100GLV21222001 | 0.75" Globe Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Plug Disc | 0.75" Globe Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Plug Disc |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275967 | PL100GLV21232001 | 2" Globe Valve, BS 1873, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 | 2" Globe Valve, BS 1873, Class 300, Raised Face, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A216 Grade WCB, Trim 13Cr, Plug Disc, ASME B16.5 |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275968 | PL100GAV21222001 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275970 | M400FM117 | METER,FLOW, ULTRASONIC | ON STORAG E TANK DRAIN LINE OF JET A1 | 939610 | FL_MTR | M400FLOW | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275971 | M400FM118 | METER,FLOW, ULTRASONIC | ON STORAG E TANK DRAIN LINE OF JET A1 | 939611 | FL_MTR | M400FLOW | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275972 | M400FM119 | METER,FLOW, ULTRASONIC | ON STORAG E TANK DRAIN LINE OF JET A1 | 939612 | FL_MTR | M400FLOW | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275973 | M400FM120 | METER,FLOW, ULTRASONIC | ON STORAG E TANK DRAIN LINE OF JET A1 | 939613 | FL_MTR | M400FLOW | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939801 | M400PI551 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-12 | Oulet line metering skid 400-FT-772 | 938969 |  | M400PIC551 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI551-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/02/19 | MC-PM-007-Y1
939802 | M400PI553 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-15 | ULG 98 line to storage tank from 400-ME-003 | 932934 |  | M400ME003 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI553-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/09/18 | MC-PM-007-Y1
939803 | M400PI555 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-15 | Jet A1 line to storage tank from 400-ME-001 | 932932 |  | M400ME001 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI555-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/08/18 | MC-PM-007-Y1
939804 | M400PI556 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-15 | Discharge line pressure Main Line pump 400-P-019 | 935830 |  | M400P019 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI556-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-007-Y1
939805 | M400PI557 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , 0-15 | Pressure at inlet line of 400-PV-561 | 938869 |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI557-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/02/19 | MC-PM-007-Y1
939806 | M400PI558 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-15 | Outlet pressure 400-PV-561 | 938869 |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI558-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/02/19 | MC-PM-007-Y1
939807 | M400PI559 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1UB1RHABU , 0-15 | Outlet pressure 400-PV-561 | 938869 |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI559-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/02/19 | MC-PM-007-Y1
939808 | M400PI560 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-12 | Outlet pressure 400-PV-561 | 938869 |  | M400SYS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI560-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 01/03/19 | MC-PM-007-Y1
939809 | M400PI561 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-12 | Off Spec Jet A1-Main line Pump Discharge | 938869 |  | M400PIC561 | 3 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI561-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 02/03/19 | MC-PM-007-Y1
939810 | M400PI565 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-15 | Jet A1 line to storage tank from 400-ME-001 | 932932 |  | M400ME001 | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI565-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/08/18 | MC-PM-007-Y1
939811 | M400PI566 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1SB1RHABU , 0-10 | Scrapper receiver SRR P/L |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI566-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 10/03/19 | MC-PM-007-Y1
939812 | M400PI571 | LOOP, PRESSURE CONTROL, JET A1 , 78 KG/CM2 , 45 DEG.C , 0.751-0.841 , MASONEILAN | Isolation line of Scrappe reciever SRR P/L |  | CLOSLOOP | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI571-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/12/18 | MC-PM-008-M6
939813 | M400PI576 | LOOP, PRESSURE CONTROL, JET A1 , 78 KG/CM2 , 45 DEG.C , 0.751-0.841 , MASONEILAN | PRESS. SCRAPER LAUNCHER SRR P/L |  | CLOSLOOP | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI576-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/12/18 | MC-PM-008-M6
939815 | M400PI900 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , O-21 | PRESS. FOR MUSSAFAH AL AIN MP PIPELINE |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI900-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/03/19 | MC-PM-007-Y1
939816 | M400PI651 | LOOP, PRESSURE INDICATOR INSTRUMEN, ENDRESS HAUSER , PMP71-1BC1WB1RHABU , O-12 | PR. RUWAIS MUSSAFAH MP P/L RECEIVING END |  |  | M400PRESS | 3 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PI651-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 26/03/19 | MC-PM-007-Y1
939817 | M400MP202 | MOTOR,ELECTRIC, FIRE WATER PUMP, IP55, 585 KW, 50 HZ, 3300 V, S1, CTV 400 Y4, 6324C3 , NU324 C3, HORIZONTAL, 1483 RPM, 3, 120 AMP, F, 3400 KG, VACUM CONTACTOR, VACUM | MOTOR,ELECTRIC, FIRE WATER PUMP, IP55, 585 KW, 50 HZ, 3300 V, S1, CTV 400 Y4, 6324C3 , NU324 C3, HORIZONTAL, 1483 RPM, 3, 120 AMP, F, 3400 KG, VACUM CONTACTOR, VACUM | 936408 | MOTOR | M400P202 | 1 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400MP202-ME1 | ACTIVE | ELEC | PM | EDS | 2 | WEEKS | 12/08/18 | ME-PM-016-W1
939824 | M400TI470B | INDICATOR, TEMPERATURE | Casing For Pump 400-P-019 | 935830 |  | M400P019 | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI470B-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939826 | M400TE470B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , DOUBLE RTD, 3-WIRE , 100 OHM @ | Casing For Pump 400-P-019 | 939824 | TEMP_ELE | M400TI470B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939827 | M400TG468 | THERMOMETER, DIAL, BIMETALLIC TEMPERATURE GAUGE , 0-100 DEG C | LUBE-OIL TEMP. GAUGE BEFOR COOLER (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939828 | M400TG469 | THERMOMETER, DIAL, BIMETALLIC TEMPERATURE GAUGE , 0-100 DEG C | LUBE OIL TEMP. GAUGE AFTER COOLER(M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939829 | M400TT474 | TRANSMITTER, TEMPERATURE, RTD , 0-100 DEG C , 4-20MADC , 12.5-55VDC , M20X1.5 , | LUBE-OIL HEADERTEMP. (M400P019) | 935830 | TEMP_TX | M400P019 | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 1 | 0 | M400TT474-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-010-Y1
939830 | M400TG466 | THERMOMETER, DIAL, BIMETALLIC TEMPERATURE GAUGE , 0-120 DEG C | HEAT TRANSFER OILTEMP. (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939831 | M400TG467 | THERMOMETER, DIAL, BIMETALLIC TEMPERATURE GAUGE , 0-120 DEG C | HEAT TRANSFER OILTEMP. (M400P019) | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939832 | M400LT401 | TRANSMITTER, LIQUID LEVEL, 4-20MA , 24VDC | Lube Oil Reservoir - Level TX. For 400-P-016A |  | LVL_TX | M400LI401C | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939833 | M400PG403 | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , 1/2" NPT , SS , 316 SS , B | LUBE OIL DISH. HEADER - PRESSURE GAUGE(M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939834 | M400PG418 | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , 1/2" NPT , SS , 316 SS , B | LUBE OIL DISH. HEADER - PRESSURE GAUGE(M400P016B) | 935827 |  | M400P016B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939835 | M400PDT404 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , 1/2" NPT | LUBE OIL FILTER (M400P016A) | 935826 | LVL_TX | M400P016A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDT404-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/09/18 | MC-PM-007-Y1
939836 | M400PDT419 | TRANSMITTER, DIFFERENTIAL PRESSURE, DIAPHRAGM , 4-20MA , 24VDC , 1/2" NPT | LUBE OIL FILTER (M400P016B) | 935827 | LVL_TX | M400P016B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDT419-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 17/10/18 | MC-PM-007-Y1
939837 | M400TG401 | THERMOMETER, DIAL, 0-100 DEG C , BIMETALLIC TEMPERATURE GAUGE , 100MM , 1/2" MNP | LUBE OIL RESEVOIR - TEMPERATURE GAUGE (M400P016A) | 935826 |  | M400P016A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939838 | M400TT414 | TRANSMITTER, TEMPERATURE, RTD , 0-100 DEG C , 4-20MADC , 24VDC , M20X1.5 , ALUM | LUBE-OIL HEADERTEMP. (M400P016A) | 935826 | TEMP_TX | M400P016A | 1 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 5 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 1 | 0 | M400TT414-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/10/18 | MC-PM-010-Y1
939840 | M400PT408 | TRANSMITTER, PRESSURE, GAGE , (-) 1 to 55.2 BAR , 4-20MA , 10.5 - 36vdc , 1/2" - | PLAN 53 B - PRESSURE TRANSMITTER (M400P016A) | 935826 | PRES_TX | M400P016A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400PT408-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 21/09/18 | MC-PM-007-Y1
939876 | M400STLIGHT | IRP 1 STREET LIGHTING | IRP1 STREET LIGHTING. |  |  | M400ELEC | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939841 | M400TE440B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100, 3 WIRE, SINGLE , 100 OH | TEMP. ELEMENT FOR CASING MAINLINE PUMP 400-P-018A | 935828 | TEMP_ELE | M400P018A | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE440B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 04/12/18 | MC-PM-010-Y1
939842 | M400TE455A | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100, 3 WIRE, SINGLE , 100 OH | TEMP. ELEMENT FOR CASING MAINLINE PUMP 400-P-018B | 935829 | TEMP_ELE | M400P018B | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE455A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 12/12/18 | MC-PM-010-Y1
939843 | M400TE455B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100, 3 WIRE, SINGLE , 100 OH | TEMP. ELEMENT FOR CASING MAINLINE PUMP 400-P-018B | 935829 | TEMP_ELE | M400P018B | 2 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400TE455B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 13/12/18 | MC-PM-010-Y1
939844 | M400VE431B | PROBE, VIBRATION | VIBRATION FOR BEARING HOUSING (CE) 400P18A. | 935828 | VIBRE_TX | M400P018A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE431B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/08/18 | MC-PM-012-M3
939845 | M400VE432A | PROBE, VIBRATION | VIBRATION FOR PUMP BEARING DE 400-P-018A | 935828 | VIBRE_TX | M400P018A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE432A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/08/18 | MC-PM-012-M3
939846 | M400VE432B | PROBE, VIBRATION | VIBRATION FOR PUMP BEARING NDE 400-P-018A | 935828 | VIBRE_TX | M400P018A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE432B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/08/18 | MC-PM-012-M3
939847 | M400VE446A | PROBE, VIBRATION | VIBRATION FOR BEARING HOUSE (NCE) 400-P-018B | 935829 | VIBRE_TX | M400P018B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE446A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/09/18 | MC-PM-012-M3
939848 | M400VE446B | PROBE, VIBRATION | VIBRATION FOR BEARING HOUSE (CE) 400-P-018B | 935829 | VIBRE_TX | M400P018B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE446B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/09/18 | MC-PM-012-M3
939849 | M400VE447A | PROBE, VIBRATION | VIBRATION FOR PUMP BEARING DE 400-P-018B | 935829 | VIBRE_TX | M400P018B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE447A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/09/18 | MC-PM-012-M3
939850 | M400VE447B | PROBE, VIBRATION | VIBRATION FOR PUMP BEARING NDE 400-P-018B | 935829 | VIBRE_TX | M400P018B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400VE447B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/09/18 | MC-PM-012-M3
939857 | M400TI410B | INDICATOR, TEMPERATURE | Casing For Pump 400-P-016A | 935826 |  | M400P016A | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI410B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 05/10/18 | MC-PM-010-Y1
939858 | M400TE410B | ELEMENT, TEMPERATURE, RTD DUAL ELEMENT, 3 WIRES , PT100, 3 WIRE, SINGLE , 0-200 | Casing For Pump 400-P-016A |  | TEMP_ELE | M400TI410B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939859 | M400TI425B | INDICATOR, TEMPERATURE | Casing For Pump 400-P-016B | 935827 |  | M400P016B | 1 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400TI425B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 07/11/18 | MC-PM-010-Y1
939862 | M400TE425B | ELEMENT, TEMPERATURE, SINGLE RTD THERMOMETER , PT100, 3 WIRE, SINGLE , 100 OHM @ | Casing For Pump 400-P-016B | 939859 | TEMP_ELE | M400TI425B | 1 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939863 | M400ZE401A | PROBE, VIBRATION , 8MM , 0.5 M | Pump - Thrust Bearing - 2nd "Z" Plane for 400P016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400ZE401A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/10/18 | MC-PM-012-M3
939864 | M400ZE401B | PROBE, VIBRATION , 8MM , 0.5 M | Pump - Thrust Bearing - 2nd "Z" Plane for 400P016A | 935826 | VIBRE_TX | M400P016A | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400ZE401B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/10/18 | MC-PM-012-M3
969195709 | M410FG076 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195710 | M410FG077 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205159 | M410MOV1006 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175663 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1006-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/02/19 | ME-PM-002-M6
969205160 | M410MOV1007 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175664 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1007-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/02/19 | ME-PM-002-M6
969205161 | M410MOV1008 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175665 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1008-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/02/19 | ME-PM-002-M6
969205162 | M410MOV1009 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175666 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1009-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/02/19 | ME-PM-002-M6
969205163 | M410MOV1010 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175667 | MOV | M410T010 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1010-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/02/19 | ME-PM-002-M6
969205164 | M410MOV1011 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175668 | MOV | M410T010 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1011-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/02/19 | ME-PM-002-M6
969205165 | M410MOV1012 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-010 | 969175669 | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1012-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/02/19 | ME-PM-002-M6
969205166 | M410MOV1101 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175670 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1101-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/02/19 | ME-PM-002-M6
969205167 | M410MOV1102 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175671 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1102-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/02/19 | ME-PM-002-M6
969205168 | M410MOV1103 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175672 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1103-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/02/19 | ME-PM-002-M6
969205169 | M410MOV1104 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175673 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1104-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/02/19 | ME-PM-002-M6
969205170 | M410MOV1105 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175674 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1105-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/02/19 | ME-PM-002-M6
969205171 | M410MOV1106 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175675 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1106-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/02/19 | ME-PM-002-M6
969205172 | M410MOV1107 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175676 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1107-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/02/19 | ME-PM-002-M6
969205173 | M410MOV1108 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175677 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1108-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/02/19 | ME-PM-002-M6
969205174 | M410MOV1109 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175678 | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1109-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969205175 | M410MOV1110 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-011 | 969175679 | MOV | M410T011 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1110-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969205176 | M410MOV1201 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175680 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1201-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969205177 | M410MOV1202 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175681 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1202-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969205178 | M410MOV1203 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175682 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1203-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/09/18 | ME-PM-002-M6
969205179 | M410MOV1204 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175683 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1204-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/09/18 | ME-PM-002-M6
969205180 | M410MOV1205 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175684 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1205-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/09/18 | ME-PM-002-M6
969205181 | M410MOV1206 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175685 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1206-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/09/18 | ME-PM-002-M6
969205182 | M410MOV1207 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175686 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1207-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/09/18 | ME-PM-002-M6
969205183 | M410MOV1208 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175687 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1208-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/09/18 | ME-PM-002-M6
969205184 | M410MOV1209 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175688 | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1209-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205185 | M410MOV1210 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-012 | 969175689 | MOV | M410T012 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1210-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969205186 | M410MOV1301 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175690 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1301-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
969205187 | M410MOV1302 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175691 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1302-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/09/18 | ME-PM-002-M6
969205188 | M410MOV1303 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175692 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1303-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/09/18 | ME-PM-002-M6
969205189 | M410MOV1304 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175693 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1304-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969205190 | M410MOV1305 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175694 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1305-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969205191 | M410MOV1306 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175695 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1306-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
969205192 | M410MOV1307 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175696 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1307-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/09/18 | ME-PM-002-M6
969205193 | M410MOV1308 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175697 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1308-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/09/18 | ME-PM-002-M6
969205194 | M410MOV1309 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175698 | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1309-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969205195 | M410MOV1310 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-013 | 969175699 | MOV | M410T013 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1310-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969205196 | M410MOV1401 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175700 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1401-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
969205197 | M410MOV1402 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175701 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1402-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/09/18 | ME-PM-002-M6
969205198 | M410MOV1403 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175702 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1403-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/10/18 | ME-PM-002-M6
969205199 | M410MOV1404 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175703 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1404-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969205200 | M410MOV1405 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175704 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1405-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969205201 | M410MOV1406 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175705 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1406-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/10/18 | ME-PM-002-M6
969205202 | M410MOV1407 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175706 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1407-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/10/18 | ME-PM-002-M6
969205203 | M410MOV1408 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175707 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1408-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/10/18 | ME-PM-002-M6
969205204 | M410MOV1409 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175708 | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1409-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969205205 | M410MOV1410 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-014 | 969175709 | MOV | M410T014 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1410-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969205206 | M410MOV1451A | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-014A | 969175710 | MOV | M410P014A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1451A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/10/18 | ME-PM-002-M6
969205207 | M410MOV1452A | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-014A | 969175711 | MOV | M410P014A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1452A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
969205208 | M410MOV1453B | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-014B | 969175712 | MOV | M410P014B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1453B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/10/18 | ME-PM-002-M6
969205209 | M410MOV1454B | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-014B | 969175713 | MOV | M410P014B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1454B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
969205210 | M410MOV1455 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM | 969175714 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1455-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
969205211 | M410MOV1456 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM | 969175715 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1456-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/10/18 | ME-PM-002-M6
969205212 | M410MOV1457 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM | 969175716 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1457-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/10/18 | ME-PM-002-M6
969205213 | M410MOV1501 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175717 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1501-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/10/18 | ME-PM-002-M6
969205214 | M410MOV1502 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175718 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1502-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969205215 | M410MOV1503 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175719 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1503-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969205216 | M410MOV1504 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175720 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1504-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/10/18 | ME-PM-002-M6
969175131 | M410LT158 | JET A1 SUMP VESSEL 410-V-004 | JET A1 SUMP VESSEL 410V004 |  | LVL_TX | M410V004 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175132 | M410LT200 | FIRE WATER STORAGE TANK 410-T-051 | FIRE WATER STORAGE TANK 410T051 |  | LVL_TX | M410T051 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175133 | M410LT201 | FIRE WATER STORAGE TANK 410-T-052 | FIRE WATER STORAGE TANK 410-T-052 |  | LVL_TX | M410T052 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175134 | M410LT450A | JET A1 INTER-TANK FILTER COALESCER 410-L-004A | JET A1 INTER-TANK FILTER COALESCER 410-L-004A |  | LVL_TX | M410L004A | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175135 | M410LT450B | JET A1 INTER-TANK FILTER COALESCER 410-L-004B | JET A1 INTER-TANK FILTER COALESCER 410-L-004B |  | LVL_TX | M410L004B | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175136 | M410LT450C | JET A1 INTER-TANK FILTER COALESCER 410-L-004C | JET A1 INTER-TANK FILTER COALESCER 410-L-004C |  | LVL_TX | M410L004C | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175137 | M410LT451A | JET A1 INTER-TANK FILTER COALESCER 410-L-004A | JET A1 INTER-TANK FILTER COALESCER 410-L-004A |  | LVL_TX | M410L004A | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175138 | M410LT451B | JET A1 INTER-TANK FILTER COALESCER 410-L-004B | JET A1 INTER-TANK FILTER COALESCER 410-L-004B |  | LVL_TX | M410L004B | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175139 | M410LT451C | JET A1 INTER-TANK FILTER COALESCER 410-L-004C | JET A1 INTER-TANK FILTER COALESCER 410-L-004C |  | LVL_TX | M410L004C | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175155 | M410LT012 | EMERSON ULG 91 TANK 410-T-001 | EMERSON ULG 91 LEVEL TRANSMITTER OF TANK 410-T-001 |  | LVL_TX | M410T001 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175156 | M410LT022 | EMERSON ULG 91 TANK 410-T-002 | EMERSON ULG 91 LEVEL TRANSMITTER OF TANK 410-T-002 |  | LVL_TX | M410T002 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175157 | M410LT032 | ULG 91 TANK 410-T-003 | EMERSON ULG 91 LEVEL TRANSMITTER OF TANK 410-T-003 |  | LVL_TX | M410T003 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175158 | M410LT042 | ULG 91 TANK 410-T-004 | EMERSON ULG 91 LEVEL TRANSMITTER OF TANK 410-T-004 |  | LVL_TX | M410T004 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175159 | M410LT052 | ULG 95 TANK 410-T-005 | EMERSON ULG 95 LEVEL TRANSMITTER OF TANK 410-T-005 |  | LVL_TX | M410T005 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175160 | M410LT062 | ULG 95 TANK 410-T-006 | EMERSON ULG 95 LEVEL TRANSMITTER OF TANK 410-T-006 |  | LVL_TX | M410T006 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175161 | M410LT072 | ULG 95 TANK 410-T-007 | EMERSON ULG 95 LEVEL TRANSMITTER OF TANK 410-T-007 |  | LVL_TX | M410T007 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175162 | M410LT082 | ULG 95 TANK 410-T-008 | EMERSON ULG 95 LEVEL TRANSMITTER OF TANK 410-T-008 |  | LVL_TX | M410T008 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175163 | M410LT092 | GAS OIL TANK 410-T-009 | EMERSON GAS OIL LEVEL TRANSMITTER OF TANK 410-T-009 |  | LVL_TX | M410T009 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175164 | M410LT102 | EMERSON GAS OIL TANK 410-T-010 | EMERSON GAS OIL LEVEL TRANSMITTER OF TANK 410-T-010 |  | LVL_TX | M410T010 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175165 | M410LT112 | JET A1 TANK 410-T-011 | EMERSON JET A1 LEVEL TRANSMITTER OF TANK 410-T-011 |  | LVL_TX | M410T011 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175166 | M410LT122 | JET A1 TANK 410-T-012 | EMERSON JET A1 LEVEL TRANSMITTER OF TANK 410-T-012 |  | LVL_TX | M410T012 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365192 | M410XGH652 | H2 GAS DETECTORS-IRP-II SUBSTATION-BATTERY ROOM CEILING-NORTH SIDE | H2 GAS DETECTORS-IRP-II SUBSTATION-BATTERY ROOM CEILING-NORTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365328 | M400WO11 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO11-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365329 | M400WO12 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO12-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365330 | M400WO13 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO13-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365331 | M400WO14 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO14-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365332 | M400WO15 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO15-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365333 | M400WO16 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO16-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365334 | M400WO17 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO17-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365335 | M400WO18 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO18-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365336 | M400WO19 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO19-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365337 | M400WO20 | WELDING OUTLET POWER SOCKET OF IRP1. | WELDING OUTLET POWER SOCKET OF IRP1. |  | LIGHT | M400WO01TO20 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400WO20-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 25/10/18 | ME-PNL1-PM-M6
969365193 | M410XGC702 | FLAMMABLE GAS DETECTORS-AT BACK OF PUMP 410P007A IRP-II AT ITTP | FLAMMABLE GAS DETECTORS-AT BACK OF PUMP 410P007A IRP-II AT ITTP |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374387 | M410LS055 | OUTDOOR LOUD SPEAKER NEAR TANK-010 NE SIDE ON POLE-ZONE-B3 | Loud Speaker with J/B-Outdoor-NEAR TANK-004 NE SIDE ON POLE | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374388 | M410LS056 | OUTDOOR LOUD SPEAKER NEAR TANK-010 NW SIDE ON POLE-ZONE-B3 | Loud Speaker with J/B-Outdoor-NEAR TANK010 NW SIDE ON POLE | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365194 | M410XGC703 | FLAMMABLE GAS DETECTORS-AT BACK OF PUMP 410P007B IRP-II AT ITTP | FLAMMABLE GAS DETECTORS-AT BACK OF PUMP 410P007B IRP-II AT ITTP |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374390 | M410LS059 | OUTDOOR LOUD SPEAKER IRP-II S/S BLDG WALL SOUTH SIDE-ZONE-C1 | Loud Speaker with J/B-Outdoor-S/S BUILDING ROOF-SOUTH SIDE | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374420 | M410LSZC4 | LOUD SPEAKER AT ZONE C-WAREHOUSE (M410LS136,M410LS137,M410LS138 ,M410LS139 ,M410LS140,M410LS141,M410LS142,M410LS143,M410LS144,M410LS145) | LOUD SPEAKER AT ZONE C-WAREHOUSE = 10 LS. |  | PA_SYS | M410LSZC | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374421 | M410LSZC5 | LOUD SPEAKER AT ZONE C-S/S IRP-I (M410LS039,M410LS040,M410LS041 ,M410LS042 ,M410LS043,M410LS116,M410LS117,M410LS118,M410LS119,M410LS120) | LOUD SPEAKER AT ZONE C-S/S IRP-I = 10 LS. |  | PA_SYS | M410LSZC | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374422 | M410LSZC6 | LOUD SPEAKER AT ZONE C-S/S IRP-II (M410LS059,M410LS025,M410LS026,M410LS027, M410LS028,M410LS100,M410LS101,M410LS102,M410LS103,M410LS104,M410LS105,M410LS060) | LOUD SPEAKER AT ZONE C-S/S IRP-II = 12 LS. |  | PA_SYS | M410LSZC | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374423 | M410FU01 | RIM SEAL PROTECTION AT TANK-001 (M410FU201A, M410FU201B, M410FU201C, M410FU201D, M410FU201E) | RIM SEAL PROTECTION AT TANK-001 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374424 | M410FU02 | RIM SEAL PROTECTION AT TANK-002(M410FU202A,M410FU202B,M410FU202C, M410FU202D,M410FU202E) | RIM SEAL PROTECTION AT TANK-002 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374425 | M410FU03 | RIM SEAL PROTECTION AT TANK-003(M410FU203A,M410FU203B,M410FU203C, M410FU203D,M410FU203E) | RIM SEAL PROTECTION AT TANK-003 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374426 | M410FU04 | RIM SEAL PROTECTION AT TANK-004(M410FU204A,M410FU204B,M410FU204C, M410FU204D,M410FU204E) | RIM SEAL PROTECTION AT TANK-004 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374427 | M410FU05 | RIM SEAL PROTECTION AT TANK-005(M410FU205A,M410FU205B,M410FU205C, M410FU205D,M410FU205E) | RIM SEAL PROTECTION AT TANK-005 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374428 | M410FU06 | RIM SEAL PROTECTION AT TANK-006(M410FU206A,M410FU206B,M410FU206C, M410FU206D,M410FU206E) | RIM SEAL PROTECTION AT TANK-006 |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365195 | M410XGC704 | FLAMMABLE GAS DETECTORS-AT BACK OF PUMP 410P007C IRP-II AT ITTP | FLAMMABLE GAS DETECTORS-AT BACK OF PUMP 410P007C IRP-II AT ITTP |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365196 | M410XGC734A | FLAMMABLE GAS DETECTORS-SIS RACK ROOMP-AIR LOCK CORRIDOR NORTH SIDE-LEFT | FLAMMABLE GAS DETECTORS-SIS RACK ROOMP-AIR LOCK CORRIDOR NORTH SIDE-LEFT |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365197 | M410XGC734B | FLAMMABLE GAS DETECTORS-SIS RACK ROOM-AIR LOCK CORRIDOR NORTH SIDE-CENTRE | FLAMMABLE GAS DETECTORS-SIS RACK ROOM-AIR LOCK CORRIDOR NORTH SIDE-CENTRE |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365198 | M410XGC734C | FLAMMABLE GAS DETECTORS-SIS RACK ROOM-AIR LOCK CORRIDOR NORTH SIDE-RIGHT | FLAMMABLE GAS DETECTORS-SIS RACK ROOM-AIR LOCK CORRIDOR NORTH SIDE-RIGHT |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365199 | M410XGC690 | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) INSIDE NEW SUMP VESSEL TANK | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) INSIDE NEW SUMP VESSEL TANK |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365200 | M410XAC600 | MANUAL CALL POINT NEAR POND FOR STORM WATER-NW SIDE | MANUAL CALL POINT NEAR POND FOR STORM WATER-NW SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365201 | M410XAC601 | MANUAL CALL POINT NEAR POND FOR STORM WATER-NE SIDE | MANUAL CALL POINT NEAR POND FOR STORM WATER-NE SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365202 | M410XAC602 | MANUAL CALL POINT NEAR FRESH WATER TANK | MANUAL CALL POINT NEAR FRESH WATER TANK |  | PB_HS-MC | M410FGSC001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365203 | M410XAC603 | MANUAL CALL POINT NEAR TANK 410-T-011 NORTH SIDE | MANUAL CALL POINT NEAR TANK 410-T-011 NORTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365204 | M410XAC604 | MANUAL CALL POINT NEAR BFF | MANUAL CALL POINT NEAR BFF |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365205 | M410XAC605 | MANUAL CALL POINT NEAR FRESH WATER TANK SOUTH SIDE | MANUAL CALL POINT NEAR FRESH WATER TANK SOUTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365206 | M410XAC606 | MANUAL CALL POINT NEAR POND FOR STORM WATER-NORTH SIDE | MANUAL CALL POINT NEAR POND FOR STORM WATER-NORTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365207 | M410XAC607 | MANUAL CALL POINT NEAR TANK-012 EAST SIDE | MANUAL CALL POINT NEAR TANK-012 EAST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365208 | M410XAC608 | MANUAL CALL POINT NEAR TANK-014 EAST SIDE | MANUAL CALL POINT NEAR TANK-014 EAST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365209 | M410XAC609 | MANUAL CALL POINT NEAR TANK-013 WEST SIDE | MANUAL CALL POINT NEAR TANK-013 WEST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365210 | M410XAC610 | MANUAL CALL POINT NEAR TANK-014 ES SIDE | MANUAL CALL POINT NEAR TANK-014 ES SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365211 | M410XAC611 | MANUAL CALL POINT NEAR TANK-016 EAST SIDE | MANUAL CALL POINT NEAR TANK-016 EAST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365212 | M410XAC612 | MANUAL CALL POINT NEAR TANK-015 WEST SIDE | MANUAL CALL POINT NEAR TANK-015 WEST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365213 | M410XAC624 | MANUAL CALL POINT NEAR EMERGENCY GATE | MANUAL CALL POINT NEAR EMERGENCY GATE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365214 | M410XAC613 | MANUAL CALL POINT AT SIS BUILDING SOUTH SIDE | MANUAL CALL POINT AT SIS BUILDING SOUTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365215 | M410XAC634 | MANUAL CALL POINT NEAR TANK-006 WEST SIDE | MANUAL CALL POINT NEAR TANK-006 WEST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365216 | M410XAC625 | MANUAL CALL POINT NEAR TANK-005 NORTH SIDE | MANUAL CALL POINT NEAR TANK-005 NORTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365217 | M410XAC614 | MANUAL CALL POINT NEAR ITTP SOUTH SIDE | MANUAL CALL POINT NEAR ITTP SOUTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365218 | M410XAC615 | MANUAL CALL POINT NEAR ITTP EAST SIDE | MANUAL CALL POINT NEAR ITTP EAST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365219 | M410XAC626 | MANUAL CALL POINT NEAR TANK-008 | MANUAL CALL POINT NEAR TANK-008 |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365220 | M410XAC638 | MANUAL CALL POINT NEAR TANK-007 EAST SIDE | MANUAL CALL POINT NEAR TANK-007 EAST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365221 | M410XAC639 | MANUAL CALL POINT NEAR TANK-007 SOUTH SIDE | MANUAL CALL POINT NEAR TANK-007 SOUTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365222 | M410XAC616 | MANUAL CALL POINT NEAR POND, NEAR PLCR | MANUAL CALL POINT NEAR POND, NEAR PLCR |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365223 | M410XAC617 | MANUAL CALL POINT NEAR AIR COMPRESSOR WEST SIDE | MANUAL CALL POINT NEAR AIR COMPRESSOR WEST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365224 | M410XAC627 | MANUAL CALL POINT NEAR TANK-004 NORTH SIDE | MANUAL CALL POINT NEAR TANK-004 NORTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365225 | M410XAC618 | MANUAL CALL POINT NEAR AIR COMPRESSOR EAST SIDE | MANUAL CALL POINT NEAR AIR COMPRESSOR EAST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365226 | M410XAC635 | MANUAL CALL POINT NEAR TANK-003 EAST SIDE | MANUAL CALL POINT NEAR TANK-003 EAST SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365227 | M410XAC640 | MANUAL CALL POINT NEAR TANK-003 SOUTH SIDE | MANUAL CALL POINT NEAR TANK-003 SOUTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365228 | M410XAC619 | MANUAL CALL POINT ON ROAD IN BETWEEN AIR COMPRESSOR AND ADNOC BOUNDARY | MANUAL CALL POINT ON ROAD IN BETWEEN AIR COMPRESSOR AND ADNOC BOUNDARY |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365229 | M410XAC628 | MANUAL CALL POINT NEAR TANK-010 NORTH SIDE | MANUAL CALL POINT NEAR TANK-010 NORTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365230 | M410XAC620 | MANUAL CALL POINT NEAR ADNOC BOUNDARY WALL, EAST OF AIR COMPRESSOR | MANUAL CALL POINT NEAR ADNOC BOUNDARY WALL, EAST OF AIR COMPRESSOR |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365231 | M410XAC641 | MANUAL CALL POINT NEAR SOUTH SIDE OF TANK-009 | MANUAL CALL POINT NEAR SOUTH SIDE OF TANK-009 |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365232 | M410XAC643 | MANUAL CALL POINT NEAR SOUTH SIDE OF POND | MANUAL CALL POINT NEAR SOUTH SIDE OF POND |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365233 | M410XAC629 | MANUAL CALL POINT NEAR BOOSTER PUMP | MANUAL CALL POINT NEAR BOOSTER PUMP |  | PB_HS-MC | M410FGSC001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365234 | M410XAC632 | MANUAL CALL POINT NEAR ZONE-25 EASTERN SIDE | MANUAL CALL POINT NEAR ZONE-25 EASTERN SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365235 | M410XAC637 | MANUAL CALL POINT NEAR ZONE-25 SOUTH SIDE | MANUAL CALL POINT NEAR ZONE-25 SOUTH SIDE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365236 | M410XAC644 | MANUAL CALL POINT NEAR WEST SIDE OF POND | MANUAL CALL POINT NEAR WEST SIDE OF POND |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365237 | M410XAC823 | MANUAL CALL POINT AT PLCR EXT-NEAR UPS ROOM-NORTH SIDE GATE | MANUAL CALL POINT AT PLCR EXT-NEAR UPS ROOM-NORTH SIDE GATE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365238 | M410XAC824 | MANUAL CALL POINT AT PLCR EXT-NEAR BATTERY ROOM-EAST SIDE GATE | MANUAL CALL POINT AT PLCR EXT-NEAR BATTERY ROOM-EAST SIDE GATE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365239 | M410XAC825 | MANUAL CALL POINT AT PLCR EXT-INSIDE BATTERY ROOM NEAR DOOR | MANUAL CALL POINT AT PLCR EXT-INSIDE BATTERY ROOM NEAR DOOR |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365240 | M410XAC826 | MANUAL CALL POINT AT PLCR EXT-NEAR UPS ROOM SOUTH SIDE GATE | MANUAL CALL POINT AT PLCR EXT-NEAR UPS ROOM SOUTH SIDE GATE |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365241 | M410XAC827 | MANUAL CALL POINT AT PLCR EXT-INSIDE UPS ROOM | MANUAL CALL POINT AT PLCR EXT-INSIDE UPS ROOM |  | PB_HS-MC | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365242 | M410XAC747 | MANUAL CALL POINT AT SIS-RACK ROOM MAIN GATE NORTH SIDE | MANUAL CALL POINT AT SIS-RACK ROOM MAIN GATE NORTH SIDE |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365243 | M410XAC748 | MANUAL CALL POINT AT SIS-RACK ROOM AIR LOCK DOOR OUTSIDE | MANUAL CALL POINT AT SIS-RACK ROOM AIR LOCK DOOR OUTSIDE |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365244 | M410XAC749 | MANUAL CALL POINT AT SIS-RACK ROOM INSIDE SIS NEAR AIR LOCK DOOR | MANUAL CALL POINT AT SIS-RACK ROOM INSIDE SIS NEAR AIR LOCK DOOR |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365245 | M410XAC750 | MANUAL CALL POINT AT SIS-HVAC ROOM MAIN GATE OUTSIDE | MANUAL CALL POINT AT SIS-HVAC ROOM MAIN GATE OUTSIDE |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365246 | M410XAC751 | MANUAL CALL POINT AT SIS-INSIDE HVAC ROOM NEAR SMALL GATE | MANUAL CALL POINT AT SIS-INSIDE HVAC ROOM NEAR SMALL GATE |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365247 | M410XAC752 | MANUAL CALL POINT AT SIS-INSIDE RACK ROOM | MANUAL CALL POINT AT SIS-INSIDE RACK ROOM |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365248 | M410XAC753 | MANUAL CALL POINT AT SIS-INSIDE UPS ROOM | MANUAL CALL POINT AT SIS-INSIDE UPS ROOM |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365249 | M410XAC754 | MANUAL CALL POINT AT SIS-OUTSIDE UPS ROOM DOOR | MANUAL CALL POINT AT SIS-OUTSIDE UPS ROOM DOOR |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365250 | M410XAC755 | MANUAL CALL POINT AT SIS-OUTSIDE BATTERY ROOM DOOR | MANUAL CALL POINT AT SIS-OUTSIDE BATTERY ROOM DOOR |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365251 | M410XAC756 | MANUAL CALL POINT AT SIS-INSIDE BATTERY ROOM | MANUAL CALL POINT AT SIS-INSIDE BATTERY ROOM |  | PB_HS-MC | M410FACP001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365252 | M410XAC674 | MANUAL CALL POINT AT HVAC ROOM-OUTSIDE S/S | MANUAL CALL POINT AT HVAC ROOM-OUTSIDE S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269637 | M410PDT412B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT412B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269638 | M410PDT412C | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT412C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269639 | M410PDT412D | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005D | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT412D-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269640 | M410PDT412E | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005E | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT412E-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269641 | M410PDT421A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L006A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT421A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269642 | M410PDT421B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L006B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT421B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269643 | M410PDT440A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT440A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269644 | M410PDT440B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT440B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269645 | M410PDT440C | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT440C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269646 | M410PDT440D | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001D | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT440D-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269647 | M410PDT441A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT441A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269648 | M410PDT441B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT441B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269649 | M410PDT441C | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT441C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269650 | M410PDT441D | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001D | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT441D-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269651 | M410PDT451 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P040A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT451-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269652 | M410PDT452 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P040B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT452-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269653 | M410PDT458A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L011A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT458A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269654 | M410PDT458B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L011B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT458B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269655 | M410PDT459A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L011A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT459A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269656 | M410PDT459B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L011B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT459B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269657 | M410JBA761A | DIGITAL JUNCTION BOX FOR AIR DRYER | DIGITAL JUNCTION BOX FOR AIR DRYER |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269658 | M410JBA761B | DIGITAL JUNCTION BOX FOR AIR DRYER | DIGITAL JUNCTION BOX FOR AIR DRYER |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269659 | M410JBC761A | DIGITAL JUNCTION BOX FOR AIR DRYER | DIGITAL JUNCTION BOX FOR AIR DRYER |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269660 | M410JBC761B | DIGITAL JUNCTION BOX FOR AIR DRYER | DIGITAL JUNCTION BOX FOR AIR DRYER |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269661 | M410P020A | DHAFRA ANTI-STATIC DILUTION PUMP | DHAFRA ANTI-STATIC DILUTION PUMP 410ME002. |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269662 | M410P020B | DHAFRA ANTI-STATIC DILUTION PUMP | DHAFRA ANTI-STATIC DILUTION PUMP 410ME002. |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269755 | M410L006A | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269756 | M410L006B | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269757 | M410L008A | GAS OIL BASKET FILTER (MUSSAFAH), ULG | GAS OIL BASKET FILTER (MUSSAFAH), ULG |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269758 | M410L008B | GAS OIL BASKET FILTER (MUSSAFAH), ULG | GAS OIL BASKET FILTER (MUSSAFAH), ULG |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269759 | M410L009A | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269760 | M410L009B | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL | GAS OIL BASKET FILTER (MUSSAFAH), GAS OIL |  | VESSEL | M410FILTER | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269204 | M410P003A | AL AIN GAS OIL BOOSTER CENTRIFUGAL PUMP. | AL AIN GAS OIL BOOSTER PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269205 | M410P003B | AL AIN GAS OIL BOOSTER CENTRIFUGAL PUMP. | AL AIN GAS OIL BOOSTER PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269215 | M410P004A | AL AIN GAS OIL MAIN LINE CENTRIFUGAL PUMP. | AL AIN GAS OIL MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269216 | M410P004B | AL AIN GAS OIL MAIN LINE CENTRIFUGAL PUMP. | AL AIN GAS OIL MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269761 | M410DCSOPCA0107 | HARD WIRED CONSOLE | HARD WIRED CONSOLE |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269762 | M410DCSOPCA0105 | HARD WIRED CONSOLE - ANNUNCIATOR | HARD WIRED CONSOLE - ANNUNCIATOR |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269763 | M410DCSOPCA0104 | HARD WIRED CONSOLE - PUSH BUTTONS, KEY SWITCHES | HARD WIRED CONSOLE - PUSH BUTTONS, KEY SWITCHES |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269764 | M410XGC600 | HC GAS DETECTOR | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-FT-209 |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269765 | M410MP002A | HIGH VOLTAGE THREE PHASE INDUCTION MOTOR | MOTOR FOR AL AIN ULG MAIN LINE PUMP 2-A |  | MOTOR | M410P002A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP002A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969269766 | M410MP002B | HIGH VOLTAGE THREE PHASE INDUCTION MOTOR | MOTOR FOR AL AIN ULG MAIN LINE PUMP 2-B |  | MOTOR | M410P002B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP002B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969269767 | M410MP004A | HIGH VOLTAGE THREE PHASE INDUCTION MOTOR | MOTOR FOR AL AIN GAS OIL MAIN LINE PUMP 4-A. |  | MOTOR | M410P004A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP004A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969269768 | M410MP004B | HIGH VOLTAGE THREE PHASE INDUCTION MOTOR | MOTOR FOR AL AIN GAS OIL MAIN LINE PUMP 4-B. |  | MOTOR | M410P004B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP004B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-HT1-6M
969484418 | M410HOS7 | #7 BIG FLOW 12" SUPER AQUADUCT HOSE FLAKING DEPLOYMENT AND RETRIEVAL POD. | #7 BIG FLOW 12" HOSE DEPLOYMENT AND RETRIEVAL POD 7/10. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269770 | M410FFE2101302 | Hose box for hydrant | Hose box for hydrant |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269772 | M410FFE2196005 | HANDHELD ELECTRIC DRIVEN FOAM CONCENTRATE BARREL PUMP. BIG FLOW SYSTEM. | HANDHELD ELECTRIC BIG FLOW FOAM CONCENTRATE BARREL PUMP. |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | Medium | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269773 | M410MK001A | Induction Motor for COMPRESSOR | Induction Motor for COMPRESSOR |  | MOTOR | M410K001A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MK001A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269774 | M410MK001B | Induction Motor for COMPRESSOR | Induction Motor for COMPRESSOR |  | MOTOR | M410K001B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MK001B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269775 | M410INS2145001 | INERGEN GAS EXTINGUISHING SYSTEM | INERGEN GAS EXTINGUISHING SYSTEM |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269776 | M410ME008 | INSTRUMENT AIR DRYER PACKGE | INSTRUMENT AIR DRYER PACKGE |  | PACKAGE | M410PKG | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 1 | 10 | 3.699 | Low | Low | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269777 | M410ME009 | INSTRUMENT AIR DRYER PACKGE | INSTRUMENT AIR DRYER PACKGE |  | PACKAGE | M410PKG | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 1 | 10 | 3.699 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269778 | M410PT761A | Instrument Air Pressure Transmiitter | Instrument Air Pressure Transmiitter |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT761A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269779 | M410PT761B | Instrument Air Pressure Transmiitter | Instrument Air Pressure Transmiitter |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT761B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269780 | M410TT761A | Instrument Air Pressure Transmiitter | Instrument Air Pressure Transmiitter |  | TEMP_TX | M410TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269781 | M410TT761B | Instrument Air Pressure Transmiitter | Instrument Air Pressure Transmiitter |  | TEMP_TX | M410TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269782 | M410V006 | INSTRUMENT AIR RECEIVER | INSTRUMENT AIR RECEIVER |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269783 | M410EA091A | INTER COOLER FOR COMPRESSOR | INTER COOLER FOR COMPRESSOR |  | HEATEXHR | M410K001A | 3 | HEATEXHR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA091A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269784 | M410EA091B | INTER COOLER FOR COMPRESSOR | INTER COOLER FOR COMPRESSOR |  | HEATEXHR | M410K001B | 3 | HEATEXHR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 10 | 50 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410EA091B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269785 | M410IRP002 | INTERPOSING RELAY PANEL | INTERPOSING RELAY PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M410IRP002-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269786 | M410IRP003 | INTERPOSING RELAY PANEL | INTERPOSING RELAY PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M410IRP003-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269787 | M410IRP004 | INTERPOSING RELAY PANEL | INTERPOSING RELAY PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M410IRP004-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269788 | M410FOM739 | 23,000 LITRE SEMI FIXED STORAGE FOAM TANKS BIG FLOW SYSTEM. | 23000 L FOAM TANKS BIG FLOW SEMI FIXED STORAGE TANK (SOUTH). |  | PACKAGE | MBFFFS | 2 | BFS | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 5 | 10 | 1 | 5 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269789 | M410L001A | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269790 | M410L001B | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269791 | M410L001C | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269792 | M410L001D | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 1 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269793 | M410L005A | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269794 | M410L005B | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269795 | M410L005C | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 1 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269796 | M410L005D | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 1 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269797 | M410L005E | JET A1 FILTER COALESCER (MUSSAFAH) | JET A1 FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269798 | M410L012A | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269799 | M410L012B | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269800 | M410L012C | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L001C | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269801 | M410L012D | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L001D | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269802 | M410L013A | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L005A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269803 | M410L013B | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L005B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269804 | M410L013C | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L005C | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269805 | M410L013D | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L005D | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269806 | M410L013E | JET A1 PRE-FILTER COALESCER (MUSSAFAH) | JET A1 PRE-FILTER COALESCER (MUSSAFAH) |  | VESSEL | M410L005E | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269809 | M410L011A | JP-8 FILTER COALESCERS (MUSSAFAH-ALDHAFA) | JP-8 FILTER COALESCERS (MUSSAFAH-ALDHAFA) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 1 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269810 | M410L011B | JP-8 FILTER COALESCERS (MUSSAFAH-ALDHAFA) | JP-8 FILTER COALESCERS (MUSSAFAH-ALDHAFA) |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269811 | M410JBAI701 | JUNCTION BOX FOR DYE(GREEN) INJECTION SYSTEM 400-ME-002 | JUNCTION BOX FOR DYE(GREEN) INJECTION SYSTEM 400-ME-002 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269812 | M410JBAI711 | JUNCTION BOX FOR DYE(RED) INJECTION SYSTEM 400-ME-003 | JUNCTION BOX FOR DYE(RED) INJECTION SYSTEM 400-ME-003 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269813 | M410JBAI721 | JUNCTION BOX FOR DYE(BLUE) INJECTION SYSTEM 410-ME-001 | JUNCTION BOX FOR DYE(BLUE) INJECTION SYSTEM 410-ME-001 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269814 | M410JBAI731 | JUNCTION BOX FOR ANTI-STATIC INJECTION SYSTEM 410-ME-002 | JUNCTION BOX FOR ANTI-STATIC INJECTION SYSTEM 410-ME-002 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269815 | M410JBAI741 | JUNCTION BOX FOR CORROSION INHIBITOR 410-ME-010 | JUNCTION BOX FOR CORROSION INHIBITOR 410-ME-010 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269816 | M410JBAI751 | JUNCTION BOX FOR ANTI-FREEZE INJECTION SYSTEM 410-ME-011 | JUNCTION BOX FOR ANTI-FREEZE INJECTION SYSTEM 410-ME-011 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269817 | M410JBEI701 | JUNCTION BOX FOR DYE(GREEN) INJECTION SYSTEM 400-ME-002 | JUNCTION BOX FOR DYE(GREEN) INJECTION SYSTEM 400-ME-002 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269818 | M410JBEI711 | JUNCTION BOX FOR DYE(RED) INJECTION SYSTEM 400-ME-003 | JUNCTION BOX FOR DYE(RED) INJECTION SYSTEM 400-ME-003 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269819 | M410JBEI721 | JUNCTION BOX FOR DYE(BLUE) INJECTION SYSTEM 410-ME-001 | JUNCTION BOX FOR DYE(BLUE) INJECTION SYSTEM 410-ME-001 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269820 | M410JBEI731 | JUNCTION BOX FOR ANTI-STATIC INJECTION SYSTEM 410-ME-002 | JUNCTION BOX FOR ANTI-STATIC INJECTION SYSTEM 410-ME-002 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269821 | M410JBEI732 | JUNCTION BOX FOR ANTI-STATIC INJECTION SYSTEM 410-ME-002 | JUNCTION BOX FOR ANTI-STATIC INJECTION SYSTEM 410-ME-002 |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969130782 | M400ELP006 | DISTRIBUTION BOARD,LIGHTING, WAREHOUSE, /S-400, 400-ELP-001 FIRE & SAFETY | INDOOR EMERGENCY LIGHTING PANEL AT WAREHOUSE |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP006-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 29/09/18 | ME-PNL1-PM-M6
969130784 | M400ELP009 | DISTRIBUTION BOARD,LIGHTING, WWTP-ELECTRICAL ROOM, S/S-400,Fed from 400-ELP-001, FIRE & SAFETY | INDOOR EMERGENCY LIGHTING DISTRIBUTION APNEL AT WWTP ELECTRICAL ROOM |  | LIGHT | M400SCB | 1 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ELP009-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
969130786 | M400ETP001 | HEATER,ELECTRIC, HEAT TRACING PANEL, 415 V, S/S-400, 7 ER-6 | ELECTRICAL HEAT TRACING PANEL AT SCRAPPER AREA |  | ELEC_HTG | M400MOTOR | 3 | ELEC_HTG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400ETP001-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/01/19 | ME-PNL1-PM-M6
969130787 | M400ETP002 | HEATER,ELECTRIC, HEAT TRACING PANEL, 415V V, S/S-400,400-PC-001, 13 AR3 | ELECTRICAL HEAT TRACING PANEL NEAR PPD SKID AREA |  | ELEC_HTG | M400MOTOR | 3 | ELEC_HTG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | M400ETP002-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 26/01/19 | ME-PNL1-PM-M6
969132701 | M400ME019 | MOTOR,ELECTRIC, 0.25 KW, 50 HZ, 415 V, 3, 2.30 AMP, 400-MCC-001 | POLY DOSING SCREW CONVEYOR |  | MOTOR | M400WWTP | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400ME019-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/11/18 | ME-PM-014-M6
969132703 | M400ME021 | MOTOR,ELECTRIC, GEAR DRIVE MOTOR, 0.37 KW, 50 HZ, 415 V, 1500 RPM, 3, 1.95 AMP, 400-MCC-001 | MOTOR (GEAR DRIVE) OIL SKIMMER RECEIVING SUMP CHAIN II |  | MOTOR | M400WWTP | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400ME021-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 21/12/18 | ME-PM-014-M6
969132704 | M400ME022 | MOTOR,ELECTRIC, GEAR DRIVE MOTOR, 0.37 KW, 50 HZ, 415 V, 1500 RPM, 3, 1.95 AMP, 400-MCC-001 | MOTOR, PUMP OF T-219 WASTE WATER TREATMENT PLANT AT MUSAFFAH TERMINAL IRP-1 |  | MOTOR | M400WWTP | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | N | Low | Y | 0 | 6 | E | 0 | N | N | 0 | 0 | 0 | M400ME022-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 22/12/18 | ME-PM-014-M6
969132705 | M400ME023 | MOTOR,ELECTRIC, GEAR DRIVE MOTOR, 0.37 KW, 50 HZ, 415 V, 1500 RPM, 3, 1.95 AMP, 400-MCC-001 | GEAR DRIVE MOTOR OIL SKIMMER TANK 3 |  | MOTOR | M400WWTP | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400ME023-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/01/19 | ME-PM-014-M6
969132708 | M400ME026 | HEATER,ELECTRIC, 4.35 AMP, 230 V, 1.0 KW/M, 400-MCC-001 | ELECTRICAL HEATER ,EXHAUST AIR HUMIDITY ABSORBER |  | MOTOR | M400WWTP | 3 | ELEC_HTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132709 | M400ME029 | MOTOR,ELECTRIC, REFRIGERANT TYPE DRIVER, 0.25 KW, 50 HZ, 230 V, 1500 RPM, 1, 1.10 AMP, 400-MCC-001 | REFERIGERANT TYPE DRIVER |  | MOTOR | M400WWTP | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M400ME029-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 30/11/18 | ME-PM-014-M6
969132710 | M400AT255 | COD ANALYSER, 230VAC 50HZ | P&TD WWTP COD ANALYZER. OUTFLOW QUALITY CONTROL - SAC |  | ANALYSER | M400WWTPANALZ | 3 | ANALYSER | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132742 | M400LSHH736 | SWITCH,LEVEL | LEVEL SWITCH-INTERMEDIATE BUFFER TANK CHAIN II |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132796 | M400POV711 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-OUTFLOW AC FILTER -A |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV711-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/08/18 | MC-PM-026-M6
969132797 | M400POV712 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV- INFLOW AC FILTER B |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV712-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 21/08/18 | MC-PM-026-M6
969132798 | M400POV713 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-INFLOW AC FILTER B |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV713-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 28/08/18 | MC-PM-026-M6
969132799 | M400POV714 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-OUTFLOW AC FILTER B |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV714-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 04/09/18 | MC-PM-026-M6
969132730 | M400LSHH252 | SWITCH,LEVEL | LEVEL SWITCH CLEAR WATER TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132731 | M400LSHH259 | SWITCH,LEVEL | LEVEL SWITCH OIL COLLECTING TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132732 | M400LSHH262 | SWITCH,LEVEL | LEVEL SWITCH-CHEMICAL SLUDGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132733 | M400LSHH702 | SWITCH,LEVEL | LEVEL SWITCH - RECEIVING SUMP CHAIN I |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132734 | M400LSHH265 | SWITCH,LEVEL | LEVEL SWITCH - OILY SLUDGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132735 | M400LSHH706 | SWITCH,LEVEL | LEVEL SWITCH INTERMEDIATE BUFFER TANK CHAIN-1 |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132736 | M400LSHH709 | SWITCH,LEVEL | LEVEL SWITCH-COAGULANT STORAGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132738 | M400LSHH722 | SWITCH,LEVEL | LEVEL SWITCH-RECEIVING SUMP CHAIN II |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132739 | M400LSHH726 | SWITCH,LEVEL | LEVEL SWITCH EFFLUENT STORAGE TANK-1 |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132743 | M400LSHH739 | SWITCH,LEVEL | LEVEL SWITCH - AIR STRIPPER |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132744 | M400LSHH744 | SWITCH,LEVEL | LEVEL SWITCH INTERMEDIATE BUFFER TANK EFFFLUENT POLISHING |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132745 | M400LSLL253 | SWITCH,LEVEL | LEVEL SWITCH CLEAR WATER TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132747 | M400LSLL263 | SWITCH,LEVEL, 24VDC, YES | LEVEL SWITCH CHEMICAL SLUDGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132748 | M400LSLL266 | SWITCH,LEVEL, 24VDC, YES | LEVEL SWITCH - OILY SLUDGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132749 | M400LSLL703 | SWITCH,LEVEL | LEVEL SWITCH - RECEIVING SUMP CHAIN- I |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132750 | M400LSLL707 | SWITCH,LEVEL, 24VDC, YES | LEVEL SWITCH-INTERMEDIATE BUFFER TANK CHAIN -I |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132751 | M400LSLL710 | SWITCH,LEVEL | LEVEL SWITCH - COAGULANT STORAGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132801 | M400POV716 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-RECIRCULATION FLOW |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV716-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/09/18 | MC-PM-026-M6
969132824 | M400P218A | PUMP, CENTRIFUGAL | OUTFLOW PUMP A |  | PUCE | M400WWTPPUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 5 | 5 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P218A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-016-M6
969132825 | M400P218B | PUMP, CENTRIFUGAL | OUTFLOW PUMP B |  | PUCE | M400WWTPPUMP | 2 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P218B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/01/19 | MM-PM-016-M6
969132826 | M400P219A | PUMP, SCREW | OIL COLLECTING TANK PUMP -A |  | PUSC | M400WWTPPUMP | 3 | PUSC | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P219A-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 17/05/19 | MM-PM-015-Y1
969132827 | M400P219B | PUMP, SCREW | OIL COLLECTING TANK PUMP -B |  | PUSC | M400WWTPPUMP | 2 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P219B-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 18/05/19 | MM-PM-015-Y1
969132828 | M400P220 | PUMP, SCREW | DISCHARGE PUMP - CHEMICAL SLUDGE |  | PUSC | M400WWTPPUMP | 3 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P220-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 14/06/19 | MM-PM-015-Y1
969132829 | M400P221 | PUMP, SCREW | DISCHARGE PUMP - OILY SLUDGE |  | PUSC | M400WWTPPUMP | 3 | PUSC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P221-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 15/06/19 | MM-PM-015-Y1
969132830 | M400AG001 | AGITATOR MIXER INTERMEDIATE BUFFER TANK - CHAIN I | MIXER INTERMEDIATE BUFFER TANK - CHAIN I |  | MIX | M400WWTP | 3 | MIX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 5 | 1 | 2.0969 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | M400AG001-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 17/01/19 | MM-PM-024-M6
969132831 | M400AG002 | AGITATOR | MIXER POLYELECTROLYTE MAKE UP TANK |  | MIX | M400WWTP | 3 | MIX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 5 | 1 | 2.0969 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | M400AG002-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 18/01/19 | MM-PM-024-M6
969132832 | M400K001A | COMPRESSOR,AIR | WTP AIR COMPRESSOR - A |  | CORE | M400WWTP | 3 | CORE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 |  | M400K001A-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 22/05/19 | MM-PM-020-Y1
969132833 | M400K001B | BLOWER, AIR | AIR BLOWER - B |  | CORE | M400WWTP | 2 | CORE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 |  | M400K001B-MM1 | ACTIVE | MECH | PM | EDS | 1 | YEARS | 23/05/19 | MM-PM-020-Y1
969132835 | M400K002B | AIR COMPRESSOR. | PROCESS AIR STRIPPER BLOWER OF WASTE WATER TREATMENT PLANT AT MS&P TERMINAL. |  | FAN | M400WWTP | 2 | FAN | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 1 | 1 | 1 | 10 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | M400K002B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/12/18 | MM-PM-022-M6
969132752 | M400LSLL713 | SWITCH,LEVEL | LEVEL SWITCH-CAUSTIC SODA STORAGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132753 | M400LSLL723 | SWITCH,LEVEL | LEVEL SWITCH-RECEIVING SUMP CHAIN- II |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275072 | M410BAV21273003 | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275073 | M410BAV21273004 | 1" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe | 1" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275074 | M410BAV21273005 | 2" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe | 2" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275075 | M410BAV21273006 | 3" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe | 3" Ball Valve Reduced Bore, ISO 17292, Class 300, Female Threaded End, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269663 | M410P026A | 98 OCT BLUE DYE DILUTION RECIPROCATING PUMP | 98 OCT BLUE DYE DILUTION PUMP 410ME001. |  | PURE | M410ME001 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269664 | M410P026B | 98 OCT BLUE DYE DILUTION RECIPROCATING PUMP | 98 OCT BLUE DYE DILUTION PUMP 410ME001. |  | PURE | M410ME001 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269665 | M410P028A | ANTI FREEZE RECIPROCATING DILUTION PUMP. | ANTI FREEZE DILUTION PUMP 410ME011. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269666 | M410P028B | ANTI FREEZE RECIPROCATING DILUTION PUMP. | ANT IFREEZE DILUTION PUMP 410ME011. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269667 | M410P035A | GREEN DYE DILUENT RECIPROCATING PUMP. | 95 OCT DILUENT PUMP GREEN DYE INJECTION 400ME002. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269668 | M410P035B | GREEN DYE DILUENT RECIPROCATING PUMP. | 95 OCT DILUENT PUMP GREEN DYE INJECTION 400ME002. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269669 | M410P036A | RED DYE DILUENT RECIPROCATING PUMP. | 91 OCT DILUENT PUMP RED DYE INJECTION 400ME003. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269670 | M410P036B | RED DYE DILUENT RECIPROCATING PUMP. | 91 OCT DILUENT PUMP RED DYE INJECTION 400ME003. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269671 | M410MP026A | MOTOR FOR DILUTED DYE (BLUE) INJECTION PUMPS 410-P-026A | MOTOR FOR DILUTED DYE (BLUE) INJECTION PUMPS 410-P-026A |  | MOTOR | M410ME001 | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP026A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269672 | M410MP026B | MOTOR FOR DILUTED DYE (BLUE) INJECTION PUMPS 410-P-026B | MOTOR FOR DILUTED DYE (BLUE) INJECTION PUMPS 410-P-026B |  | MOTOR | M410ME001 | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP026B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269675 | M410PP002 | DISTRIBUTION PANEL | DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410PP002-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269676 | M410PP004 | DISTRIBUTION PANEL | DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410PP004-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269677 | M410PP005 | DISTRIBUTION PANEL | DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410PP005-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269679 | M410PP001 | DISTRIBUTION PANEL | DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410PP001-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969205032 | M410P033A | FIRE WATER PUMP- MOTOR | JOCKEY PUMP ELECTRIC MOTOR DRIVEN | 969147475 | MOTOR | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 12 | e | 0 | Y | Y | 0 | 0 | 0 | M410P033A-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 25/11/18 | MC-PM-02-M6
969269681 | M410LCP008 | DRYER LOCAL CONTROL PANEL | DRYER LOCAL CONTROL PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | M410LCP008-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269682 | M410MP036A | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-036A | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-036A |  | MOTOR | M410P036A | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP036A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269683 | M410MP036B | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-036B | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-036B |  | MOTOR | M410P036B | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP036B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269684 | M410T019 | DYE(BLUE) CHEMICAL STORAGE TANK | BLUE DYE CHEMICAL STORAGE TANK |  | PACKAGE | M410ME001 | 1 | PACKAGE | 0 | MTERMINAL | OPERATING | 1 | 1 | 1 | 10 | 50 | 10 | 3.699 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269685 | M410FT721 | FLOW TRANSMITTER FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 | FLOW TRANSMITTER FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 |  | PACKAGE | M410ME001 | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269686 | M410LT721 | LEVEL TRANSMITTER FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 | LEVEL TRANSMITTER FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 |  | PACKAGE | M410ME001 | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269687 | M410PSV721 | PRESSURE SAFETY VALVE FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 | PRESSURE SAFETY VALVE FOR BLUE DYE INJECTION PACKAGE 410-ME-001 FOR ULG 98. |  | PACKAGE | M410ME001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269688 | M410PSV722 | PRESSURE SAFETY VALVE FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 | PRESSURE SAFETY VALVE FOR BLUE DYE INJECTION PACKAGE 410-ME-001 FOR ULG 98. |  | PACKAGE | M410ME001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269689 | M410PSV723 | PRESSURE SAFETY VALVE FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 | PRESSURE SAFETY VALVE FOR BLUE DYE INJECTION PACKAGE 410-ME-001 FOR ULG 98. |  | PACKAGE | M410ME001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269690 | M410PSV724 | PRESSURE SAFETY VALVE FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 | PRESSURE SAFETY VALVE FOR BLUE DYE INJECTION PACKAGE 410-ME-001 FOR ULG 98. |  | PACKAGE | M410ME001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269691 | M410XV721 | PNEUMATIC VAVLE FOR DYE(BLUE) INJECTION PACKAGE FOR 410-ME-001 ULG 98 | PNEUMATIC VAVLE FOR BLUE DYE INJECTION PACKAGE FOR 410-ME-001 ULG 98 |  | PACKAGE | M410ME001 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269692 | M410XV722 | PNEUMATIC VAVLE FOR DYE(BLUE) INJECTION PACKAGE FOR 410-ME-001 ULG 98 | PNEUMATIC VAVLE FOR BLUE DYE INJECTION PACKAGE FOR 410-ME-001 ULG 98 |  | PACKAGE | M410ME001 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269693 | M410MP035A | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-035A | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-035A |  | MOTOR | M410P035A | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP035A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269968 | M410MOV229 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269969 | M410MOV230 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269970 | M410MOV2301A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P023A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269971 | M410MOV2301B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P023B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269972 | M410MOV2301C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P023C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269973 | M410MOV2302A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P023A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269974 | M410MOV2302B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P023B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269975 | M410MOV2302C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P023C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269976 | M410MOV231 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269977 | M410MOV232 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269978 | M410MOV233 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L009A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269979 | M410MOV234 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L009B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269980 | M410MOV235 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L009A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269981 | M410MOV236 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410L009B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269982 | M410MOV300A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P003A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269983 | M410MOV300B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P003B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269984 | M410MOV301A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P003A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269985 | M410MOV301B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P003B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269986 | M410MOV302A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P024A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269987 | M410MOV302B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P024B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269988 | M410MOV302C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P024C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269989 | M410MOV303A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P024A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269990 | M410MOV303B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P024B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269991 | M410MOV303C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P024C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269992 | M410MOV400AA | MOTOR OPERATED VALVE | JET A1 MOTOR OPERATED VALVE |  | MOV | M410FT400A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269993 | M410MOV400BA | MOTOR OPERATED VALVE | JET A1 MOTOR OPERATED VALVE |  | MOV | M410FT400B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269994 | M410MOV400CA | MOTOR OPERATED VALVE | JET A1 MOTOR OPERATED VALVE |  | MOV | M410FT400C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269995 | M410MOV401AA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT401A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269996 | M410MOV401BA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT401B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269997 | M410MOV401CA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT401C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269998 | M410MOV402 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269999 | M410MOV403 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PLR001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270000 | M410MOV406A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270001 | M410MOV406B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270002 | M410MOV406C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270003 | M410MOV406D | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270004 | M410MOV406E | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270005 | M410MOV407A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270006 | M410MOV407B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270007 | M410MOV407C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270008 | M410MOV407D | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 3 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270009 | M410MOV407E | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270010 | M410MOV410 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410PT412 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270096 | M410PSV752A | OIL RELIEF VALVE FOR COMPRESSOR | OIL RELIEF VALVE FOR COMPRESSOR |  | PSV | M410K001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270097 | M410PSV752B | OIL RELIEF VALVE FOR COMPRESSOR | OIL RELIEF VALVE FOR COMPRESSOR |  | PSV | M410K001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270098 | M410PSV753A | OIL RELIEF VALVE FOR COMPRESSOR | OIL RELIEF VALVE FOR COMPRESSOR |  | PSV | M410K001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270099 | M410PSV753B | OIL RELIEF VALVE FOR COMPRESSOR | OIL RELIEF VALVE FOR COMPRESSOR |  | PSV | M410K001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270100 | M410PSV754A | OIL RELIEF VALVE FOR COMPRESSOR | OIL RELIEF VALVE FOR COMPRESSOR |  | PSV | M410K001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270101 | M410PSV754B | OIL RELIEF VALVE FOR COMPRESSOR | OIL RELIEF VALVE FOR COMPRESSOR |  | PSV | M410K001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270102 | M410D093A | OIL TANK FOR COMPRESSOR | OIL TANK FOR COMPRESSOR |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 10 | 10 | 1 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270103 | M410D093B | OIL TANK FOR COMPRESSOR | OIL TANK FOR COMPRESSOR |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 10 | 10 | 1 | 10 | 4.699 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270104 | M410FMS001 | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, MUSSAFAH TERMINAL | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, MUSSAFAH TERMINAL |  | BLDGS | M410SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | M410FMS001-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969270105 | M410FMS002 | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, MUSSAFAH TERMINAL | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, MUSSAFAH TERMINAL |  | BLDGS | M410SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | M410FMS002-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969270106 | M410FMS003 | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, MUSSAFAH TERMINAL | PANEL FOR CUSTODY TRANSFER METERING SYSTEM, MUSSAFAH TERMINAL |  | BLDGS | M410SCB | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | M410FMS003-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969270113 | M410P021 | 98 OCT BLUE DYE FILLING PNEUMATIC PUMP | 98 OCT BLUE DYE FILLING PNEUMATIC PUMP FOR FILLING 410ME001. |  | PURE | M410ME001 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270114 | M410P022 | 98 OCT BLUE DYE FILLING PNEUMATIC PUMP | DHAFRA ANTI-STATIC FILLING PNEUMATIC PUMP FOR FILLING 410ME002. |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270115 | M410P032 | CORROSION INHIBITOR FILLING PNEUMATIC PUMP | CORROSION IN HIBITOR FILLING PNEUMATIC PUMP 410ME010. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270116 | M410P202 | GAS OIL FILLING PNEUMATIC PUMP | GAS OIL FILLING PNEUMATIC PUMP |  | PURE | M410ME201 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270117 | M410PDB003 | POWER DISTRIBUTION BOARD CABINET FOR SIS-001DCSSYSTEM | POWER DISTRIBUTION BOARD SIS - 001 |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270118 | M410PDT761A | Pre, After Filter Diff. Pressure Sensor | Pre, After Filter Diff. Pressure Sensor |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT761A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270119 | M410PDT761B | Pre, After Filter Diff. Pressure Sensor | Pre, After Filter Diff. Pressure Sensor |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT761B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270120 | M410PDT762A | Pre, After Filter Diff. Pressure Sensor | Pre, After Filter Diff. Pressure Sensor |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT762A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270121 | M410PDT762B | Pre, After Filter Diff. Pressure Sensor | Pre, After Filter Diff. Pressure Sensor |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT762B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270122 | M410L093A | PRE-FILTERS | PRE-FILTERS |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270123 | M410L093B | PRE-FILTERS | PRE-FILTERS |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270124 | M410PG203AA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270125 | M410PG203AB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270126 | M410PG203BA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270127 | M410PG203BB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270128 | M410PG206AA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270129 | M410PG206AB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270130 | M410PG206BA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270131 | M410PG206BB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270132 | M410PG209AA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270133 | M410PG209AB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270134 | M410PG209BA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270135 | M410PG209BB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270136 | M410PG211AA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270137 | M410PG211AB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270138 | M410PG211BA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270139 | M410PG211BB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270140 | M410PG400AA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270141 | M410PG400AB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270142 | M410PG400BA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270143 | M410PG400BB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270144 | M410PG400CA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270145 | M410PG400CB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270146 | M410PG401AA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270147 | M410PG401AB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270148 | M410PG401BA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270149 | M410PG401BB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270150 | M410PG401CA | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270151 | M410PG401CB | Pressure Gauge | Pressure Gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270152 | M410PG120 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270153 | M410PG271 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P001A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270154 | M410PG272 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P001A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270155 | M410PG273 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P001B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270156 | M410PG274 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P001B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932832 | M400BD42211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932833 | M400BD42611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932834 | M400BD43011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , FLANGED , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932835 | M400BD44411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932836 | M400BD44911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932837 | M400BD47211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 1" , 150 LB | SIGHT FLOW INDICATOR, SIZE-1" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932838 | M400BD47811051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 1" , 150 LB | SIGHT FLOW INDICATOR, SIZE-1" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932839 | M400BD49211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932840 | M400BD50011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932841 | M400BD50111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932842 | M400BD50211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932843 | M400BD514711051X | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932844 | M400BD53211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932845 | M400BD53311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932846 | M400BD54011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932847 | M400BD54811051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932848 | M400BD55011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932849 | M400BD55311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932850 | M400BD58011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932851 | M400BD60311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932852 | M400BD60611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932853 | M400BD60811051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932854 | M400BD61311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 1" , 150 LB | SIGHT FLOW INDICATOR, SIZE-1" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932855 | M400BD65211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 4" , 150 LB | SIGHT FLOW INDICATOR, SIZE-4" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932856 | M400BD65711051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932857 | M400BD75111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932858 | M400BD76211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932859 | M400BD78211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932860 | M400BD80211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932861 | M400BD80611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932862 | M400BD85111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 3" , 150 LB | SIGHT FLOW INDICATOR, SIZE-3" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932863 | M400BD85911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932864 | M400BD87411051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932865 | M400BD89011051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932866 | M400BD89111051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932867 | M400BD89711051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932868 | M400BD92611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932869 | M400BD93211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 1" , 150 LB | SIGHT FLOW INDICATOR, SIZE-1" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932870 | M400BD96311051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 1" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932871 | M400BD96611051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 1" , 150 LB | SIGHT FLOW INDICATOR, SIZE-1" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932872 | M400BD97211051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 2" , 150 LB | SIGHT FLOW INDICATOR, SIZE-2" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932873 | M400BD97911051XV | INDICATOR, SIGHT FLOW, SINGLE WINDOW PLAIN , HARD GLASS , 1" , 150 LB | SIGHT FLOW INDICATOR, SIZE-1" |  | INDICATR | M400FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932874 | MQ600BD0211051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-3" |  |  | MQ600FLOW | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932875 | MQ600BD0411051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-2" |  |  | MQ600FLOW | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933617 | M400MOV890 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" CL 900, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR BATTERY LIMIT (ULG 95 / ULG 98 / JET A1 / GO, 10" CL 900) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV890-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/12/18 | ME-PM-002-M6
933624 | MQ600MOV001 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" CL 900, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | ULG 95 / ULG 98 / JET A1 / GO, 10" CL 900 |  | MOV | MQ600MOV | 2 | MOV | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | MQ600MOV001-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933625 | MQ600MOV002 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 900, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ25F14B4, IP68, 203Nm | ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 900 |  | MOV | MQ600MOV | 2 | MOV | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | MQ600MOV002-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933626 | MQ600MOV003 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" CL 900, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ25F14B4, IP68, 203Nm | ULG 95 / ULG 98 / JET A1 / GO, 10" CL 900 |  | MOV | MQ600MOV | 2 | MOV | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | MQ600MOV003-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933627 | MQ600MOV004 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 900, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ25F14B4, IP68, 203Nm | ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 900 |  | MOV | MQ600MOV | 2 | MOV | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | MQ600MOV004-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933628 | MQ600MOV005 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 900, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ25F14B4, IP68, 203Nm | ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 900 |  | MOV | MQ600MOV | 2 | MOV | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | MQ600MOV005-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933629 | MQ600MOV006 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" CL 900, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ25F14B4, IP68, 203Nm | ULG 95 / ULG 98 / JET A1 / GO, 10" CL 900 |  | MOV | MQ600MOV | 2 | MOV | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | MQ600MOV006-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933953 | M400VA34GA095 | GATE VALVE | GATE VALVE, 3/4" 800 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933954 | M400VA34GA096 | GATE VALVE | GATE VALVE, 3/4" 800 LB, SW+NPT |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933955 | M400VA34GA191 | GATE VALVE | GATE VALVE, 3/4" 1500 LB, SW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933956 | M400VA34GA192 | GATE VALVE | GATE VALVE, 3/4" 1500 LB, BW |  | VALVE | M400VALVE | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934154 | PL300PG30302B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #2 |  |  | PL300SVS2 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934155 | PL300PG30303A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #3 |  |  | PL300SVS3 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934156 | PL300PG30303B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #3 |  |  | PL300SVS3 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934157 | PL300PG30305A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #5 |  |  | PL300SVS5 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934158 | PL300PG30305B | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #5 |  |  | PL300SVS5 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934159 | PL300PG30306A | GAUGE PRESSURE | PRESSURE GAUGE AT VALVE STATION #6 |  |  | PL300SVS6 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934160 | PL300PG30306B | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | PRESSURE GAUGE AT VALVE STATION #6 |  |  | PL300SVS6 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934161 | M400PDI928 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Suction for FW Pump 400-P-203A | 936409 |  | M400P203A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI928-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/10/18 | MC-PM-011-M3
934162 | M400PDI929 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Suction for FW Pump 400-P-203B | 936410 |  | M400P203B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI929-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/10/18 | MC-PM-011-M3
934163 | M400PDI930 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Suction for FW Pump 400-P-201A | 936404 |  | M400P201A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI930-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/10/18 | MC-PM-011-M3
934164 | M400PDI931 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Suction for FW Pump 400-P-201B | 936405 |  | M400P201B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI931-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/10/18 | MC-PM-011-M3
934165 | M400PDI932 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Suction for FW Pump 400-P-201C | 936406 |  | M400P201C | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI932-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/10/18 | MC-PM-011-M3
934166 | M400PDI933 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Suction for FW Pump 400-P-202 | 936408 |  | M400P202 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI933-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 13/10/18 | MC-PM-011-M3
934167 | M400PDI934 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI934-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/10/18 | MC-PM-011-M3
934168 | M400PDI935 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI935-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/10/18 | MC-PM-011-M3
934169 | M400PDI936 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/DIFF. PRESSURE GAUGE |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI936-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 20/10/18 | MC-PM-011-M3
934170 | M400PDI937 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI937-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 24/10/18 | MC-PM-011-M3
934171 | M400PDI938 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI938-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 26/01/19 | MC-PM-011-M3
934172 | M400PDI939 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI939-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/08/18 | MC-PM-011-M3
934173 | M400PDI940 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water PIT Storage (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI940-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/08/18 | MC-PM-011-M3
934174 | M400PDI942 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI942-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/08/18 | MC-PM-011-M3
934175 | M400PDI950 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI950-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/08/18 | MC-PM-011-M3
934176 | M400PDI960 | GAUGE, DIFFERENTIAL PRESSURE, 0-0.1 KG/CM2 , 100MM , ½ NPTF , SS316 , SS316 , SS | Inlet Line of Potable water U/G Storage Tank (RCC) |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PDI960-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM-016-M6
934177 | M400PG001 | GAUGE, PRESSURE, BOURDON TUBE , -1-+3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | SUCTION PRESSURE GAUGE OF M400P021A |  |  | M400P021A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934178 | M400PG002 | GAUGE, PRESSURE, BOURDON TUBE , -1-+3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | SUCTION PRESSURE GAUGE OF M400P021B | 934052 |  | M400P021B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934179 | M400PG003 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS | SUCTION PRESSURE GAUGE OF M400P021C | 934053 |  | M400P021C | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934180 | M400PG004 | GAUGE, PRESSURE, BOURDON TUBE , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Discharge Pressure at 400-P-021A | 934051 |  | M400P021A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934181 | M400PG005 | GAUGE, PRESSURE, BOURDON TUBE , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Discharge Pressure at 400-P-021B | 934052 |  | M400P021B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934182 | M400PG006 | GAUGE, PRESSURE, BOURDON TUBE , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Discharge Pressure at 400-P-021C | 934053 |  | M400P021C | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934183 | M400PG007 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS | SUCTION PRESSURE GAUGE OF M400P024A | 934056 |  | M400P024A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934184 | M400PG008 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS | SUCTION PRESSURE GAUGE OF M400P024B | 934057 |  | M400P024B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934185 | M400PG009 | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | DISCHARGE PRESSURE GAUGE OF M400P022A | 934054 |  | M400P022A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934186 | M400PG010 | GAUGE, PRESSURE, BOURDON TUBE , 0 TO 10 , 100MM , ½" NPTM , SS 316L , SS 316 , B | Discharge Pressure at 400-P-022B | 934055 |  | M400P022B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934187 | M400PG015 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 , 100MM , ½" NPTM , SS 316L , SS 316 , B | Suction Pressure at 400-P-024A | 934056 |  | M400P024A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934188 | M400PG016 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 , 100MM , ½" NPTM , SS 316L , SS 316 , B | Suction Pressure at 400-P-024B | 934057 |  | M400P024B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934189 | M400PG17A | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | SEAL OIL PRESSURE GAUGE FOR PUMP M400P17A | 933876 |  | M400P017A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934190 | M400PG018 | GAUGE, PRESSURE, DIRECT , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , BOT | Discharge Pressure at 400-P-024B | 934057 |  | M400P024B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934191 | M400PG502 | GAUGE, PRESSURE, BOURDON TUBE , 0 TO 160 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. Scrapper Receiver 400-PLR-002 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934192 | M400PG503 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pr. Scrapper Receiver 400-PLR-002 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934193 | M400PG504 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. Naphtha Reformate P/L from ADR to Ruwais |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934194 | M400PG505 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. Naph. Ref. P/L from ADR to 400-PLR-002 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934195 | M400PG506 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. Scrapper Launcher 400-PLR-003 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934196 | M400PG507 | GAUGE, PRESSURE, INDICATION , -1-+3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. Scrapper Launcher 400-PLR-003 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934197 | M400PG508 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. Naph. Ref. P/L from ADR to 400-PLR-002 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934198 | M400PG548 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Off Spec Jet A1 Booster Pump 400-P-020 Suction Pr. | 933878 |  | M400P020 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934199 | M400PG549 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Off Spec Jet A1Booster Pump 400-P-020 Discharge Pr | 933878 |  | M400P020 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934200 | M400PG553 | GAUGE, PRESSURE, INDICATION , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. at Outlet of Metering Skid 400-FT-772 | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934201 | M400PG554 | GAUGE, PRESSURE, INDICATION , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Off spec Jet A1 Mainline Pump 400-P-019 Suction Pr | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934202 | M400PG555 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | DISCHARGE PRESSURE GAUGE FOR M400P019 | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934203 | M400PG561 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pr. Off spec Jet A1 line from Stor. Tank to 40-P-0 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934204 | M400PG567 | GAUGE, PRESSURE, INDICATION , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Pr. Scrapper Recvr. 400-PLR-006 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934205 | M400PG568 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , | Pr. Scrapper Recvr. 400-PLR-006 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934206 | M400PG569 | GAUGE, PRESSURE, INDICATION , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Pr. ADR Ruwais SRR P/L to Ruwais Recpt. Terminal |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934207 | M400PG570 | GAUGE, PRESSURE, INDICATION , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Pr. ADR Ruwais SRR P/L to Scr. Rec. 400-PLR-006 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934208 | M400PG572 | GAUGE, PRESSURE, INDICATION , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Pr. Scrapper Launcherr. 400-PLR-007 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934209 | M400PG573 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , | Pr. Scrapper Launcherr. 400-PLR-007 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934210 | M400PG574 | GAUGE, PRESSURE, INDICATION , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Pr. ADR Ruwais SRR P/L to Ruwais Recpt. Terminal |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934211 | M400PG575 | GAUGE, PRESSURE, INDICATION , 0-100 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Pr. ADR Ruwais SRR P/L from Scr. Launch. 400-PLR-0 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934212 | M400PG576 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , 2" RF FLANGE , SS 316L , SS | Pr. for Sump TankSRR P/L 400-V-175 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934213 | M400PG577 | GAUGE, PRESSURE, INDICATION , 0-160 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. for Sump Tank MP P/L 400-V-176 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934214 | M400PG615 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-296 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934215 | M400PG616 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-298 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934216 | M400PG617 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-302 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934217 | M400PG618 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-297 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934218 | M400PG619 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-300 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934219 | M400PG620 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-313 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934220 | M400PG621 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-316 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934221 | M400PG622 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-318 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934222 | M400PG623 | GAUGE, PRESSURE, INDICATION , 0-16 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Hydrant 400-ME-283 Pressure |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934223 | M400PG625 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS | Sump Tank Pressure Gauge |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934224 | M400PG652 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. Scrapper Recvr. 400-PLR-011 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934225 | M400PG653 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pr. Scrapper Recvr. 400-PLR-011 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934226 | M400PG655 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. Ruwais-Mussafah MP P/L to Jet A1/GO/ULG 95/98 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934227 | M400PG665 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. Rws-Mussafah MP P/L to Scr. Recvr. 400-PLR-011 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934228 | M400PG671 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. Ruwais-Mussafah MP P/L to Jet A1/GO/ULG 95/98 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934229 | M400PG751 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pressure at Jet A1 P/L from storage tanks |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934230 | M400PG753 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pressure at Jet A1 P/L from storage tanks |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934231 | M400PG757 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS | Mussafah-Adia Jet A1 P/L Suct. Pr. of 400-P-017A | 933876 |  | M400P017A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934232 | M400PG758 | GAUGE, PRESSURE, BOURDON TUBE , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS | Mussafah-Adia Jet A1 P/L Suct. Pr. of 400-P-017B | 933877 |  | M400P017B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934233 | M400PG759 | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Mussafah-Adia Jet A1 P/L Disch. Pr. of 400-P-017A | 933876 |  | M400P017A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934234 | M400PG760 | GAUGE, PRESSURE, BOURDON TUBE , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Mussafah-Adia Jet A1 P/L Disch. Pr. of 400-P-017B | 933877 |  | M400P017B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934235 | M400PG763 | GAUGE, PRESSURE, INDICATION , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Prssure at Filt. Coalescer 400-L-004A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934236 | M400PG802 | GAUGE, PRESSURE, INDICATION , 0-4 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pressure at Jet A1 P/L to 400-P-018A/B | 935830 |  | M400P019 | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934237 | M400PG805 | GAUGE, PRESSURE, INDICATION , 0-4 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Suction Pr. of 400-P-018A at Jet A1 P/L | 935828 |  | M400P018A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934238 | M400PG806 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Discharge Pr. of 400-P-018A at Jet A1 P/L | 935828 |  | M400P018A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934239 | M400PG809 | GAUGE, PRESSURE, INDICATION , 0-4 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Suction Pr. of 400-P-018B at Jet A1 P/L |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934240 | M400PG810 | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Discharge Pr. of 400-P-018B at Jet A1 P/L | 935829 |  | M400P018B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207826 | M410MS001 | 3.3kV SWITCHGEAR Panel | 3.3kV SWITCHGEAR |  | SWBOARD | M410SCB | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS001-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969207837 | M400POV887 | VALVE,SEQUENCIAL CONTROL/ESD, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN | ESD VALVE MUSSAFFAH-TIE IN MP P/L | 936427 |  | M400VALVE | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269288 | M410D091B | 1st DRAIN SEPARATOR FOR COMPRESSOR | 1st DRAIN SEPARATOR FOR COMPRESSOR |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269289 | M410K091A | 1ST STAGE OF COMPRESSOR FOR 410-K-001A AIR COMPRESSOR UNIT | 1ST STAGE OF COMPRESSOR FOR 410-K-001A AIR COMPRESSOR UNIT |  | COMPRS | M410K001A | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269290 | M410K091B | 1ST STAGE OF COMPRESSOR FOR 410-K-001B AIR COMPRESSOR UNIT | 1ST STAGE OF COMPRESSOR FOR 410-K-001B AIR COMPRESSOR UNIT |  | COMPRS | M410K001B | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269291 | M410PDT751A | 1st Suction Pressure Transmitter | 1st Suction Pressure Transmitter |  | PRES_TX | M410K001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT751A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269292 | M410PDT751B | 1st Suction Pressure Transmitter | 1st Suction Pressure Transmitter |  | PRES_TX | M410K001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT751B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969132785 | MGATEAC1 | HVAC, SPLIT, 2.5 TON, 30,000.0 BTU/HR, TTK530KB00GA | SPLIT AC UNIT AT MAIN GATE OF MUSAFFAH TERMINAL IRP-1 |  | HVAC | MGATE1 | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132786 | MGATEAC2 | HVAC, SPLIT, 2.5 TON, 30,000.0 BTU/HR, 230.0 V, TTK 530KB00GA | SPLIT A/C NO.2 AT MAIN GATE OF MUSAFFAH TERMINAL IRP NO.1 |  | HVAC | MGATE1 | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132787 | M400POV701 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-OIL SEPERATOR CHAIN -1 |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV701-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/11/18 | MC-PM-026-M6
969132789 | M400POV703 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV2-DISSOLVED AIR FLOTATION |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV703-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/11/18 | MC-PM-026-M6
969132791 | M400POV705 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV - OUTFLOW SAFETY FILTER |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV705-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 08/12/18 | MC-PM-026-M6
969132792 | M400POV707 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-FLUSHING WATER OUTFLOW SAFETY FILTER |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV707-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 12/01/19 | MC-PM-026-M6
969132793 | M400POV708 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-OIL SEPERATOR CHAIN - II |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV708-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/01/19 | MC-PM-026-M6
969132794 | M400POV709 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-INFLOW AC FILTER-A |  | SD_VLV | M400WWTP | 1 | SD_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV709-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/01/19 | MC-PM-026-M6
969132795 | M400POV710 | VALVE,SEQUENCIAL CONTROL/ESD | PNEUMATIC DRIVEN BV-BYPASS AC FILTER-A |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | M400POV710-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/08/18 | MC-PM-026-M6
EMV57071 | S21MOV112 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOV, PIG LAUNCHER S21R102 |  | MOV | S21R02 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57072 | S21MOV110 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | BY PASS MOTOR OPERATED VALVE TO PIG LAUNCHER |  | MOV | S21R02 | 2 | MOV | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57073 | S21MOV109 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE FROM SANT TO AVIATION |  | MOV | S21R02 | 2 | MOV | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57501 | M51MOV107 | ACTUATOR ELECTRIC MOTOR | MOV AT LPG PIPELEINE PIG RECEIVER IN MTF |  | MOV | M5101R02 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M51MOV107-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/11/18 | ME-PM-002-M6
EMV57502 | M51MOV109 | ACTUATOR ELECTRIC MOTOR | MOV AT LPG PIPELEINE PIG RECEIVER IN MTF |  | MOV | M5101R02 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M51MOV109-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/12/18 | ME-PM-002-M6
EMV57502931277 | M51MOV108 | ACTUATOR ELECTRIC MOTOR | MOV AT LPG PIPELEINE PIG RECEIVER IN MTF |  | MOV | M5101R02 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M51MOV108-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/11/18 | ME-PM-002-M6
EMV57503 | M15MOV117 | ACTUATOR ELECTRIC MOTOR | MOV AT MULTIPRODUCT PIPELEINE PIG RECEIVER IN MTF |  | MOV | M15R04 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M15MOV117-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/11/18 | ME-PM-002-M6
EMV57504 | M15MOV118 | ACTUATOR ELECTRIC MOTOR | MOV AT MULTIPRODUCT PIPELEINE PIG RECEIVER IN MTF |  | MOV | M15R04 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M15MOV118-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
EMV57505 | M15MOV119 | ACTUATOR ELECTRIC MOTOR | MOV AT MULTIPRODUCT PIPELEINE PIG RECEIVER IN MTF |  | MOV | M15R04 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M15MOV119-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/11/18 | ME-PM-002-M6
EMV57506 | M10MOV541 | ACTUATOR, ELECTRIC MOTOR, MULTI PRODUCT , DATA N/A , DATA N/A , DATA N/A DEGC, D | MOV FOR MULTI PRODUCT METERING INLET. |  | MOV | M10INLETMET | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV541-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57507 | M10MOV542 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | MOV FOR MULTI PRODUCT MANIFOLD INLET. |  | MOV | M10INLETMAN | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV542-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57508 | M10MOV543 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | MOV FOR MULTI PRODUCT MANIFOLD INLET. |  | MOV | M10INLETMAN | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV543-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57509 | M10MOV544 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | MOV FOR MULTI PRODUCT MANIFOLD INLET. |  | MOV | M10INLETMAN | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV544-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57510 | M10MOV545 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | MOV FOR MULTI PRODUCT MANIFOLD INLET. |  | MOV | M10INLETMAN | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV545-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57511 | M10MOV546 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | MOV FOR MULTI PRODUCT MANIFOLD INLET. |  | MOV | M10INLETMAN | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV546-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57512 | M10MOV561 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-101. |  | MOV | M10T101 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV561-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57513 | M10MOV562 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-101. |  | MOV | M10T101 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV562-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57515 | M50MOV124A | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY MOV FOR TANK T-101 , | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-101. |  | MOV | M10T101 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV124A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/12/18 | ME-PM-002-M6
EMV57516 | M50MOV124B | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY MOV FOR TANK T-101 , | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-101. |  | MOV | M10T101 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV124B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/01/19 | ME-PM-002-M6
EMV57519 | M10MOV564 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-102. |  | MOV | M10T102 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV564-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57520 | M10MOV565 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-102. |  | MOV | M10T102 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | M10MOV565-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/01/19 | ME-PM-002-M6
EMV57522 | M50MOV125A | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY MOV FOR TANK T-102 , | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-102. |  | MOV | M10T102 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV125A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/01/19 | ME-PM-002-M6
EMV57523 | M50MOV125B | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY MOV FOR TANK T-102 , | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-102. |  | MOV | M10T102 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV125B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/02/19 | ME-PM-002-M6
EMV57526 | M10MOV567 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | INLET MOTOR OPERATED VALVE (MOV) FOR TANK T-103. |  | MOV | M10T103 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 |  | AA213MOV146-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
EMV57527 | M10MOV568 | ACTUATOR, ELECTRIC MOTOR, DATA N/A , DATA N/A , DATA N/A , DATA N/A DEGC, DATA N | OUTLET MOTOR OPERATED VALVE (MOV) FOR TANK T-103. |  | MOV | M10T103 | 2 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EMV57529 | M50MOV126A | ACTUATOR, ELECTRIC MOTOR, WATER , FIRE FIGHTING WATER SPRAY MOV FOR TANK T-103 , | FIRE FIGHTING WATER SPRAY MOV FOR TANK T-103. |  | MOV | M10T103 | 2 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M50MOV126A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/02/19 | ME-PM-002-M6
969253231 | M410FU118 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253223 | M410STL2362001 | LIGHTING AND FIXTURES | LIGHTING AND FIXTURES |  |  | M410SCB | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253224 | M410FU111 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253225 | M410FU112 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253226 | M410FU113 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253227 | M410FU114 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253228 | M410FU115 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253230 | M410FU117 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938800 | M400XGC207 | DETECTOR, GAS | Flammable GD for Inter Tank Transfer Pump 400P021C | 934053 | FG_DET | M400P021C | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC207-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 26/09/18 | MFPS-PM02.M3
938801 | M400XGC208 | DETECTOR, GAS | Flammable GD in Inter Tank Tranfer Pump 024A (10% | 934056 | FG_DET | M400P024A | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC208-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 29/09/18 | MFPS-PM02.M3
938802 | M400XGC209 | DETECTOR, GAS | Flammable GD in Inter Tank Tranfer Pump 024B (10% | 934057 | FG_DET | M400P024B | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC209-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 04/10/18 | MFPS-PM02.M3
938803 | M400XGC211 | DETECTOR, GAS | Flammable GD for 400-PLR-003 for Scraper L/R Area |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC211-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 02/08/18 | MFPS-PM02.M3
938804 | M400XGC212 | DETECTOR, GAS | Flammabe GD for 400-PLR-011 in Scraper L/R |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC212-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 04/08/18 | MFPS-PM02.M3
938805 | M400XGC213 | DETECTOR, GAS | Flammable GD for 400-PLR-12 for Scraper L/R |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC213-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 09/08/18 | MFPS-PM02.M3
938806 | M400XGC214 | DETECTOR, GAS | Flammable GD for 400-PLR-002/ Scraper L/R Area |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC214-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 11/08/18 | MFPS-PM02.M3
938807 | MTERMINAL | OIL STORAGE TERMINAL AT MUSSAFAH. | OIL PIPELINES & STORAGE VIA MUSSAFAH TERMINAL. |  |  | SD | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938808 | M400XGC215 | DETECTOR, GAS | Flammable GD for Sump Tank 400-V-175 | 937629 | FG_DET | M400V175 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC215-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 06/10/18 | MFPS-PM02.M3
938809 | M400XGC216 | DETECTOR, GAS | Flammabe GD for Sump Tank 400-V-176 | 937630 | FG_DET | M400V176 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGC216-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 11/10/18 | MFPS-PM02.M3
938810 | M400XGH001 | DETECTOR, HYDROGEN GAS | H2 Gas Detector for Battery Room-PLCR |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGH001-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 16/08/18 | MFPS-PM02.M3
938811 | M400XGH002 | DETECTOR, HYDROGEN GAS | H2 Gas Detector for Battery Room-PLCR |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGH002-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 18/08/18 | MFPS-PM02.M3
938812 | M400XGH003 | DETECTOR, HYDROGEN GAS | H2 Gas Detector for Battery Room-PLCR |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGH003-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 23/08/18 | MFPS-PM02.M3
938813 | M400XGH004 | DETECTOR, HYDROGEN GAS | Hydrogen Gas Detector in Substation's Battery Room |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGH004-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 25/08/18 | MFPS-PM02.M3
938814 | M400XGH005 | DETECTOR, HYDROGEN GAS | Hydrogen Gas Detector in Substation's Battery Room |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGH005-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 28/08/18 | MFPS-PM02.M3
938815 | M400XGH006 | DETECTOR, HYDROGEN GAS | Hydrogen Gas Detector in Substation's Battery Room |  | FG_DET | M400MISC | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M400XGH006-UFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 01/09/18 | MFPS-PM02.M3
938816 | M400LI461C | INDICATOR | Lube Oil Reservoir - Level For 400-P-019 | 935830 | OPENLOOP | M400P019 | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400LI461C-MC1 | INACTIVE | CONT | PM | FIC | 1 | YEARS | 05/07/18 | MC-PM-004-Y1
938834 | M400PT421 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20mA , 10.5-30 VDC , 1/2" | PLAN 53 B - PRESSURE TRANSMITTER (M400P016B) | 936301 | PRES_TX | M400PI421C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938835 | M400PT416 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20mA , 10.5-30 VDC , 1/2" | LUBE OIL DISCHARGE PRESS. TX PUMP A (M400P016B) | 939780 | PRES_TX | M400PI416C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938836 | M400PT417 | TRANSMITTER, PRESSURE, PRESSURE TRANSMITTER-SMART , 4-20mA , 10.5-30 VDC , 1/2" | LUBE OIL DISCHARGE PRESS. TX PUMPB (M400P016B) | 939782 | PRES_TX | M400PI417C | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938837 | M400ZE416A | PROBE, VIBRATION , 8MM , 0.5 M | Pump - Thrust Bearing - 2nd "Z" Plane for M400P016B. | 935827 | VIBRE_TX | M400P016B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400ZE416A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/10/18 | MC-PM-012-M3
938838 | M400ZE416B | PROBE, VIBRATION , 8MM , 0.5 M | Pump - Thrust Bearing - 2nd "Z" Plane for M400P016B. | 935827 | VIBRE_TX | M400P016B | 1 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | M400ZE416B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/10/18 | MC-PM-012-M3
938839 | M400PT771A | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | Pr. at 400-FT-771A in Muss.- ADIA JET A1 P/L | 938686 | PRES_TX | M400FC771A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT771A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 27/06/19 | MC-PM-007-Y1
938840 | M400PT771B | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | Pr. at 400-FT-771B in Muss.- ADIA JET A1 P/L | 938687 | PRES_TX | M400FC771B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT771B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 28/06/19 | MC-PM-007-Y1
938841 | M400TT771A | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX MUSSAFAH -ALAIN P/L | 939216 | TEMP_TX | M400TI771A | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938842 | M400TT771B | TRANSMITTER, TEMPERATURE, SMART , 0-100 DEG C , 4-20MA , 12-42.4VDC , 1/2" NPT , | TEMP. TX MUSSAFAH -ALAIN P/L | 939217 | TEMP_TX | M400TI771B | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938843 | M400PDT771B | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | Diff. Pressure at 400-FT-771B | 939748 |  | M400PDI771B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938844 | M400PDT772 | TRANSMITTER, DIFFERENTIAL PRESSURE, ELECTRONIC , 0-2 KG/CM2 , 4-20MA , 10.5-42.4 | D.P. TX 400-FT-772,CUSTODY METERING SYSTEM | 939749 |  | M400PDI772 | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938845 | M400FE771A | SENSOR, DIFFERENTIAL PRESSURE | FLOW METER MUSSAFAH ALAIN P/L | 938686 | FL_MTR | M400FC771A | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938846 | M400FE771B | SENSOR, DIFFERENTIAL PRESSURE | FLOW METER MUSSAFAH ALAIN P/L | 938687 | FL_MTR | M400FC771B | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938847 | M400PT861A | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX MUSSAFAH ALAIN MULTI PRODUCT P/L | 938689 | PRES_TX | M400FC861A | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT861A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 03/08/18 | MC-PM-007-Y1
938848 | M400PT861B | TRANSMITTER, PRESSURE, GAGE , 0-800 PSIG , 4-20MA , 10.5-30 VDC , 1/2"-14 NPT , | PRESS. TX MUSSAFAH ALAIN MULTI PRODUCT P/L | 938690 | PRES_TX | M400FC861B | 2 | PRES_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400PT861B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 08/08/18 | MC-PM-007-Y1
969130672 | M400MP015B | MOTOR,ELECTRIC, BOOSTER PUMP 'B' FOR ALAIN MAIN LINE PUMP, IP55, 75 KW, 50 HZ, 415 V, S1, Ex n, M3GP 280SMB AV1, 6316/C3,6316/C3, VERTICAL IM3011, 1484 RPM, 3, DELTA, 127 AMP, CCW, F, II A T3, 665 KG, 400-PC-001 | VERTICAL MOTOR, ELECTRIC, BOOSTER PUMP 'B' FOR ALAIN MAIN LINE PUMP, IP55, 75 KW, 50 HZ, 415 V, S1 |  | MOTOR | M400P015B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP015B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 02/11/18 | ME-PM-014-M6
969130692 | M400MP017B | MOTOR,ELECTRIC, BOOSTER PUMP 'B' FOR JET-A1 ADIA PUMP, IP55, 75 KW, 50 HZ, 415 V, S1, Ex n AIIT3, 280SMB, 6316/C3,6316/C3, FOOT MOUNTED, 1484 RPM, 3, DELTA, 127 AMP, F, EEx n AIIT3, 665 KG, 400-PC-001, T3 | MOTOR,ELECTRICMOTOR,ELECTRIC, BOOSTER PUMP 'B' FOR JET-A1 PUMP |  | MOTOR | M400P017B | 2 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP017B-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/11/18 | ME-PM-014-M6
969130702 | M400MP020 | MOTOR,ELECTRIC, BOOSTER PUMP FOR SPEC.JET-A1 PUMP, IP55, 75 KW, 50 HZ, 415 V, S1, Ex n A II T3, 280SMB, 6316C3, FOOT MOUNTING, 1484 RPM, 3, DELTA, 127 AMP, F, II T3, 665 KG, 400-PC-001, T3, 70gm | MOTOR,ELECTRIC, BOOSTER PUMP FOR OFF SPEC.JET-A1 PUMP |  | MOTOR | M400P020 | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP020-ME1 | INACTIVE | ELEC | PM | EDS | 6 | MONTHS | 05/07/18 | ME-PM-014-M6
969130727 | M400VSD16ATR | TRANSFORMER,DISTRIBUTION, VSD TRANSFORMER, 2000KVA, DYN 11, 50 HZ, 3, 3300, 1800, 350 AMP, 321 AMP, 7.2/20/60 KV, 7.2/20/60 KV, 8 % | INPUT CONVERTER TRANSFORMER FOR VSD16A MOTOR |  | TRANSFMR | M400SCB | 3 | TRANSFMR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400VSD16ATR-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 15/09/18 | ME-PM-009-M6
FFF56583 | M50J104F | FIRE FIGHTING FOAM GENERATOR FOR T-104 | FIRE FIGHTING FOAM GENERATOR FOR T-104 |  | F_MIXR | M10T104 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56593 | M50J105A | FIRE FIGHTING FOAM GENERATOR FOR T-105 | FIRE FIGHTING FOAM GENERATOR FOR T-105 |  | F_MIXR | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56594 | M50J105B | FIRE FIGHTING FOAM GENERATOR FOR T-105 | FIRE FIGHTING FOAM GENERATOR FOR T-105 |  | F_MIXR | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56595 | M50J105C | FIRE FIGHTING FOAM GENERATOR FOR T-105 | FIRE FIGHTING FOAM GENERATOR FOR T-105 |  | F_MIXR | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56596 | M50J105D | FIRE FIGHTING FOAM GENERATOR FOR T-105 | FIRE FIGHTING FOAM GENERATOR FOR T-105 |  | F_MIXR | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56597 | M50J105E | FIRE FIGHTING FOAM GENERATOR FOR T-105 | FIRE FIGHTING FOAM GENERATOR FOR T-105 |  | F_MIXR | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56598 | M50J105F | FIRE FIGHTING FOAM GENERATOR FOR T-105 | FIRE FIGHTING FOAM GENERATOR FOR T-105 |  | F_MIXR | M10T105 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56610 | M60J106A | FIRE FIGHTING FOAM GENERATOR FOR T-106 | FIRE FIGHTING FOAM GENERATOR FOR T-106 |  |  | M10T106 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56611 | M60J106B | FIRE FIGHTING FOAM GENERATOR FOR T-106 | FIRE FIGHTING FOAM GENERATOR FOR T-106 |  |  | M10T106 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56612 | M60J106C | FIRE FIGHTING FOAM GENERATOR FOR T-106 | FIRE FIGHTING FOAM GENERATOR FOR T-106 |  |  | M10T106 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56613 | M60J106D | FIRE FIGHTING FOAM GENERATOR FOR T-106 | FIRE FIGHTING FOAM GENERATOR FOR T-106 |  |  | M10T106 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56614 | M60J106E | FIRE FIGHTING FOAM GENERATOR FOR T-106 | FIRE FIGHTING FOAM GENERATOR FOR T-106 |  |  | M10T106 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56628 | M50J107A | FIRE FIGHTING FOAM GENERATOR FOR T-107 | FIRE FIGHTING FOAM GENERATOR FOR T-107 |  | F_MIXR | M10T107 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56629 | M50J107B | FIRE FIGHTING FOAM GENERATOR FOR T-107 | FIRE FIGHTING FOAM GENERATOR FOR T-107 |  | F_MIXR | M10T107 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56630 | M50J107C | GENERATOR, FOAM | FIRE FIGHTING FOAM GENERATOR FOR T-107 |  | F_MIXR | M10T107 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56631 | M50J107D | FIRE FIGHTING FOAM GENERATOR FOR T-107 | FIRE FIGHTING FOAM GENERATOR FOR T-107 |  | F_MIXR | M10T107 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56632 | M50J107E | FIRE FIGHTING FOAM GENERATOR FOR T-107 | FIRE FIGHTING FOAM GENERATOR FOR T-107 |  | F_MIXR | M10T107 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56644 | M50J108 | FIRE FIGHTING FOAM GENERATOR FOR T-108 | FIRE FIGHTING FOAM GENERATOR FOR T-108 |  | F_MIXR | M10T108 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56655 | M50J109 | FIRE FIGHTING FOAM GENERATOR FOR T-109 | FIRE FIGHTING FOAM GENERATOR FOR T-109 |  | F_MIXR | M10T109 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFF56666 | M50J110 | FIRE FIGHTING FOAM GENERATOR FOR T-110 | FIRE FIGHTING FOAM GENERATOR FOR T-110 |  | F_MIXR | M10T110 | 1 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFP57532 | M50XMC006 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-103 |  | PB_HS-MC | M10T103 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC006-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 25/10/18 | MFPS-PM07.M3
FFP57537 | M50XMC011 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-104 |  | PB_HS-MC | M10T104 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC011-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 06/08/18 | MFPS-PM07.M3
FFP57538 | M50XMC012 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-104 |  | PB_HS-MC | M10T104 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC012-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 23/08/18 | MFPS-PM07.M3
FFP57539 | M50XMC003 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-102 |  | PB_HS-MC | M10T102 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC003-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 24/10/18 | MFPS-PM07.M3
FFP57540 | M50XMC005 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-103 |  | PB_HS-MC | M10T103 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC005-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 28/07/18 | MFPS-PM07.M3
969207867 | M410EXP002 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207869 | M410EXP004 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207870 | M410EXP005 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207877 | M410EXP013 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207882 | M410EXP018 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207871 | M410EXP006 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207872 | M410EXP007 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207873 | M410EXP008 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207875 | M410EXP011 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207874 | M410EXP009 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207876 | M410EXP012 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207880 | M410EXP016 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175152 | M410PDT451C | 410-L-014C JET A1 PRE-FILTER | 410-L-014C JET A1 PRE-FILTER |  | PRES_TX | M410L014C | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT451C-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/08/18 | MC-PM-PT1-M6
969175153 | M410PDT701A | 410-L-007A GAS OIL INTER-TANK TRANSFER BASKET FILTER | 410-L-007A GAS OIL INTER-TANK TRANSFER BASKET FILTER |  | PRES_TX | M410L007A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT701A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/08/18 | MC-PM-PT1-M6
969175154 | M410PDT701B | 410-L-007B GAS OIL INTER-TANK TRANSFER BASKET FILTER | 410-L-007B GAS OIL INTER-TANK TRANSFER BASKET FILTER |  | PRES_TX | M410L007B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT701B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/08/18 | MC-PM-PT1-M6
969175308 | M410PG257 | 410-P-014B SUCTION | 410-P-014B SUCTION |  | INDICATR | M410P014B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175309 | M410PG258 | 410-P-014B DISCHARGE | 410-P-014B DISCHARGE |  | INDICATR | M410P014B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175310 | M410PG450A | 410-L-004A | PG OF COL/FILT 410L004A |  | INDICATR | M410L004A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175311 | M410PG450B | 410-L-004B | PG OF COL/FILT 410L004B |  | INDICATR | M410L004B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175312 | M410PG450C | 410-L-004C | PG OF COL/FILT 410L004C |  | INDICATR | M410L004C | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175313 | M410PG720 | WATER SPRAY FOR 410-T-011FROM 410-RO-720 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-720 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175314 | M410PG721 | WATER SPRAY FOR 410-T-011FROM 410-RO-721 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-721 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175315 | M410PG722 | WATER SPRAY FOR 410-T-011FROM 410-RO-722 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-722 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175171 | M410PT018 | ANTI-STATIC CHEMICAL INJECTION TO 410-P-014A/B DISCHARGE | ANTI-STATIC CHEMICAL INJECTION TO 410-P-014A/B DISCHARGE |  | PRES_TX | M410P014A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT018-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/09/18 | MC-PM-PT1-M6
969175172 | M410PT201 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A SUCTION HEADER |  | PRES_TX | M410P007A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT201-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 02/10/18 | MC-PM-PT1-M6
969175173 | M410PT202 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A DISCHARGE HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A DISCHARGE HEADER |  | PRES_TX | M410P007A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT202-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 03/10/18 | MC-PM-PT1-M6
969175174 | M410PT204 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B SUCTION HEADER |  | PRES_TX | M410P007B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT204-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/10/18 | MC-PM-PT1-M6
969175175 | M410PT205 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B DISCHARGE HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B DISCHARGE HEADER |  | PRES_TX | M410P007B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT205-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/10/18 | MC-PM-PT1-M6
969175176 | M410PT207 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C SUCTION HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C SUCTION HEADER |  | PRES_TX | M410P007C | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT207-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/10/18 | MC-PM-PT1-M6
969175177 | M410PT208 | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C DISCHARGE HEADER | ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007C DISCHARGE HEADER |  | PRES_TX | M410P007C | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT208-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/10/18 | MC-PM-PT1-M6
969175178 | M410PT216 | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008A SUCTION HEADER | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008A SUCTION HEADER |  | PRES_TX | M410P008A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT216-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 16/10/18 | MC-PM-PT1-M6
969175179 | M410PT217 | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008A DISCHARGE HEADER | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008A DISCHARGE HEADER |  | PRES_TX | M410P008A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT217-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 17/10/18 | MC-PM-PT1-M6
969175180 | M410PT219 | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008B SUCTION HEADER | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008B SUCTION HEADER |  | PRES_TX | M410P008B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT219-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 18/10/18 | MC-PM-PT1-M6
969175181 | M410PT220 | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008B DISCHARGE HEADER | GAS OIL INTER-TANK TRANSFER PUMP 410-P-008B DISCHARGE HEADER |  | PRES_TX | M410P008B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT220-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 19/10/18 | MC-PM-PT1-M6
969175182 | M410PT251 | JET A1 INTER-TANK TRANSFER PUMP 410-P-014A SUCTION HEADER | JET A1 INTER-TANK TRANSFER PUMP 410-P-014A SUCTION HEADER |  | PRES_TX | M410P014A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT251-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 22/10/18 | MC-PM-PT1-M6
969175183 | M410PT254 | JET A1 INTER-TANK TRANSFER PUMP 410-P-014A DISCHARGE HEADER | JET A1 INTER-TANK TRANSFER PUMP 410-P-014A DISCHARGE HEADER |  | PRES_TX | M410P014A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT254-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 23/10/18 | MC-PM-PT1-M6
969175184 | M410PT256 | JET A1 INTER-TANK TRANSFER PUMP 410-P-014B SUCTION HEADER | JET A1 INTER-TANK TRANSFER PUMP 410-P-014B SUCTION HEADER |  | PRES_TX | M410P014B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT256-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 24/10/18 | MC-PM-PT1-M6
969175185 | M410PT259 | JET A1 INTER-TANK TRANSFER PUMP 410-P-014B DISCHARGE HEADER | JET A1 INTER-TANK TRANSFER PUMP 410-P-014B DISCHARGE HEADER |  | PRES_TX | M410P014B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT259-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 25/10/18 | MC-PM-PT1-M6
969175186 | M410PT260 | INSTRUMENT AIR HEADER | INSTRUMENT AIR HEADER |  | PRES_TX | M410PRESS | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT260-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 26/10/18 | MC-PM-PT1-M6
969175187 | M410PT357 | FROM FIRE WATER PUMP DISCHARGE HEADER TO FIRE WATER TANK | FROM FIRE WATER PUMP DISCHARGE HEADER TO FIRE WATER TANK |  | PRES_TX | M410FIRE | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT357-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 01/12/18 | MC-PM-PT1-M6
969175188 | M410RO150 | ULG/GAS OIL SUMP PUMP 410-P-009 DISCHARGE HEADER TO TANKER LOADING | ULG/GAS OIL SUMP PUMP 410-P-009 DISCHARGE HEADER TO TANKER LOADING |  | ORIFICE | M410P009 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175189 | M410RO151 | JET A1 SUMP PUMP 410-P-010 DISCHARGE HEADER TO TANKER LOADING | JET A1 SUMP PUMP 410-P-010 DISCHARGE HEADER TO TANKER LOADING |  | ORIFICE | M410P010 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175190 | M410RO720 | WATER SPRAY FOR 410-T-011FROM 410-STR-720 TO 410-PG-720 | WATER SPRAY FOR 410-T-011FROM 410-STR-720 TO 410-PG-720 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175191 | M410RO721 | WATER SPRAY FOR 410-T-011FROM 410-STR-721 TO 410-PG-721 | WATER SPRAY FOR 410-T-011FROM 410-STR-721 TO 410-PG-721 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175316 | M410PG723 | WATER SPRAY FOR 410-T-011FROM 410-RO-723 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-723 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175317 | M410PG724 | WATER SPRAY FOR 410-T-011FROM 410-RO-724 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-724 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175318 | M410PG725 | WATER SPRAY FOR 410-T-011FROM 410-RO-725 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-725 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175319 | M410PG726 | WATER SPRAY FOR 410-T-011FROM 410-RO-726 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-726 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175320 | M410PG727 | WATER SPRAY FOR 410-T-011FROM 410-RO-727 TO RISER PIPE | WATER SPRAY FOR 410-T-011FROM 410-RO-727 TO RISER PIPE |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175321 | M410PG728 | WATER SPRAY FOR 410-T-012FROM 410-RO-728 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-728 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175322 | M410PG729 | WATER SPRAY FOR 410-T-012FROM 410-RO-729 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-729 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175323 | M410PG730 | WATER SPRAY FOR 410-T-012FROM 410-RO-730 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-730 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175324 | M410PG731 | WATER SPRAY FOR 410-T-012FROM 410-RO-731 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-731 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175325 | M410PG732 | WATER SPRAY FOR 410-T-012FROM 410-RO-732 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-732 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175192 | M410RO722 | WATER SPRAY FOR 410-T-011FROM 410-STR-722 TO 410-PG-722 | WATER SPRAY FOR 410-T-011FROM 410-STR-722 TO 410-PG-722 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175326 | M410PG733 | WATER SPRAY FOR 410-T-012FROM 410-RO-733 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-733 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175327 | M410PG734 | WATER SPRAY FOR 410-T-012FROM 410-RO-734 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-734 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175328 | M410PG735 | WATER SPRAY FOR 410-T-012FROM 410-RO-735 TO RISER PIPE | WATER SPRAY FOR 410-T-012FROM 410-RO-735 TO RISER PIPE |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175329 | M410PG736 | WATER SPRAY FOR 410-T-013FROM 410-RO-736 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-736 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175330 | M410PG737 | WATER SPRAY FOR 410-T-013FROM 410-RO-737 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-737 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175331 | M410PG738 | WATER SPRAY FOR 410-T-013FROM 410-RO-738 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-738 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175332 | M410PG739 | WATER SPRAY FOR 410-T-013FROM 410-RO-739 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-739 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175333 | M410PG740 | WATER SPRAY FOR 410-T-013FROM 410-RO-740 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-740 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175334 | M410PG741 | WATER SPRAY FOR 410-T-013FROM 410-RO-741 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-741 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175335 | M410PG742 | WATER SPRAY FOR 410-T-013FROM 410-RO-742 TO RISER PIPE | WATER SPRAY FOR 410-T-013FROM 410-RO-742 TO RISER PIPE |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175193 | M410RO723 | WATER SPRAY FOR 410-T-011FROM 410-STR-723 TO 410-PG-723 | WATER SPRAY FOR 410-T-011FROM 410-STR-723 TO 410-PG-723 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175194 | M410RO724 | WATER SPRAY FOR 410-T-011FROM 410-STR-724 TO 410-PG-724 | WATER SPRAY FOR 410-T-011FROM 410-STR-724 TO 410-PG-724 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175195 | M410RO725 | WATER SPRAY FOR 410-T-011FROM 410-STR-725 TO 410-PG-725 | WATER SPRAY FOR 410-T-011FROM 410-STR-725 TO 410-PG-725 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175196 | M410RO726 | WATER SPRAY FOR 410-T-011FROM 410-STR-726 TO 410-PG-726 | WATER SPRAY FOR 410-T-011FROM 410-STR-726 TO 410-PG-726 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175197 | M410RO727 | WATER SPRAY FOR 410-T-011FROM 410-STR-727 TO 410-PG-727 | WATER SPRAY FOR 410-T-011FROM 410-STR-727 TO 410-PG-727 |  | ORIFICE | M410T011 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175198 | M410RO728 | WATER SPRAY FOR 410-T-012FROM 410-STR-728 TO 410-PG-728 | WATER SPRAY FOR 410-T-012FROM 410-STR-728 TO 410-PG-728 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175199 | M410RO729 | WATER SPRAY FOR 410-T-012FROM 410-STR-729 TO 410-PG-729 | WATER SPRAY FOR 410-T-012FROM 410-STR-729 TO 410-PG-729 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175200 | M410RO730 | WATER SPRAY FOR 410-T-012FROM 410-STR-730 TO 410-PG-730 | WATER SPRAY FOR 410-T-012FROM 410-STR-730 TO 410-PG-730 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175201 | M410RO731 | WATER SPRAY FOR 410-T-012FROM 410-STR-731 TO 410-PG-731 | WATER SPRAY FOR 410-T-012FROM 410-STR-731 TO 410-PG-731 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175202 | M410RO732 | WATER SPRAY FOR 410-T-012FROM 410-STR-732 TO 410-PG-732 | WATER SPRAY FOR 410-T-012FROM 410-STR-732 TO 410-PG-732 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175203 | M410RO733 | WATER SPRAY FOR 410-T-012FROM 410-STR-733 TO 410-PG-733 | WATER SPRAY FOR 410-T-012FROM 410-STR-733 TO 410-PG-733 |  | ORIFICE | M410T012 | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175515 | M410LS109 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS RACK ROOM NEAR RIM SEAL PANEL-SOUTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175516 | M410LS110 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SIS UPS ROOM-EAST SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175517 | M410LS111 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-TELECOM ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175518 | M410LS113 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-CONSOLE ROOM SOUTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175519 | M410LS114 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SCADA ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175520 | M410LS115 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-SCADA ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175521 | M410LS118 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-S/S BUILDING HVAC ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175522 | M410LS119 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR 400-VSD-016A ELECTRICAL PANEL NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175523 | M410LS120 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-NEAR 400-TMM-001B ELECTRICAL PANEL WEST SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175524 | M410LS128 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-TRUCK PARKING NEAR FIRE CONTROL ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175525 | M410LS129 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT FIRE STATION-TRAINING ROOM FIRST FLOOR |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175526 | M410LS130 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT TRUCK PARKING NEAR D.P FILLING |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175527 | M410LS133 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT RACK ROOM NEAR VESDA PANEL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175528 | M410LS134 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT RACK ROOM NEAR VESDA PANEL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175529 | M410LS135 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT RACK ROOM NEAR VESDA PANEL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175530 | M410LS138 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE BUILDING OLD ELECTRICAL SUPERVISOR OFFICE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175531 | M410LS139 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE BUILDING SOUTH SIDE WALL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175532 | M410LS140 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE BUILDING HALFWAY NEAR MECH TOOL ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175533 | M410LS143 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE SECTOR HALFWAY NEAR ELECTRICAL PANEL |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175534 | M410LS144 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE SECTOR HALFWAY NEAR MECHANICAL TOOL ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175535 | M410LS145 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-WAREHOUSE SECTOR HALFWAY NORTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175536 | M410LS148 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT LOBBY NEAR PIPELINE COORDINATOR ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175537 | M410LS149 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT LOBBY |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175538 | M410LS150 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT CONTROL ROOM SUPERVISOR |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175539 | M410LS151 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT ADMN BUILDING MAIN GATE ENTRY |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175540 | M410LS152 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT ADMN BUILDING MAIN GATE ENTRY |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175541 | M410LS155 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT ADMIN BUILDING IN LOBBY NEAR TOILET ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175542 | M410LS156 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT HVAC ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175543 | M410LS157 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT DOCUMENT ROOM-SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175544 | M410LS158 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT DOCUMENT ROOM-SOUTH SIDE |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175545 | M410LS159 | Loud Speaker with J/B-Indoor | LOUD SPEAKER WITH J/B-OUTDOOR-AT LOBBY NEAR ELECTRICAL ROOM |  | PA_SYS | M410TELM | 3 | PA_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175546 | M410CPS232901 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410TELM | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPS232901-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 06/12/18 | ME-PM-008-Y1
969365117 | M410XHD609B | LINEAR HEAT DETECTOR FOR TANK-003 | LINEAR HEAT DETECTOR FOR TANK-003 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365118 | M410XHD607A | LINEAR HEAT DETECTOR FOR TANK-004 | LINEAR HEAT DETECTOR FOR TANK-004 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365119 | M410XHD607B | LINEAR HEAT DETECTOR FOR TANK-004 | LINEAR HEAT DETECTOR FOR TANK-004 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365120 | M410XHD610A | LINEAR HEAT DETECTOR FOR TANK-005 | LINEAR HEAT DETECTOR FOR TANK-005 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365121 | M410XHD610B | LINEAR HEAT DETECTOR FOR TANK-005 | LINEAR HEAT DETECTOR FOR TANK-005 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365122 | M410XHD612A | LINEAR HEAT DETECTOR FOR TANK-006 | LINEAR HEAT DETECTOR FOR TANK-006 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365123 | M410XHD612B | LINEAR HEAT DETECTOR FOR TANK-006 | LINEAR HEAT DETECTOR FOR TANK-006 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365124 | M410XHD613A | LINEAR HEAT DETECTOR FOR TANK-007 | LINEAR HEAT DETECTOR FOR TANK-007 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365165 | M410XHD658A | LINEAR HEAT DETECTOR FOR PUMP-007B AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-007B AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365166 | M410XHD658B | LINEAR HEAT DETECTOR FOR PUMP-007B AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-007B AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365167 | M410XHD659A | LINEAR HEAT DETECTOR FOR PUMP-007C AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-007C AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365168 | M410XHD659B | LINEAR HEAT DETECTOR FOR PUMP-007C AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-007C AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365169 | M410XGH738A | H2 GAS DETECTORS-SIS HVAC ROOM-NORTH SIDE | H2 GAS DETECTORS-SIS HVAC ROOM-NORTH SIDE |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365170 | M410XGH738B | H2 GAS DETECTORS-SIS HVAC ROOM-SOUTH SIDE | H2 GAS DETECTORS-SIS HVAC ROOM-SOUTH SIDE |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365171 | M410XGH736 | H2 GAS DETECTORS IN IRP2-SIS BATTERY ROOM CEILING-EAST SIDE | H2 GAS DETECTORS IN IRP2-SIS BATTERY ROOM CEILING-EAST SIDE |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365172 | M410XGH737 | H2 GAS DETECTORS IN IRP2-SIS BATTERY ROOM CEILING-WEST SIDE | H2 GAS DETECTORS IN IRP2-SIS BATTERY ROOM CEILING-WEST SIDE |  | PB_HS-MC | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365173 | M410XGC648A | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-NORTH SIDE LEFT | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-NORTH SIDE LEFT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365174 | M410XGC648B | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-NORTH SIDE CENTRE | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-NORTH SIDE CENTRE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365175 | M410XGC648C | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-NORTH SIDE RIGHT | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-NORTH SIDE RIGHT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365176 | M410XGC649A | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-SOUTH SIDE RIGHT | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-SOUTH SIDE RIGHT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365177 | M410XGC649B | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-SOUTH SIDE CENTRE | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-SOUTH SIDE CENTRE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365178 | M410XGC649C | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-SOUTH SIDE LEFT | FLAMMABLE GAS DETECTORS-IRP-II SUB STATION-CORRIDOR-SOUTH SIDE LEFT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365179 | M410XGC828A | FLAMMABLE GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE LEFT | FLAMMABLE GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE LEFT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365180 | M410XGC828B | FLAMMABLGAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE CENTRE | FLAMMABLGAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE CENTRE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365181 | M410XGC828C | FLAMMABLE GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE RIGHT | FLAMMABLE GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE RIGHT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365182 | M410XGH814A | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-NORTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365183 | M410XGH814B | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-SOUTH SIDE | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-HVAC ROOM-SOUTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365184 | M410XGH812 | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-BATTERY ROOM CEILING-NORTH SIDE | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-BATTERY ROOM CEILING-NORTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M410XGH812-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 04/08/18 | MFPS-PM02.M3
969365185 | M410XGH813 | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-BATTERY ROOM CEILING-SOUTH SIDE | H2 GAS DETECTORS-IRP-II PLCR EXTENSION-BATTERY ROOM CEILING-SOUTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M410XGH813-MFPS | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 04/08/18 | MFPS-PM02.M3
969365186 | M410XGC650A | FLAMMABLE GASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-NORTH SIDE LEFT | FLAMMABLE GASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-NORTH SIDE LEFT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365187 | M410XGC650B | FLAMMABLGASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-NORTH SIDE CENTRE | FLAMMABLGASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-NORTH SIDE CENTRE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365188 | M410XGC650C | FLAMMABLGASS DETECTORS-IRP-II SUBSTATION-HVAC ROOMNORTH SIDE RIGHT | FLAMMABLGASS DETECTORS-IRP-II SUBSTATION-HVAC ROOMNORTH SIDE RIGHT |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365189 | M410XGH653A | H2 GASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-NORTH SIDE | H2 GASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-NORTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365190 | M410XGH653B | H2 GASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-SOUTH SIDE | H2 GASS DETECTORS-IRP-II SUBSTATION-HVAC ROOM-SOUTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365191 | M410XGH651 | H2 GAS DETECTORS-IRP-II SUBSTATION-BATTERY ROOM CEILING-SOUTH SIDE | H2 GAS DETECTORS-IRP-II SUBSTATION-BATTERY ROOM CEILING-SOUTH SIDE |  | PB_HS-MC | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512485 | A-MSFH-AHMED | Lenovo PC | Tasnim Kittaneh |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512487 | A-MSFH-NAJOUD | HP Prodesk 600 G1 | NAJOUD KHAMIS AL MANSOORI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512479 | SDSECURITY | HP PRODESK 600 G1 | SDSECURITY |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512482 | A-MSFH-KHALIFA | Dell Optiplex 9020 | KHALIFA ABDUL HAMEED AL KURDI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512483 | A-MSFH-HAMED | Dell Optiplex 9020 | Training PC |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512486 | SDAFU | HP Prodesk 600 G1 | Anwar Ibrahim |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512488 | A-MSFH-IBRAHIM | Dell Optiplex 9020 | Ibrahim Omer Redwan |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512489 | SD-PT-IOR8161 | HP PRODESK 600 G3 | Ibrahim Omer Redwan |  |  | P&T_NEW_ADMIN | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | d
969512490 | SDNIYAS | Dell Optiplex 9020 | NIYAS AHMED JEGABBER ALI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512491 | SCDENETWORK | Dell Optiplex 9020 | Mohammed Thaupeek |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512492 | SDDIMITRIOS | HP Prodesk 600 G1 | DIMITRIOS PANAPAKKIDS |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512496 | A-ROMAITHI-D21 | HP Prodesk 600 G1 | MOHAMMED ALI AL ROMAITHI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512498 | A-MSFH-ICCSP2 | HP Prodesk 60 G1 | ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512729 | A-TAS-A3 | Lenovo - M7491 | IBM LENOVO |  |  | P&T_SECURITY | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147433 | M410L007A | GAS OIL INTER-TANK TRANSFER BASKET FILTERS | GAS OIL INTER-TANK TRANSFER BASKET FILTERS |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147434 | M410L007B | GAS OIL INTER-TANK TRANSFER BASKET FILTERS | GAS OIL INTER-TANK TRANSFER BASKET FILTERS |  | VESSEL | M410FILTER | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 10 | 50 | 10 | 5 | 8.3979 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147435 | M410T031A | DIESEL DAY TANK (FIREWATER PUMP) | DIESEL DAY TANK (FIREWATER PUMP) |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 |  | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147436 | M410T031B | DIESEL DAY TANK (FIREWATER PUMP) | DIESEL DAY TANK (FIREWATER PUMP) |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147459 | M410ME003 | ANTI-STATIC CHEMICALINJECTION PACKAGE | ANTI-STATIC CHEMICALINJECTION PACKAGE |  | PACKAGE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147460 | M410P018A | ANTI-STATIC NEAT CHEMICALINJECTION PUMP | ITT ANTI-STATIC CHEMICAL INJECTION PUMP OF 410ME003 |  | PURE | M410ME003 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P018A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-8-Y1
969147461 | M410P018B | ANTI-STATIC NEAT CHEMICALINJECTION PUMP | ITT ANTI-STATIC NEAT CHEMICAL INJECTION PUMP 410ME003 |  | PURE | M410ME003 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 5 | 6 | m | 0 | N | N | 0 | 0 | 0 | M410P018B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-8-Y1
969147462 | M410P019A | ANTI-STATIC CHEMICAL DILUTION PUMP | ITT ANTI-STATIC CHEMICAL DILUTION PUMP(CONTINUOUS) 410ME003 |  | PURE | M410ME003 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P019A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-8-Y1
969147463 | M410P019B | ANTI-STATIC CHEMICAL DILUTION PUMP | ITT ANTI-STATIC CHEMICAL DILUTION PUMP 410ME003 |  | PURE | M410ME003 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P019B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 07/10/18 | MM-PM-8-Y1
969147464 | M410P025 | DHAFRA ANTI-STATIC CHEMICAL PNEUMATIC PUMP | DHAFRA ANTI-STATIC FILLING PNEUMATIC PUMP 410ME002. |  | PURE | M410ME002 | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P025-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/11/18 | MM-PM-8-Y1
969147465 | M410T021 | ANTI-STATIC NEAT CHEMICALSTORAGE TANK | ANTI-STATIC NEAT CHEMICALSTORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Non Critical | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205033 | M410P033B | FIRE WATER PUMP- MOTOR | JOCKEY PUMP ELECTRIC MOTOR DRIVEN | 969147476 | MOTOR | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | e | 0 | Y | Y | 0 | 0 | 0 | M410P033B-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 28/11/18 | MC-PM-02-M6
969205034 | M410P031A | Pressure Gauge Discharge water Pump | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | 969147466 | INDICATR | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | Non Critical | N | 1 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P031A-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969147412 | M410T001 | ULG 91 STORAGE TANK | ULG 91 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147413 | M410T002 | ULG 91 STORAGE TANK | ULG 91 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147414 | M410T003 | ULG 91 STORAGE TANK | ULG 91 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147437 | M410T031C | DIESEL DAY TANK (FIREWATER PUMP) | DIESEL DAY TANK (FIREWATER PUMP) |  | VESSEL | M410VESSEL | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 10 | 5 | 10 | 5 | 4.7959 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205035 | M410P031A | Pressure Gauge Suction water pump | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | 969147466 | INDICATR | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | Non Critical | N | 1 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P031A-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969205036 | M410P033A | Pressure Gauge Discharge water Pump | JOCKEY PUMP ELECTRIC MOTOR DRIVEN | 969147475 | INDICATR | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | Non Critical | N | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P033A-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 25/11/18 | MC-PM-02-M6
969205037 | M410P033A | Pressure Gauge Suction water pump | JOCKEY PUMP ELECTRIC MOTOR DRIVEN | 969147475 | INDICATR | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | Non Critical | N | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P033A-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 25/11/18 | MC-PM-02-M6
969205039 | M410P031A | PRESSURE SAFETY VALVE | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | 969147466 | PSV | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 1 | 12 | i | 0 | Y | Y | 0 | 0 | 0 | M410P031A-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
938780 | M400WOV831 | DELUGE VALVE | M/L Pumps Deluge Valve |  |  | M400VALVE | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938787 | M400WOV832 | DELUGE VALVE | M/L Pumps Deluge Valve |  |  | M400VALVE | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938788 | M400WOV833 | DELUGE VALVE | M/L Pumps Deluge Valve |  |  | M400VALVE | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938789 | M400WOV834 | DELUGE VALVE | Booster Pumps Deluge Valve |  |  | M400VALVE | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938790 | M400WOV835 | DELUGE VALVE | Booster Pumps Deluge Valve |  |  | M400VALVE | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147477 | M410P034 | FRESH WATER MAKE-UP CENTRIFUGAL PUMP (FIRE TANKS) | FRESH WATER MAKE-UP PUMP (FIRE TANKS) |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P034-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 08/08/18 | MM-PM-3-Y1
969147445 | M410T054 | FRESH WATER STORAGE TANK | FRESH WATER STORAGE TANK |  | VESSEL | M410FIRE | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 5 | 50 | 10 | 5 | 6.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59178 | M10LIA081 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 108 ON DCS | TNK56634 | TANKGAUG | M10T108 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59179 | M10LI081 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-108 | IIL59178 | TANKGAUG | M10LIA081 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59195 | M10LIT091 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-109 | IIL59198 | TANKGAUG | M10LIA091 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT091-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/09/18 | MC-PM067.M6
IIL59196 | M10LI091 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-109 | IIL59198 | TANKGAUG | M10LIA091 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59198 | M10LIA091 | LOOP, LEVEL INDICATOR INSTRUMENT | LEVEL INDICATOR OF T109 ON DCS | TNK56645 | TANKGAUG | M10T109 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59212 | M10LIT101 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | ENRAF LEVEL INDICATOR(SERVO) FOR TANK T-110 | IIL59213 | TANKGAUG | M10LIA101 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M10LIT101-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/09/18 | MC-PM067.M6
IIL59213 | M10LIA101 | LOOP LEVEL INDICATOR INSTRUMENT | LEVEL INDICATION OF TANK 110 ON DCS | TNK56656 | TANKGAUG | M10T110 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59214 | M10LI101 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , M20 X 1.5 | DIGITAL FIELD INDICATOR FOR TANK T-110 | IIL59213 | TANKGAUG | M10LIA101 | 2 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIL59250 | M40LT721 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , 4" 150 LB | LEVEL TRANSMITTER FOR SLOPS LOADING PUMP 172 ADNOC DIST. | PMC56668 | LVL_TX | M40P172 | 2 | LVL_TX | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M40LT721-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 29/05/19 | MC-PM-004-Y1
IIL59253 | M40LT731 | TRANSMITTER, LIQUID LEVEL, DISPLACEMENT , 0 - 100 perc. mm , 4-20MA , 24VDC , 4" | LEVEL TRANSMITTER FOR SLOPS LOADING PUMP 173 ADNOC DIST. | PMC56670 | LVL_TX | M40P173 | 2 | LVL_TX | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | c | 0 | N | N | 0 | 0 | 0 | M40LT731-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 31/05/19 | MC-PM-004-Y1
969281992 | PL318CCTVP004 | CCTV CABINET - MUSS.–AL AIN PL - KP 100+926.760 | CCTV CABINET - MUSS.–AL AIN PL - KP 100+926.760 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281993 | PL318CCTVP005 | CCTV CABINET - MUSS.–AL AIN PL - KP 136+931.00 | CCTV CABINET - MUSS.–AL AIN PL - KP 136+931.00 |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281994 | PL100CCTVP001 | CCTV CABINET | CCTV CABINET Shweihat Terminal |  | BLDGS | PL300CCTV | 3 | CCTVSEC | 616101-310600 | SHWEIHAT TERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935530 | SALAINTP75 |  | TEST POINT # 75 (C.P.STATION-3 AT KM 84.5) |  |  | SALAINCPS3 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935531 | SALAINTP76 |  | TEST POINT # 76 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935532 | SALAINTP77 |  | TEST POINT # 77 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935549 | SALAINTP91 |  | TEST POINT # 91 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935550 | SALAINTP92 |  | TEST POINT # 92 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935551 | SALAINTP93 |  | TEST POINT # 93 (C.P.STATION-4 AT KM 149) |  |  | SALAINCPS4 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935450 | SALAINTP5 |  | TEST POINT # 5 (C.P. STATION 1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935451 | SALAINTP6 |  | TEST POINT # 6 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XXX935452 | SALAINTP7 |  | TEST POINT # 7 (C.P. STATION-1 AT KM 3.8) |  |  | SALAINCPS1 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132689 | UNISSAN13078 | 13078 NISSAN PATROL (MAINT. PIPELINE) | NISSAN PATROL 13078 (MAINT. PIPELINE) |  |  | MREDUNDANT | 4 | 0 | 648701-610920 | MTERMINAL | DECOMMISSIONED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UNISSAN13078-UHE | INACTIVE | MECH | PM | EDS | 1 | MONTHS | 05/07/18 | MM-PM-029-M1
969132690 | UNISSAN10861 | 10861 NISSAN PATROL ( MANAGER MSPD) | NISSAN PATROL 10861 ( MANAGER MSPD) |  |  | MREDUNDANT | 4 | 0 | 648701-610920 | MTERMINAL | DECOMMISSIONED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UNISSAN10861-UHE | INACTIVE | MECH | PM | EDS | 1 | MONTHS | 05/07/18 | MM-PM-029-M1
969130669 | M400MP015A | MOTOR,ELECTRIC, BOOSTER PUMP 'A' FOR ALAIN MAIN LINE PUMP, IP55, 75 KW, 50 HZ, 415 V, S1, Exn IIT3, M3GP 280SMB AV1, 6316/C3,6316/C3, VERTICAL, 1484 RPM, 3, DELTA, 127 AMP, F, II T3, 665 KG, 400-PCC-001, T3 | VERTICAL MOTOR, ELECTRIC, BOOSTER PUMP 'A' FOR ALAIN MAIN LINE PUMP, 75 KW KW, 50 HZ, 415 V |  | MOTOR | M400P015A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | M400MP015A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 01/10/18 | ME-PM-014-M6
969130689 | M400MP017A | MOTOR,ELECTRIC, BOOSTER PUMP 'A' FOR JET-A1 ADIA PUMP, IP55, 75 KW, 50 HZ, 415 V, S1, Ex n, 280SMB, 6316C3/6316C3, FOOT MOUNTING IM1001, 1484 RPM, 3, DELTA, 127 AMP, F, II T3, 665 KG, 400-PC-001, T3 | MOTOR,ELECTRIC, BOOSTER PUMP 'A' FOR JET-A1 PUMP |  | MOTOR | M400P017A | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MP017A-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 06/10/18 | ME-PM-014-M6
969353387 | PL315EOV31613 | HCU FOR THE ELECTRO HYDRAULIC VALVE | ELECTRO HYDRAULIC VALVE, SVSTATION-13 | 969275359 | PACKAGE | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935369 | SADIAVS1V1 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE 10" AT VALVE STATION # 1 AT KM 1.75 |  | VALVE | SADIAVS1 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935370 | SADIAVS2V1 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE 10" AT VALVE STATION # 2 AT KM 2.5 |  | VALVE | SADIAVS2 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935371 | SMVS1V1 | VALVE, GLOBE, 12" , HANDWHEEL | VALVE 12" AT VALVE STAT. # 1 AT KM 0.8 (MULTI PRODUCT) |  | VALVE | SMVS1 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935372 | SMVS2V1 | VALVE, GLOBE, 12" , HANDWHEEL | VALVE 12" AT VALVE STAT. # 2 AT KM 1.8 (MULTI PRODUCT) |  | VALVE | SMVS2 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935373 | SMVS3V1 | VALVE, GLOBE, 12" , HANDWHEEL | VALVE 12" AT VALVE STAT. #3 AT KM 12 (MULTI PRODUCT) |  | VALVE | SMVS3 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935374 | SMLPGVS1V1 | VALVE, GLOBE, 8" , HANDWHEEL | LPG VALVE 8" AT VALVE STAT. #1 AT KM 0.8 |  | VALVE | SMLPGVS1 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935375 | SMLPGVS2V1 | VALVE, GLOBE, 8" , HANDWHEEL | LPG VALVE 8" AT VALVE STAT. #2 AT KM 1.8 |  | VALVE | SMLPGVS2 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935376 | SMLPGVS3V1 | VALVE, GLOBE, 8" , HANDWHEEL | LPG VALVE 8" AT VALVE STAT. # 3 AT KM 12 |  | VALVE | SMLPGVS3 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935386 | SALAINVS1V1 | VALVE, GLOBE, 10" , HANDWHEEL | MQTAA_ALAIN VALVE 10'' AT VALVE STATN # 1 AT 2 KM. |  | VALVE | SALAINVS1 | 3 | VALVE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935414 | SALAINVS2V1 | VALVE, GLOBE, 10" , HANDWHEEL | MQTAA_ALAIN VALVE STATION # 2 AT KM 27.5 |  | VALVE | SALAINVS2 | 3 | VALVE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935415 | SALAINVS3V1 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE 10'' AT VALVE STATION # 3 AT KM 48.5 |  | VALVE | SALAINVS3 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935416 | SALAINVS4V1 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE AT VALVE STATION # 4 AT KM 75 |  | VALVE | SALAINVS4 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935417 | SALAINVS4V2 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE AT VALVE STATION # 4 AT KM 75 |  | VALVE | SALAINVS4 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935418 | SALAINVS4V3 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE AT VALVE STATION # 4 AT KM 75 |  | VALVE | SALAINVS4 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935419 | SALAINVS5V1 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE 10'' AT VALVE STATION # 5 AT KM 85.9 |  | VALVE | SALAINVS5 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVC935421 | SALAINVS6V1 | VALVE, GLOBE, 10" , HANDWHEEL | VALVE 10'' AT VALVE STATION # 6 AT KM 125.2 |  | VALVE | SALAINVS6 | 3 | VALVE | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175919 | M410LT013A | SAAB ROSEMOUNT ULG 91 TANK 410-T-001 | SAAB ROSEMOUNT ULG 91 TANK 410-T-001 |  | LVL_TX | M410T001 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175920 | M410LT013B | ULG 91 TANK 410-T-001 | SAAB ROSEMOUNT ULG 91 TANK 410-T-001 |  | LVL_TX | M410T001 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE11252 | M41SV601 | VALVE, SOLENOID, 1/2" , 110VDC , THD , 316 SS , 3/2-WAY , NC , 0-10 BAR , EExd I | OUTLET SOLENOID ESD VALVE FOR TANK T-110. | ISD59223 | SOL_VLV | M41ESD601 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVE11253 | M41SV541 | VALVE, SOLENOID, 1/2" , 110VDC , THD , 316 SS , 3/2-WAY , NC , 0-10 BAR , EExd I | SOLENOID ESD VALVE FOR MULTIPRODUCT INLET METERING | ISD59015 | SOL_VLV | M41ESD541 | 1 | SOL_VLV | 616101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969165723 | M410MP014A | JET A1 INTER-TANK TRANSFER PUMP MOTOR | JET A1 INTER-TANK TRANSFER PUMP MOTOR |  | MOTOR | M410P014A | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP014A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-HT1-6M
969165724 | M410MP014B | JET A1 INTER-TANK TRANSFER PUMP MOTOR | JET A1 INTER-TANK TRANSFER PUMP MOTOR |  | MOTOR | M410P014B | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP014B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-HT1-6M
969165725 | M410MP009 | ULG/GAS OIL SUMP PUMP MOTOR | ULG/GAS OIL SUMP PUMP MOTOR |  | MOTOR | M410P009 | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP009-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-LT1-6M
969165726 | M410MP010 | JET A1 SUMP PUMP MOTOR | JET A1 SUMP PUMP MOTOR |  | MOTOR | M410P010 | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP010-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/11/18 | ME-PM-LT1-6M
969147415 | M410T004 | ULG 91 STORAGE TANK | ULG 91 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147416 | M410T005 | ULG 95 STORAGE TANK | ULG 95 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147417 | M410T006 | ULG 95 STORAGE TANK | ULG 95 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147418 | M410T007 | ULG 95 STORAGE TANK | ULG 95 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147419 | M410T008 | ULG 95 STORAGE TANK | ULG 95 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147420 | M410T009 | GAS OIL STORAGE TANK | GAS OIL STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278618 | PL312CCTV046 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278619 | PL312CCTV047 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278620 | PL312CCTV048 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278621 | PL312CCTV049 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278622 | PL312CCTV050 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278623 | PL312CCTV051 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278624 | PL312CCTV052 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278625 | PL312CCTV053 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278626 | PL312CCTV054 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278627 | PL312CCTV055 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278628 | PL312CCTV056 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278629 | PL312CCTV057 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278630 | PL312CCTV058 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278631 | PL312CCTV059 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278632 | PL312CCTV060 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278633 | PL312CCTV061 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278634 | PL312CCTV062 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278635 | PL312CCTV063 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278636 | PL312CCTV064 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278637 | PL312CCTV065 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278638 | PL312CCTV066 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278639 | PL312CCTV067 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278640 | PL312CCTV068 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278641 | PL312CCTV069 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278642 | PL312CCTV070 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278643 | PL312CCTV071 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278644 | PL312CCTV072 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278645 | PL312CCTV073 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278646 | PL312CCTV074 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278647 | PL312CCTV075 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278648 | PL312CCTV076 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278649 | PL312CCTV077 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278650 | PL312CCTV078 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278651 | PL312CCTV079 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278652 | PL312CCTV080 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278653 | PL312CCTV081 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278654 | PL312CCTV082 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278655 | PL312CCTV083 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278656 | PL312CCTV084 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278657 | PL312CCTV085 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278658 | PL312CCTV086 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278659 | PL312CCTV087 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278660 | PL312CCTV088 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278661 | PL312CCTV089 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278662 | PL312CCTV090 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278663 | PL312CCTV091 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278664 | PL312CCTV092 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278665 | PL312CCTV093 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278666 | PL312CCTV094 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278667 | PL312CCTV095 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278668 | PL312CCTV096 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278669 | PL312CCTV097 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278670 | PL312CCTV098 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278671 | PL312CCTV099 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278672 | PL312CCTV100 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278673 | PL312CCTV101 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278674 | PL312CCTV102 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278675 | PL312CCTV103 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278676 | PL312CCTV104 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278677 | PL312CCTV105 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278678 | PL312CCTV106 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278679 | PL312CCTV107 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278680 | PL312CCTV108 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278681 | PL312CCTV109 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278682 | PL312CCTV110 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278683 | PL312CCTV111 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969253229 | M410FU116 | FOAM SKID | FOAM SKID |  |  | M410MISC | 1 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Non Critical | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935270 | M10NRVO-102 | OUTLET NON-RETURN VALVE - 16" | OUTLET NON-RETURN VALVE - 16" FOR TANK T-102 |  | VALCH | M10T102 | 3 | VALCH | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935267 | M10NRVI-104 | INLET NON-RETURN VALVE - 10" | INLET NON-RETURN VALVE - 10" FOR TANK T - 104 |  | VALCH | M10T104 | 3 | VALCH | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS935268 | M10OGV-101 | OUTLET GATE VALVE - 16" | OUTLET GATE VALVE - 16" FOR TANK T - 101 |  | VALVE | M10T101 | 3 | VALVE | 617101-310600 | MTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270443 | M410PT425 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410PLR005 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT425-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969516420 | PL312GDH612 | FLAMMABLE GAS DETECTOR AT SV STATION-6 | FLAMMABLE GAS DETECTOR AT SV STATION-6 |  | FG_DET | PL312SV6 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516421 | PL312XAC113 | MANUAL CALL POINT AT SV STATION - 1 | MANUAL CALL POINT AT SV STATION - 1 |  | PA_SYS | PL312SV1 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516422 | PL312XAC114 | MANUAL CALL POINT AT SV STATION - 1 | MANUAL CALL POINT AT SV STATION - 1 |  | PA_SYS | PL312SV1 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516423 | PL312XAC115 | MANUAL ALARM CALL POINT AT SV STATION - 1 | MANUAL ALARM CALL POINT AT SV STATION - 1 |  | PA_SYS | PL312SV1 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516559 | M400XAC024 | MANUAL CALL POINT AT CORRIDOR WWTP | MANUAL CALL POINT AT CORRIDOR WWTP |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516560 | M400XAC025 | MANUAL CALL POINT AT RACK ROOM WWTP | MANUAL CALL POINT AT RACK ROOM WWTP |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516561 | M400XAC027 | MANUAL CALL POINT AT CHEMICAL ROOM WWTP | MANUAL CALL POINT AT CHEMICAL ROOM WWTP |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516562 | M400XAC028 | MANUAL CALL POINT AT STORE ROOM WWTP | MANUAL CALL POINT AT STORE ROOM WWTP |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516563 | M400XAC300 | MANUAL CALL POINT AT New Admin Building, Corridor Ground Floor | MANUAL CALL POINT AT New Admin Building, Corridor Ground Floor |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516564 | M400XAC301 | MANUAL CALL POINT AT New Admin Building,Corridor Ground Floor | MANUAL CALL POINT AT New Admin Building,Corridor Ground Floor |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516565 | M400XAC302 | MANUAL CALL POINT AT New Admin Building,Corridor Ground Floor | MANUAL CALL POINT AT New Admin Building,Corridor Ground Floor |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516566 | M400XAC303 | MANUAL CALL POINT AT New Admin Building,Corridor Ground Floor | MANUAL CALL POINT AT New Admin Building,Corridor Ground Floor |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516567 | M400XAC304 | MANUAL CALL POINT AT New Admin Building,Corridor Ist Floor | MANUAL CALL POINT AT New Admin Building,Corridor Ist Floor |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516568 | M400XAC305 | MANUAL CALL POINT AT New Admin Building,Corridor Ist Floor | MANUAL CALL POINT AT New Admin Building,Corridor Ist Floor |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516569 | M400XAC306 | MANUAL CALL POINT AT New Admin Building, First Floor | MANUAL CALL POINT AT New Admin Building, First Floor |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516424 | PL312XAC116 | MANUAL ALARM CALL POINT AT SV STATION - 1 | MANUAL ALARM CALL POINT AT SV STATION - 1 |  | PA_SYS | PL312SV1 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516570 | M400XAC307 | MANUAL CALL POINT AT 2nd Floor Corridor New Admin Building | MANUAL CALL POINT AT 2nd Floor Corridor New Admin Building |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516571 | M400XAC308 | MANUAL CALL POINT AT 2nd Floor Corridor New Admin Building | MANUAL CALL POINT AT 2nd Floor Corridor New Admin Building |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516572 | M400XAC309 | MANUAL CALL POINT AT 2nd Floor Corridor New Admin Building | MANUAL CALL POINT AT 2nd Floor Corridor New Admin Building |  | PA_SYS | M400FAGP006 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516573 | M400XGC300 | FLAMMABLE GAS DETECTOR AT LOWER ROOF ADMIN BUILDING | FLAMMABLE GAS DETECTOR AT LOWER ROOF ADMIN BUILDING |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516574 | M400XGC301 | FLAMMABLE GAS DETECTOR AT LOWER ROOF ADMIN BUILDING | FLAMMABLE GAS DETECTOR AT LOWER ROOF ADMIN BUILDING |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516575 | M400XGC303 | FLAMMABLE GAS DETECTOR AT LOWER ROOF ADMIN BUILDING | FLAMMABLE GAS DETECTOR AT LOWER ROOF ADMIN BUILDING |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516576 | M400XGH300 | HYDROGEN GAS DETECTOR AT BATTERY ROOM GROUND FLOOR | HYDROGEN GAS DETECTOR AT BATTERY ROOM GROUND FLOOR |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516577 | M400XGT300 | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516578 | M400XGT301 | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516579 | M400XGT302 | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516580 | M400XGT303 | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING | H2S Gas Detector AT LOWER ROOF ADMIN BUILDING |  | FG_DET | M400FAGP006 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516425 | PL312XAC213 | MANUAL CALL POINT AT SV STATION - 2 | MANUAL CALL POINT AT SV STATION - 2 |  | PA_SYS | PL312SV2 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516426 | PL312XAC214 | MANUAL CALL POINT AT SV STATION - 2 | MANUAL CALL POINT AT SV STATION - 2 |  | PA_SYS | PL312SV2 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516427 | PL312XAC215 | MANUAL ALARM CALL POINT AT SV STATION - 2 | MANUAL ALARM CALL POINT AT SV STATION - 2 |  | PA_SYS | PL312SV2 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516428 | PL312XAC216 | MANUAL ALARM CALL POINT AT SV STATION - 2 | MANUAL ALARM CALL POINT AT SV STATION - 2 |  | PA_SYS | PL312SV2 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516429 | PL312XAC313 | MANUAL CALL POINT AT SV STATION - 3 | MANUAL CALL POINT AT SV STATION - 3 |  | PA_SYS | PL312SV3 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516430 | PL312XAC314 | MANUAL CALL POINT AT SV STATION - 3 | MANUAL CALL POINT AT SV STATION - 3 |  | PA_SYS | PL312SV3 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516431 | PL312XAC315 | MANUAL ALARM CALL POINT AT SV STATION - 3 | MANUAL ALARM CALL POINT AT SV STATION - 3 |  | PA_SYS | PL312SV3 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516432 | PL312XAC316 | MANUAL ALARM CALL POINT AT SV STATION - 3 | MANUAL ALARM CALL POINT AT SV STATION - 3 |  | PA_SYS | PL312SV3 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516433 | PL312XAC401 | MANUAL CALL POINT AT SV STATION - 4 | MANUAL CALL POINT AT SV STATION - 4 |  | PA_SYS | PL312SV4 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516434 | PL312XAC402 | MANUAL CALL POINT AT SV STATION - 4 | MANUAL CALL POINT AT SV STATION - 4 |  | PA_SYS | PL312SV4 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516435 | PL312XAC403 | MANUAL CALL POINT AT SV STATION - 4 | MANUAL CALL POINT AT SV STATION - 4 |  | PA_SYS | PL312SV4 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516436 | PL312XAC404 | MANUAL ALARM CALL POINT AT SV STATION - 4 | MANUAL ALARM CALL POINT AT SV STATION - 4 |  | PA_SYS | PL312SV4 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516437 | PL312XAC405 | MANUAL ALARM CALL POINT AT SV STATION - 4 | MANUAL ALARM CALL POINT AT SV STATION - 4 |  | PA_SYS | PL312SV4 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516438 | PL312XAC513 | MANUAL CALL POINT AT SV STATION - 5 | MANUAL CALL POINT AT SV STATION - 5 |  | PA_SYS | PL312SV5 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516439 | PL312XAC514 | MANUAL CALL POINT AT SV STATION - 5 | MANUAL CALL POINT AT SV STATION - 5 |  | PA_SYS | PL312SV5 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516440 | PL312XAC515 | MANUAL ALARM CALL POINT AT SV STATION - 5 | MANUAL ALARM CALL POINT AT SV STATION - 5 |  | PA_SYS | PL312SV5 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516441 | PL312XAC516 | MANUAL ALARM CALL POINT AT SV STATION - 5 | MANUAL ALARM CALL POINT AT SV STATION - 5 |  | PA_SYS | PL312SV5 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516442 | PL312XAC613 | MANUAL CALL POINT AT SV STATION - 6 | MANUAL CALL POINT AT SV STATION - 6 |  | PA_SYS | PL312SV6 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516443 | PL312XAC614 | MANUAL CALL POINT AT SV STATION - 6 | MANUAL CALL POINT AT SV STATION - 6 |  | PA_SYS | PL312SV6 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516444 | PL312XAC615 | MANUAL ALARM CALL POINT AT SV STATION - 6 | MANUAL ALARM CALL POINT AT SV STATION - 6 |  | PA_SYS | PL312SV6 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516445 | PL312XAC616 | MANUAL ALARM CALL POINT AT SV STATION - 6 | MANUAL ALARM CALL POINT AT SV STATION - 6 |  | PA_SYS | PL312SV6 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516446 | PL312XGH201 | HYDROGEN GAS DETECTOR AT SV STATION-2 | HYDROGEN GAS DETECTOR AT SV STATION-2 |  | FG_DET | PL312SV2 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516447 | PL312XGH301 | HYDROGEN GAS DETECTOR AT SV STATION-3 | HYDROGEN GAS DETECTOR AT SV STATION-3 |  | FG_DET | PL312SV3 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516448 | PL312XGH401 | HYDROGEN GAS DETECTOR AT SV STATION-4 | HYDROGEN GAS DETECTOR AT SV STATION-4 |  | FG_DET | PL312SV4 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516449 | PL312XGH501 | HYDROGEN GAS DETECTOR AT SV STATION-5 | HYDROGEN GAS DETECTOR AT SV STATION-5 |  | FG_DET | PL312SV5 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516450 | PL312XGH601 | HYDROGEN GAS DETECTOR AT SV STATION-6 | HYDROGEN GAS DETECTOR AT SV STATION-6 |  | FG_DET | PL312SV6 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516451 | PL312XHE217 | HEAT DETECTOR AT SV Station-2 | HEAT DETECTOR AT SV Station-2 |  | FGBHFD | PL312SV2 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516452 | PL312XHE301 | HEAT DETECTOR AT SV Station-3 | HEAT DETECTOR AT SV Station-3 |  | FGBHFD | PL312SV3 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516453 | PL312XHE401 | HEAT DETECTOR AT SV Station-4 | HEAT DETECTOR AT SV Station-4 |  | FGBHFD | PL312SV4 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516454 | PL312XHE517 | HEAT DETECTOR AT SV STATION-5 | HEAT DETECTOR AT SV STATION-5 |  | FGBHFD | PL312SV5 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516455 | PL312XHE617 | HEAT DETECTOR AT SV STATION-6 | HEAT DETECTOR AT SV STATION-6 |  | FGBHFD | PL312SV6 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516456 | PL312XSP216 | SMOKE DETECTOR AT SV Station-2 | SMOKE DETECTOR AT SV Station-2 |  | FGBHFD | PL312SV2 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516457 | PL312XSP316 | SMOKE DETECTOR AT SV Station-3 | SMOKE DETECTOR AT SV Station-3 |  | FGBHFD | PL312SV3 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516458 | PL312XSP401 | SMOKE DETECTOR AT SV Station-4 | SMOKE DETECTOR AT SV Station-4 |  | FGBHFD | PL312SV4 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516459 | PL312XSP516 | SMOKE DETECTOR AT SV STATION-5 | SMOKE DETECTOR AT SV STATION-5 |  | FGBHFD | PL312SV5 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516460 | PL312XSP616 | SMOKE DETECTOR AT SV STATION-6 | SMOKE DETECTOR AT SV STATION-6 |  | FGBHFD | PL312SV6 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516506 | PL318GDH901 | FLAMMABLE GAS DETECTOR AT SV STATION-9 | FLAMMABLE GAS DETECTOR AT SV STATION-9 |  | FG_DET | PL318SV9 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516507 | PL318GDH902 | FLAMMABLE GAS DETECTOR AT SV STATION-9 | FLAMMABLE GAS DETECTOR AT SV STATION-9 |  | FG_DET | PL318SV9 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516508 | PL318GDH903 | FLAMMABLE GAS DETECTOR AT SV STATION-9 | FLAMMABLE GAS DETECTOR AT SV STATION-9 |  | FG_DET | PL318SV9 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516509 | PL318GDH904 | FLAMMABLE GAS DETECTOR AT SV STATION-9 | FLAMMABLE GAS DETECTOR AT SV STATION-9 |  | FG_DET | PL318SV9 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516520 | PL318XAC1114 | MANUAL CALL POINT AT SV STATION - 11 | MANUAL CALL POINT AT SV STATION - 11 |  | PA_SYS | PL318SV11 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516521 | PL318XAC1115 | MANUAL ALARM CALL POINT AT SV STATION - 11 | MANUAL ALARM CALL POINT AT SV STATION - 11 |  | PA_SYS | PL318SV11 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516522 | PL318XAC1116 | MANUAL ALARM CALL POINT AT SV STATION - 11 | MANUAL ALARM CALL POINT AT SV STATION - 11 |  | PA_SYS | PL318SV11 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516523 | PL318XAC1117 | MANUAL CALL POINT AT SV STATION - 11 | MANUAL CALL POINT AT SV STATION - 11 |  | PA_SYS | PL318SV11 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516524 | PL318XAC1213 | MANUAL CALL POINT AT SV STATION - 12 | MANUAL CALL POINT AT SV STATION - 12 |  | PA_SYS | PL318SV12 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516525 | PL318XAC1214 | MANUAL CALL POINT AT SV STATION - 12 | MANUAL CALL POINT AT SV STATION - 12 |  | PA_SYS | PL318SV12 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516526 | PL318XAC1215 | MANUAL ALARM CALL POINT AT SV STATION - 12 | MANUAL ALARM CALL POINT AT SV STATION - 12 |  | PA_SYS | PL318SV12 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516527 | PL318XAC1216 | MANUAL ALARM CALL POINT AT SV STATION - 12 | MANUAL ALARM CALL POINT AT SV STATION - 12 |  | PA_SYS | PL318SV12 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516528 | PL318XAC1217 | MANUAL CALL POINT AT SV STATION - 12 | MANUAL CALL POINT AT SV STATION - 12 |  | PA_SYS | PL318SV12 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516529 | PL318XAC813 | MANUAL CALL POINT AT SV STATION - 8 | MANUAL CALL POINT AT SV STATION - 8 |  | PA_SYS | PL318SV8 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516530 | PL318XAC814 | MANUAL CALL POINT AT SV STATION - 8 | MANUAL CALL POINT AT SV STATION - 8 |  | PA_SYS | PL318SV8 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969444422 | MQ600XGC001 | FLAMMABLE GAS DETECTOR, HVAC DUCT | FLAMMABLE GAS DETECTOR HVAC DUCT MAQTA STATION |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969444423 | MQ600XGC002 | FLAMMABLE GAS DETECTOR, HVAC DUCT | FLAMMABLE GAS DETECTOR HVAC DUCT MAQTA STATION |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969444424 | MQ600XGC003 | FLAMMABLE GAS DETECTOR, HVAC DUCT | FLAMMABLE GAS DETECTOR HVAC DUCT MAQTA STATION |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132431 | PL300XGH001/01 | DETECTOR, GAS | HYDROGEN GAS DETECTOR FOR PASSIVE SHELTER SV STATION 1 |  | FG_DET | PL300SVS1 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XGH001/01-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/10/18 | MFPS-PM02.M3
969132432 | PL300XGH001/07 | DETECTOR, GAS | HYDROGEN GAS DETECTOR FOR PASSIVE SHELTER SV STATION 7 |  | FG_DET | PL300SVS7 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XGH001/07-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM02.M3
969132433 | PL300XGH001/04 | DETECTOR, GAS | HYDROGEN GAS DETECTOR FOR PASSIVE SHELTER SV STATION 4 |  | FG_DET | PL300SVS4 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XGH001/04-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM02.M3
969132434 | PL300XGH001/06 | DETECTOR, GAS | HYDROGEN GAS DETECTOR FOR PASSIVE SHELTER SV STATION 6 |  | FG_DET | PL300SVS6 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 1 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XGH001/06-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 02/09/18 | MFPS-PM02.M3
969132435 | PL300XGH001/02 | DETECTOR, GAS | HYDROGEN GAS DETECTOR FOR PASSIVE SHELTER SV STATION 2 |  | FG_DET | PL300SVS2 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XGH001/02-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/10/18 | MFPS-PM02.M3
969132436 | PL300XGH001/05 | DETECTOR, GAS | HYDROGEN GAS DETECTOR FOR PASSIVE SHELTER SV STATION 5 |  | FG_DET | PL300SVS5 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XGH001/05-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM02.M3
969132437 | PL300XGH001/03 | DETECTOR, GAS | HYDROGEN GAS DETECTOR FOR PASSIVE SHELTER SV STATION 3 |  | FG_DET | PL300SVS3 | 3 | FG_DET | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | PL300XGH001/03-UFP | ACTIVE | CONT | PM | FIC | 3 | MONTHS | 08/08/18 | MFPS-PM02.M3
969278689 | PL312CCTV117 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278690 | PL312CCTV118 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278691 | PL312CCTV119 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278692 | PL312CCTV120 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278693 | PL312CCTV121 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278694 | PL312CCTV122 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278695 | PL312CCTV123 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278696 | PL312CCTV124 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278697 | PL312CCTV125 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278698 | PL312CCTV126 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278699 | PL312CCTV127 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278700 | PL312CCTV128 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278701 | PL312CCTV129 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278702 | PL312CCTV130 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278703 | PL312CCTV131 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278704 | PL312CCTV132 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278705 | PL312CCTV133 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278706 | PL312CCTV134 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278707 | PL312CCTV135 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278708 | PL312CCTV136 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278709 | PL312CCTV137 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278710 | PL312CCTV138 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278711 | PL312CCTV139 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278712 | PL312CCTV140 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278713 | PL312CCTV141 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278714 | PL312CCTV142 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278715 | PL312CCTV143 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278716 | PL312CCTV144 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278717 | PL312CCTV145 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278718 | PL312CCTV146 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278719 | PL312CCTV147 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278720 | PL312CCTV148 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278721 | PL312CCTV149 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278722 | PL312CCTV150 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278723 | PL312CCTV151 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278724 | PL312CCTV152 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278725 | PL312CCTV153 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278726 | PL312CCTV154 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278727 | PL312CCTV155 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278728 | PL312CCTV156 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278729 | PL312CCTV157 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278730 | PL312CCTV158 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278731 | PL312CCTV159 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278732 | PL312CCTV160 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278733 | PL312CCTV161 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278734 | PL312CCTV162 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278735 | PL312CCTV163 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278736 | PL312CCTV164 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278737 | PL312CCTV165 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278738 | PL312CCTV166 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278739 | PL312CCTV167 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278740 | PL312CCTV168 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278741 | PL312CCTV169 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278742 | PL312CCTV170 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278743 | PL312CCTV171 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278744 | PL312CCTV172 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278745 | PL312CCTV173 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278746 | PL312CCTV174 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278747 | PL312CCTV175 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278748 | PL312CCTV176 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278749 | PL312CCTV177 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278756 | PL312TEL001 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278757 | PL312TEL002 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278758 | PL312TEL003 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278759 | PL312TEL004 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278760 | PL312TEL005 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278761 | PL312TEL006 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL312MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278762 | PL315CCTV001 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278763 | PL315CCTV002 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278764 | PL315CCTV003 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278765 | PL315CCTV004 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278766 | PL315CCTV005 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278767 | PL315CCTV006 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278768 | PL315CCTV007 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278769 | PL315CCTV008 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265900 | PL100L001A | GAS OIL BASKET FILTER | GAS OIL BASKET FILTER |  | VESSEL | PL100FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 5 | 50 | 10 | 5 | 6.7959 | Non Critical | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265901 | PL100L001B | GAS OIL BASKET FILTER | GAS OIL BASKET FILTER |  | VESSEL | PL100FILTER | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 5 | 50 | 10 | 5 | 6.7959 | Non Critical | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265902 | PL100LDS001 | LDS SYSTEM CABINET | LDS SYSTEM CABINET |  | BLDGS | PL100MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265903 | PL100LP001 | 415V NEW POWER & LIGHTING PANEL | 415V NEW POWER & LIGHTING PANEL |  | BLDGS | PL100SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279501 | M410BFV21253001 | 2" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 2" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279502 | M410BFV21253002 | 3" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 3" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279503 | M410BFV21253003 | 4" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 4" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279504 | M410BFV21253004 | 6" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 6" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279505 | M410BFV21253005 | 10" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 10" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279506 | M410BFV21253006 | 12" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 12" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279507 | M410BFV21253007 | 14" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 14" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279508 | M410BFV21253008 | 18" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 18" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279509 | M410BFV21253009 | 20" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 20" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279510 | M410BFV21253010 | 24" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 24" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279511 | M410BFV21253011 | 8" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved | 8" Butterfly Valve Lug Type, API 609 Category A, Class 150, Raised Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, EPDM Lined Body, PN 16, ASME B16.5, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279512 | M410BFV21253012 | 20" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 | 20" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279513 | M410BFV21253013 | 8" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 | 8" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Gear Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279514 | M410BFV21253014 | 6" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 | 6" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279515 | M410BFV21253015 | 3" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 | 3" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279516 | M410BFV21253016 | 4" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 | 4" Butterfly Valve Wafer Type, API 609 Category A, Class 150, Flat Face, Lever Operator, ASTM A216 Grade WCB, Trim Al-Bronze, Chloroprene Rubber Lined Body, PN 16, ASME B16.5 |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969279517 | M410CPL902 | HOSE CONNECTOR | HOSE CONNECTOR |  | PACKAGE | M410MISC | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | m
969279518 | M410CPL903 | Quick Coupling | Quick Coupling |  | PACKAGE | M410MISC | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | m
969279519 | M410HOS902 | Flexible Hose | Flexible Hose |  | PACKAGE | M410MISC | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | m
969279520 | M410HOS903 | Flexible Hose | Flexible Hose |  | PACKAGE | M410MISC | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | m
969279521 | M410LAN002 | LAN SYSTEM | LAN SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275349 | PL312EOV31204 | ELECTRO HYDRAULIC VALVE, SV STATION-4 | ELECTRO HYDRAULIC VALVE, SV STATION-4 |  | CONTHNDV | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275936 | PL100BAV21243008 | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275937 | PL100BAV21243009 | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275938 | PL100BAV21243010 | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 2" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275939 | PL100BAV21243011 | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 3" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275940 | PL100BAV21243012 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 615101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275941 | PL100CHV21263001 | 16" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 | 16" Dual Plate Double-Flanged Check Valve, API 594, Class 150, Raised Face, ASTM A216 Grade WCB, Trim 13Cr, ASME B16.5 |  | CONTHNDV | PL100VALVE | 3 | CONTHNDV | 616101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275942 | PL100FA001A20 | FAN FOR BATTERY ROOM | FAN FOR BATTERY ROOM |  | HVAC | PL100HVAC | 3 | HVAC | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275943 | PL100FA001B20 | FAN FOR BATTERY ROOM | FAN FOR BATTERY ROOM |  | HVAC | PL100HVAC | 3 | HVAC | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275843 | PL318TE31809A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275844 | PL318TE31809B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275845 | PL318TE31810A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275846 | PL318TE31810B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275847 | PL318TE31811A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275848 | PL318TE31811B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275849 | PL318TE31812A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275850 | PL318TE31812B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275851 | PL318TE31908A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275852 | PL318TE31908B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275853 | PL318TE31909A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275854 | PL318TE31909B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275855 | PL318TE31910A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275856 | PL318TE31910B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275857 | PL318TE31911A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275858 | PL318TE31911B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275859 | PL318TE31912A | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275860 | PL318TE31912B | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | PL318TEMP | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275861 | PL318TEL001 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL318MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275862 | PL318TT31808A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275863 | PL318TT31808B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275864 | PL318TT31809A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275865 | PL318TT31809B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275866 | PL318TT31810A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275867 | PL318TT31810B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275868 | PL318TT31811A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275869 | PL318TT31811B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275870 | PL318TT31812A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275871 | PL318TT31812B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275872 | PL318TT31908A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275873 | PL318TT31908B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275874 | PL318TT31909A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275875 | PL318TT31909B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275876 | PL318TT31910A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275877 | PL318TT31910B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275878 | PL318TT31911A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275879 | PL318TT31911B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275880 | PL318TT31912A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275881 | PL318TT31912B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | PL318TEMP | 3 | TEMP_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275882 | PL318XGH1001 | H2 GAS DETECTOR | H2 GAS DETECTOR |  | FG_DET | PL318GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275883 | PL318YYIS31808A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275884 | PL318YYIS31808B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275885 | PL318YYIS31809A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275886 | PL318YYIS31809B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275887 | PL318YYIS31810A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275888 | PL318YYIS31810B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275889 | PL318YYIS31811A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275890 | PL318YYIS31811B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275891 | PL318YYIS31812A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275892 | PL318YYIS31812B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275893 | PL318YYIS31908A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275894 | PL318YYIS31908B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275895 | PL318YYIS31909A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275896 | PL318YYIS31909B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275897 | PL318YYIS31910A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275898 | PL318YYIS31910B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275899 | PL318YYIS31911A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275900 | PL318YYIS31911B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275901 | PL318YYIS31912A | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275902 | PL318YYIS31912B | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL318MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275903 | PL325BAV21243001 | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL325VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275904 | PL325BAV21243002 | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 4" S-40, Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Bevel End x Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | PL325VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275905 | PL325BAV21243003 | 10" 6.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 300, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe | 10" 6.40mm, Ball Valve Long Pattern Full Bore, API 6D, Class 300, Bevel End, Top Entry Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, Fire Safe |  | CONTHNDV | PL325VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275906 | PL325BB701 | BATTERY BANK | BATTERY BANK |  | BATTERY | PL325BATT | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281592 | M410P006C | MECHANICAL SEAL (NDE) | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269222 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281593 | M410P024A | MECHANICAL SEAL (DE) | AL DHAFRA JP-8 MAIN LINE PUMP | 969269223 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281594 | M410P024A | MECHANICAL SEAL (NDE) | AL DHAFRA JP-8 MAIN LINE PUMP | 969269223 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281595 | M410P024B | MECHANICAL SEAL (DE) | AL DHAFRA JP-8 MAIN LINE PUMP | 969269224 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281596 | M410P024B | MECHANICAL SEAL (NDE) | AL DHAFRA JP-8 MAIN LINE PUMP | 969269224 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281597 | M410P024C | MECHANICAL SEAL (DE) | AL DHAFRA JP-8 MAIN LINE PUMP | 969269225 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281598 | M410P024C | MECHANICAL SEAL (NDE) | AL DHAFRA JP-8 MAIN LINE PUMP | 969269225 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281599 | M410FG511 | Sight Glass | Sight Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281600 | M410FLX101 | Flexible Hose | Flexible Hose |  | PACKAGE | M410MISC | [14 empty] | Non Critical | N | Non Critical | N |  |  | m
969281601 | M410CCTVP001 | CCTV CABINET | L&D CCTV CABINET MCR, PIPELINE SURVEILLANCE. |  | BLDGS | M410CCTV | 3 | CCTV_SYS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281602 | M410CCTVP002 | CCTV CABINET | L&D CCTV CABINET MCR, PIPELINE SURVEILLANCE. |  | BLDGS | M410CCTV | 3 | CCTV_SYS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281603 | M410CCTVP003 | CCTV CABINET | L&D CCTV CABINET MCR, PIPELINE SURVEILLANCE. |  | BLDGS | M410CCTV | 3 | CCTV_SYS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175100 | M410LG450A | JET A1 INTER-TANK FILTER COALESCER 410-L-004A | JET A1 INTER-TANK FILTER COALESCER 410-L-004A |  | INDICATR | M410L004A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175101 | M410LG450B | JET A1 INTER-TANK FILTER COALESCER 410-L-004B | JET A1 INTER-TANK FILTER COALESCER 410-L-004B |  | INDICATR | M410L004B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175102 | M410LG450C | JET A1 INTER-TANK FILTER COALESCER 410-L-004C | JET A1 INTER-TANK FILTER COALESCER 410-L-004C |  | INDICATR | M410L004C | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195257 | M410LP001 | Small Power Distribution Board | Small Power Distribution Board |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 24/12/18 | ME-PNL1-PM-M6
969195258 | M410MPDP001 | MISCELLANEOUS POWER DISTRIBUTION PANEL | MISCELLANEOUS POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410MPDP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/01/19 | ME-PNL1-PM-M6
969195259 | M410MPDP002 | MISCELLANEOUS POWER DISTRIBUTION PANEL | MISCELLANEOUS POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410MPDP002-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 02/11/18 | ME-PNL1-PM-M6
969195260 | M410MVP001 | Small Power Distribution Board | Small Power Distribution Board |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 02/11/18 | ME-PNL1-PM-M6
969175122 | M410FT450A | 410-L-004A OUTLET | JET A1 INTER-TANK TRANSFER FILTER 410-L-004A OUTLET |  | DP_TXTR | M410L004A | 1 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175123 | M410FT450B | 410-L-004B OUTLET | JET A1 INTER-TANK TRANSFER FILTER 410-L-004B OUTLET |  | DP_TXTR | M410L004B | 3 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175105 | M410LT114A | AGAR LEVEL TRANSMITTER JET A1 TANK 410T011 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T011 |  | LVL_TX | M410T011 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175106 | M410LT114B | LEVEL TRANSMITTER JET A1 TANK 410T011 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T011 |  | LVL_TX | M410T011 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175107 | M410LT124A | LEVEL TRANSMITTER JET A1 TANK 410T012 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T012 |  | LVL_TX | M410T012 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175108 | M410LT124B | LEVEL TRANSMITTER JET A1 TANK 410T012 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T012 |  | LVL_TX | M410T012 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175109 | M410LT134A | LEVEL TRANSMITTER JET A1 TANK 410T013 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T013 |  | LVL_TX | M410T013 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175110 | M410LT134B | LEVEL TRANSMITTER JET A1 TANK 410T013 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T013 |  | LVL_TX | M410T013 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175111 | M410LT144A | LEVEL TRANSMITTER JET A1 TANK 410T014 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T014 |  | LVL_TX | M410T014 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175112 | M410LT144B | LEVEL TRANSMITTER JET A1 TANK 410T014 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T014 |  | LVL_TX | M410T014 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175113 | M410LT154A | LEVEL TRANSMITTER JET A1 TANK 410T015 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T015 |  | LVL_TX | M410T015 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175288 | M410PG017 | GAS OIL FROM 410-T-009/010TO ROAD TANKER LOADING PUMP | GAS OIL FROM 410-T-009/010TO ROAD TANKER LOADING PUMP |  | INDICATR | M410T010 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175289 | M410PG018 | INSTRUMENT AIR HEADER | INSTRUMENT AIR HEADER |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175290 | M410PG019 | POTABLE WATER HEADER | POTABLE WATER HEADER |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175291 | M410PG020 | FROM PIPELINE MANIFOLDTO 410-T-009/010 | FROM PIPELINE MANIFOLDTO 410-T-009/010 |  | INDICATR | M410T009 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175292 | M410PG150 | 410-V-003 | PG FOR 410V003 |  | INDICATR | M410V003 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175293 | M410PG151 | 410-P-009 DISCHARGE | PG ON 410-P-009 DISCHARGE |  | INDICATR | M410P009 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175294 | M410PG152 | 410-V-004 | PG FOR 410V004 |  | INDICATR | M410V004 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175295 | M410PG153 | 410-P-010 DISCHARGE | 410-P-010 DISCHARGE |  | INDICATR | M410P010 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175296 | M410PG209 | 410-P-007A SUCTION | 410-P-007A SUCTION |  | INDICATR | M410P007A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175297 | M410PG210 | 410-P-007A DISCHARGE | 410-P-007A DISCHARGE |  | INDICATR | M410P007A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175927 | M410LT033C | ULG 91 TANK 410-T-003 | SAAB ROSEMOUNT ULG 91 TANK 410-T-003 |  | LVL_TX | M410T003 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175928 | M410LT043A | ULG 91 TANK 410-T-004 | SAAB ROSEMOUNT ULG 91 TANK 410-T-004 |  | LVL_TX | M410T004 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175929 | M410LT043B | ULG 91 TANK 410-T-004 | SAAB ROSEMOUNT ULG 91 TANK 410-T-004 |  | LVL_TX | M410T004 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175930 | M410LT043C | ULG 91 TANK 410-T-004 | SAAB ROSEMOUNT ULG 91 TANK 410-T-004 |  | LVL_TX | M410T004 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175931 | M410LT053A | ULG 95 TANK 410-T-005 | SAAB ROSEMOUNT ULG 95 TANK 410-T-005 |  | LVL_TX | M410T005 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175932 | M410LT053B | ULG 95 TANK 410-T-005 | SAAB ROSEMOUNT ULG 95 TANK 410-T-005 |  | LVL_TX | M410T005 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175933 | M410LT053C | ULG 95 TANK 410-T-005 | SAAB ROSEMOUNT ULG 95 TANK 410-T-005 |  | LVL_TX | M410T005 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175934 | M410LT063A | ULG 95 TANK 410-T-006 | SAAB ROSEMOUNT ULG 95 TANK 410-T-006 |  | LVL_TX | M410T006 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175935 | M410LT063B | ULG 95 TANK 410-T-006 | SAAB ROSEMOUNT ULG 95 TANK 410-T-006 |  | LVL_TX | M410T006 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175936 | M410LT063C | ULG 95 TANK 410-T-006 | SAAB ROSEMOUNT ULG 95 TANK 410-T-006 |  | LVL_TX | M410T006 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175937 | M410LT073A | ULG 95 TANK 410-T-007 | SAAB ROSEMOUNT ULG 95 TANK 410-T-007 |  | LVL_TX | M410T007 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175938 | M410LT073B | ULG 95 TANK 410-T-007 | SAAB ROSEMOUNT ULG 95 TANK 410-T-007 |  | LVL_TX | M410T007 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175939 | M410LT073C | ULG 95 TANK 410-T-007 | SAAB ROSEMOUNT ULG 95 TANK 410-T-007 |  | LVL_TX | M410T007 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175940 | M410LT083A | ULG 95 TANK 410-T-008 | SAAB ROSEMOUNT ULG 95 TANK 410-T-008 |  | LVL_TX | M410T008 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175941 | M410LT083B | ULG 95 TANK 410-T-008 | SAAB ROSEMOUNT ULG 95 TANK 410-T-008 |  | LVL_TX | M410T008 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175942 | M410LT083C | ULG 95 TANK 410-T-008 | SAAB ROSEMOUNT ULG 95 TANK 410-T-008 |  | LVL_TX | M410T008 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175943 | M410LT093A | GAS OIL TANK 410-T-009 | SAAB ROSEMOUNT GAS OIL TANK 410-T-009 |  | LVL_TX | M410T009 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175944 | M410LT093B | GAS OIL TANK 410-T-009 | SAAB ROSEMOUNT GAS OIL TANK 410-T-009 |  | LVL_TX | M410T009 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175945 | M410LT093C | GAS OIL TANK 410-T-009 | SAAB ROSEMOUNT GAS OIL TANK 410-T-009 |  | LVL_TX | M410T009 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175946 | M410LT103A | SAAB ROSEMOUNT GAS OIL TANK 410-T-010 | SAAB ROSEMOUNT GAS OIL TANK 410-T-010 |  | LVL_TX | M410T010 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175947 | M410LT103B | GAS OIL TANK 410-T-010 | SAAB ROSEMOUNT GAS OIL TANK 410-T-010 |  | LVL_TX | M410T010 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175948 | M410LT103C | GAS OIL TANK 410-T-010 | SAAB ROSEMOUNT GAS OIL TANK 410-T-010 |  | LVL_TX | M410T010 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175949 | M410LT113A | JET A1 TANK 410-T-011 | SAAB ROSEMOUNT JET A1 TANK 410-T-011 |  | LVL_TX | M410T011 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175950 | M410LT113B | JET A1 TANK 410-T-011 | SAAB ROSEMOUNT JET A1 TANK 410-T-011 |  | LVL_TX | M410T011 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175951 | M410LT113C | JET A1 TANK 410-T-011 | SAAB ROSEMOUNT JET A1 TANK 410-T-011 |  | LVL_TX | M410T011 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175952 | M410LT123A | JET A1 TANK 410-T-012 | SAAB ROSEMOUNT JET A1 TANK 410-T-012 |  | LVL_TX | M410T012 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175953 | M410LT123B | JET A1 TANK 410-T-012 | SAAB ROSEMOUNT JET A1 TANK 410-T-012 |  | LVL_TX | M410T012 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175954 | M410LT123C | JET A1 TANK 410-T-012 | SAAB ROSEMOUNT JET A1 TANK 410-T-012 |  | LVL_TX | M410T012 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175955 | M410LT133A | JET A1 TANK 410-T-013 | SAAB ROSEMOUNT JET A1 TANK 410-T-013 |  | LVL_TX | M410T013 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175956 | M410LT133B | JET A1 TANK 410-T-013 | SAAB ROSEMOUNT JET A1 TANK 410-T-013 |  | LVL_TX | M410T013 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175957 | M410LT133C | JET A1 TANK 410-T-013 | SAAB ROSEMOUNT JET A1 TANK 410-T-013 |  | LVL_TX | M410T013 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175958 | M410LT143A | JET A1 TANK 410-T-014 | SAAB ROSEMOUNT JET A1 TANK 410-T-014 |  | LVL_TX | M410T014 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175959 | M410LT143B | JET A1 TANK 410-T-014 | SAAB ROSEMOUNT JET A1 TANK 410-T-014 |  | LVL_TX | M410T014 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175960 | M410LT143C | JET A1 TANK 410-T-014 | SAAB ROSEMOUNT JET A1 TANK 410-T-014 |  | LVL_TX | M410T014 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175961 | M410LT153A | JET A1 TANK 410-T-015 | SAAB ROSEMOUNT JET A1 TANK 410-T-015 |  | LVL_TX | M410T015 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175962 | M410LT153B | JET A1 TANK 410-T-015 | SAAB ROSEMOUNT JET A1 TANK 410-T-015 |  | LVL_TX | M410T015 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175963 | M410LT153C | JET A1 TANK 410-T-015 | SAAB ROSEMOUNT JET A1 TANK 410-T-015 |  | LVL_TX | M410T015 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175964 | M410LT163A | JET A1 TANK 410-T-016 | SAAB ROSEMOUNT JET A1 TANK 410-T-016 |  | LVL_TX | M410T016 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175965 | M410LT163B | JET A1 TANK 410-T-016 | SAAB ROSEMOUNT JET A1 TANK 410-T-016 |  | LVL_TX | M410T016 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175966 | M410LT163C | JET A1 TANK 410-T-016 | SAAB ROSEMOUNT JET A1 TANK 410-T-016 |  | LVL_TX | M410T016 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270685 | M410TSV711 | THERMAL SAFETY VALVE FOR ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) | THERMAL SAFETY VALVE FOR ANTI FREEZE INJECTION PACKGAE FOR JET A1(JP-8) |  | PSV | M400ME003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270686 | M410TSV731 | THERMAL SAFETY VALVE FOR ANTI-STATIC INJECTION PACKGAE FOR JET A1 / JP-8 | THERMAL SAFETY VALVE FOR ANTI-STATIC INJECTION PACKGAE FOR JET A1 / JP-8 |  | PSV | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270687 | M410TSV732 | THERMAL SAFETY VALVE FOR ANTI-STATIC INJECTION PACKGAE FOR JET A1 / JP-8 | THERMAL SAFETY VALVE FOR ANTI-STATIC INJECTION PACKGAE FOR JET A1 / JP-8 |  | PSV | M410ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270688 | M410TSV741 | THERMAL SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | THERMAL SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 1 | PACKAGE | 0 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 50 | 10 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270689 | M410TSV721 | THERMAL SAFETY VALVE FOR DYE(BLUE) INJECTION PACKAGE 410-ME-001 FOR ULG 98 | THERMAL SAFETY VALVE BLUE DYE INJECTION PACKAGE 410-ME-001 ULG 98 |  | PACKAGE | M410ME001 | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 50 | 10 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270690 | M410TCP010 | TRANSFOMER / RECTIFIER FOR CABIMET OF UNIT 410 CATHODIC PROTECTION | TRANSFOMER / RECTIFIER FOR CABINET OF UNIT 410 CATHODIC PROTECTION. |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TCP010-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969270691 | M410TCP020 | TRANSFOMER / RECTIFIER FOR CABIMET OF UNIT 410 CATHODIC PROTECTION | TRANSFOMER / RECTIFIER FOR CABIMET OF UNIT 410 CATHODIC PROTECTION |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TCP020-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969270692 | M410TCP021 | TRANSFOMER / RECTIFIER FOR CABIMET OF UNIT 410 CATHODIC PROTECTION | TRANSFOMER / RECTIFIER FOR CABIMET OF UNIT 410 CATHODIC PROTECTION |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TCP021-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969270693 | M410TCP022 | TRANSFOMER / RECTIFIER FOR CABIMET OF UNIT 410 CATHODIC PROTECTION | TRANSFOMER / RECTIFIER FOR CABIMET OF UNIT 410 CATHODIC PROTECTION |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TCP022-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969270694 | M410TCP053A | TRANSFOMER / RECTIFIER FOR TANK AND PIPING UNIT 410 | TRANSFOMER / RECTIFIER FOR TANK AND PIPING UNIT 410 |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N |  | 0 | Y | M410TCP053A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-009-M6
969298503 | M410INS2308001 | ESD | INERGEN GAS SYSTEM | 969175977 |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175350 | M410PG757 | WATER SPRAY FOR 410-T-015FROM 410-RO-757 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-757 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175548 | M410LG200 | FIRE WATER STORAGE TANK 410-T-051 | FIRE WATER STORAGE TANK 410-T-051 |  | INDICATR | M410T051 | 1 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175549 | M410LG201 | FIRE WATER STORAGE TANK 410-T-052 | FIRE WATER STORAGE TANK 410-T-052 |  | INDICATR | M410T052 | 1 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175550 | M410MOV0101 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0101-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175551 | M410MOV0102 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0102-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175552 | M410MOV0103 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0103-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175553 | M410MOV0104 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0104-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175554 | M410MOV0105 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0105-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175555 | M410MOV0106 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0106-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175556 | M410MOV0107 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0107-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175557 | M410MOV0108 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0108-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175351 | M410PG758 | WATER SPRAY FOR 410-T-015FROM 410-RO-758 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-758 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175558 | M410MOV0109 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0109-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
969175559 | M410MOV0110 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0110-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
969175560 | M410MOV0111 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0111-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/09/18 | ME-PM-002-M6
969175561 | M410MOV0112 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-001 |  | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0112-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969175562 | M410MOV0201 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0201-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969175563 | M410MOV0202 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0202-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
969175564 | M410MOV0203 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0203-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
969175565 | M410MOV0204 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0204-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/09/18 | ME-PM-002-M6
969175566 | M410MOV0205 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0205-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969175567 | M410MOV0206 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0206-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969175352 | M410PG759 | WATER SPRAY FOR 410-T-015FROM 410-RO-759 TO RISER PIPE | WATER SPRAY FOR 410-T-015FROM 410-RO-759 TO RISER PIPE |  | INDICATR | M410T015 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175353 | M410PG760 | WATER SPRAY FOR 410-T-016FROM 410-RO-760 TO RISER PIPE | WATER SPRAY FOR 410-T-016FROM 410-RO-760 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175354 | M410PG761 | PRESSURE GAUGES | WATER SPRAY FOR 410-T-016FROM 410-RO-761 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175355 | M410PG762 | PRESSURE GAUGES | WATER SPRAY FOR 410-T-016FROM 410-RO-762 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175356 | M410PG763 | WATER SPRAY FOR 410-T-016FROM 410-RO-763 TO RISER PIPE | WATER SPRAY FOR 410-T-016FROM 410-RO-763 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175357 | M410PG764 | WATER SPRAY FOR 410-T-016FROM 410-RO-764 TO RISER PIPE | WATER SPRAY FOR 410-T-016FROM 410-RO-764 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175358 | M410PG765 | WATER SPRAY FOR 410-T-016FROM 410-RO-765 TO RISER PIPE | WATER SPRAY FOR 410-T-016FROM 410-RO-765 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175359 | M410PG766 | WATER SPRAY FOR 410-T-016FROM 410-RO-766 TO RISER PIPE | WATER SPRAY FOR 410-T-016FROM 410-RO-766 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175360 | M410PG767 | WATER SPRAY FOR 410-T-016FROM 410-RO-767 TO RISER PIPE | WATER SPRAY FOR 410-T-016FROM 410-RO-767 TO RISER PIPE |  | INDICATR | M410T016 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175361 | M410PG768 | WATER SPRAY FOR 410-T-005FROM 410-RO-768 TO RISER PIPE | WATER SPRAY FOR 410-T-005FROM 410-RO-768 TO RISER PIPE |  | INDICATR | M410T005 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175362 | M410PG769 | WATER SPRAY FOR 410-T-005FROM 410-RO-769 TO RISER PIPE | WATER SPRAY FOR 410-T-005FROM 410-RO-769 TO RISER PIPE |  | INDICATR | M410T005 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175363 | M410PG770 | WATER SPRAY FOR 410-T-005FROM 410-RO-770 TO RISER PIPE | WATER SPRAY FOR 410-T-005FROM 410-RO-770 TO RISER PIPE |  | INDICATR | M410T005 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175364 | M410PG771 | WATER SPRAY FOR 410-T-005FROM 410-RO-771 TO RISER PIPE | WATER SPRAY FOR 410-T-005FROM 410-RO-771 TO RISER PIPE |  | INDICATR | M410T005 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175365 | M410PG772 | WATER SPRAY FOR 410-T-006FROM 410-RO-772 TO RISER PIPE | WATER SPRAY FOR 410-T-006FROM 410-RO-772 TO RISER PIPE |  | INDICATR | M410T006 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175366 | M410PG773 | WATER SPRAY FOR 410-T-006FROM 410-RO-773 TO RISER PIPE | WATER SPRAY FOR 410-T-006FROM 410-RO-773 TO RISER PIPE |  | INDICATR | M410T006 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175367 | M410PG774 | WATER SPRAY FOR 410-T-006FROM 410-RO-774 TO RISER PIPE | WATER SPRAY FOR 410-T-006FROM 410-RO-774 TO RISER PIPE |  | INDICATR | M410T006 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175368 | M410PG775 | WATER SPRAY FOR 410-T-006FROM 410-RO-775 TO RISER PIPE | WATER SPRAY FOR 410-T-006FROM 410-RO-775 TO RISER PIPE |  | INDICATR | M410T006 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175369 | M410PG776 | WATER SPRAY FOR 410-T-007FROM 410-RO-776 TO RISER PIPE | WATER SPRAY FOR 410-T-007FROM 410-RO-776 TO RISER PIPE |  | INDICATR | M410T007 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175370 | M410PG777 | WATER SPRAY FOR 410-T-007FROM 410-RO-777 TO RISER PIPE | WATER SPRAY FOR 410-T-007FROM 410-RO-777 TO RISER PIPE |  | INDICATR | M410T007 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175371 | M410PG778 | WATER SPRAY FOR 410-T-007FROM 410-RO-778 TO RISER PIPE | WATER SPRAY FOR 410-T-007FROM 410-RO-778 TO RISER PIPE |  | INDICATR | M410T007 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175372 | M410PG779 | WATER SPRAY FOR 410-T-007FROM 410-RO-779 TO RISER PIPE | WATER SPRAY FOR 410-T-007FROM 410-RO-779 TO RISER PIPE |  | INDICATR | M410T007 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175373 | M410PG780 | WATER SPRAY FOR 410-T-008FROM 410-RO-780 TO RISER PIPE | WATER SPRAY FOR 410-T-008FROM 410-RO-780 TO RISER PIPE |  | INDICATR | M410T008 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175374 | M410PG781 | WATER SPRAY FOR 410-T-008FROM 410-RO-781 TO RISER PIPE | WATER SPRAY FOR 410-T-008FROM 410-RO-781 TO RISER PIPE |  | INDICATR | M410T008 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175375 | M410PG782 | WATER SPRAY FOR 410-T-008FROM 410-RO-782 TO RISER PIPE | WATER SPRAY FOR 410-T-008FROM 410-RO-782 TO RISER PIPE |  | INDICATR | M410T008 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175376 | M410PG783 | WATER SPRAY FOR 410-T-008FROM 410-RO-783 TO RISER PIPE | WATER SPRAY FOR 410-T-008FROM 410-RO-783 TO RISER PIPE |  | INDICATR | M410T008 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175377 | M410PG784 | WATER SPRAY FOR 410-T-001FROM 410-RO-784 TO RISER PIPE | WATER SPRAY FOR 410-T-001FROM 410-RO-784 TO RISER PIPE |  | INDICATR | M410T001 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175378 | M410PG785 | WATER SPRAY FOR 410-T-001FROM 410-RO-785 TO RISER PIPE | WATER SPRAY FOR 410-T-001FROM 410-RO-785 TO RISER PIPE |  | INDICATR | M410T001 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175379 | M410PG786 | WATER SPRAY FOR 410-T-001FROM 410-RO-786 TO RISER PIPE | WATER SPRAY FOR 410-T-001FROM 410-RO-786 TO RISER PIPE |  | INDICATR | M410T001 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175380 | M410PG787 | WATER SPRAY FOR 410-T-001FROM 410-RO-787 TO RISER PIPE | WATER SPRAY FOR 410-T-001FROM 410-RO-787 TO RISER PIPE |  | INDICATR | M410T001 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175381 | M410PG788 | WATER SPRAY FOR 410-T-002FROM 410-RO-788 TO RISER PIPE | WATER SPRAY FOR 410-T-002FROM 410-RO-788 TO RISER PIPE |  | INDICATR | M410T002 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175382 | M410PG789 | WATER SPRAY FOR 410-T-002FROM 410-RO-789 TO RISER PIPE | WATER SPRAY FOR 410-T-002FROM 410-RO-789 TO RISER PIPE |  | INDICATR | M410T002 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175383 | M410PG790 | WATER SPRAY FOR 410-T-002FROM 410-RO-790 TO RISER PIPE | WATER SPRAY FOR 410-T-002FROM 410-RO-790 TO RISER PIPE |  | INDICATR | M410T002 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175384 | M410PG791 | WATER SPRAY FOR 410-T-002FROM 410-RO-791 TO RISER PIPE | WATER SPRAY FOR 410-T-002FROM 410-RO-791 TO RISER PIPE |  | INDICATR | M410T002 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175385 | M410PG792 | WATER SPRAY FOR 410-T-003FROM 410-RO-792 TO RISER PIPE | WATER SPRAY FOR 410-T-003FROM 410-RO-792 TO RISER PIPE |  | INDICATR | M410T003 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175386 | M410PG793 | WATER SPRAY FOR 410-T-003FROM 410-RO-793 TO RISER PIPE | WATER SPRAY FOR 410-T-003FROM 410-RO-793 TO RISER PIPE |  | INDICATR | M410T003 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175387 | M410PG794 | WATER SPRAY FOR 410-T-003FROM 410-RO-794 TO RISER PIPE | WATER SPRAY FOR 410-T-003FROM 410-RO-794 TO RISER PIPE |  | INDICATR | M410T003 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175388 | M410PG795 | WATER SPRAY FOR 410-T-003FROM 410-RO-795 TO RISER PIPE | WATER SPRAY FOR 410-T-003FROM 410-RO-795 TO RISER PIPE |  | INDICATR | M410T003 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175389 | M410PG796 | WATER SPRAY FOR 410-T-004FROM 410-RO-796 TO RISER PIPE | WATER SPRAY FOR 410-T-004FROM 410-RO-796 TO RISER PIPE |  | INDICATR | M410T004 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175390 | M410PG797 | WATER SPRAY FOR 410-T-004FROM 410-RO-797 TO RISER PIPE | WATER SPRAY FOR 410-T-004FROM 410-RO-797 TO RISER PIPE |  | INDICATR | M410T004 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175391 | M410PG798 | WATER SPRAY FOR 410-T-004FROM 410-RO-798 TO RISER PIPE | WATER SPRAY FOR 410-T-004FROM 410-RO-798 TO RISER PIPE |  | INDICATR | M410T004 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175392 | M410PG799 | WATER SPRAY FOR 410-T-004FROM 410-RO-799 TO RISER PIPE | WATER SPRAY FOR 410-T-004FROM 410-RO-799 TO RISER PIPE |  | INDICATR | M410T004 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175393 | M410PG800 | WATER SPRAY FOR 410-T-009FROM 410-RO-800 TO RISER PIPE | WATER SPRAY FOR 410-T-009FROM 410-RO-800 TO RISER PIPE |  | INDICATR | M410T009 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175394 | M410PG801 | WATER SPRAY FOR 410-T-009FROM 410-RO-801 TO RISER PIPE | WATER SPRAY FOR 410-T-009FROM 410-RO-801 TO RISER PIPE |  | INDICATR | M410T009 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175395 | M410PG802 | WATER SPRAY FOR 410-T-009FROM 410-RO-802 TO RISER PIPE | WATER SPRAY FOR 410-T-009FROM 410-RO-802 TO RISER PIPE |  | INDICATR | M410T009 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175396 | M410PG803 | WATER SPRAY FOR 410-T-009FROM 410-RO-803 TO RISER PIPE | WATER SPRAY FOR 410-T-009FROM 410-RO-803 TO RISER PIPE |  | INDICATR | M410T009 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175397 | M410PG804 | WATER SPRAY FOR 410-T-010FROM 410-RO-804 TO RISER PIPE | WATER SPRAY FOR 410-T-010FROM 410-RO-804 TO RISER PIPE |  | INDICATR | M410T010 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175398 | M410PG805 | WATER SPRAY FOR 410-T-010FROM 410-RO-805 TO RISER PIPE | WATER SPRAY FOR 410-T-010FROM 410-RO-805 TO RISER PIPE |  | INDICATR | M410T010 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175399 | M410PG806 | WATER SPRAY FOR 410-T-010FROM 410-RO-806 TO RISER PIPE | WATER SPRAY FOR 410-T-010FROM 410-RO-806 TO RISER PIPE |  | INDICATR | M410T010 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175400 | M410PG807 | WATER SPRAY FOR 410-T-010FROM 410-RO-807 TO RISER PIPE | WATER SPRAY FOR 410-T-010FROM 410-RO-807 TO RISER PIPE |  | INDICATR | M410T010 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938791 | M400WOV836 | DELUGE VALVE | Transfer Pumps Deluge Valve 400WOV836, 837. |  |  | M400VALVE | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175402 | M410TMM001A | Transformer and NER | Transformer and NER |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TMM001A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 07/09/18 | ME-PM-009-M6
969175403 | M410TMM001B | Transformer and NER | Transformer and NER |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TMM001B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 08/09/18 | ME-PM-009-M6
969175404 | M410MMS001 | 11KV Switchgear | 11KV Switchgear |  | MCC_SWBD | M410SCB | 3 | MCC_SWBD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969207827 | M410MS00116B | SWITCHGEAR Panel | SPARE MOTOR FEEDER |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410MS00116B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969175406 | M410PC001 | 415V Switchgear and MCC | 415V Switchgear and MCC |  | MCC_SWBD | M410SCB | 3 | MCC_SWBD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC001-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969175407 | M410PFI001A | Power Capacitor Bank | Power Capacitor Bank |  | BAT_CHRG | M410BATT | 3 | BAT_CHRG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001A-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 22/10/18 | ME-PM-005-Y1
969175408 | M410PFI001B | Power Capacitor Bank | Power Capacitor Bank |  | BAT_CHRG | M410BATT | 3 | BAT_CHRG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410PFI001B-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 27/10/18 | ME-PM-005-Y1
969175409 | M410UPSAC001A | AC UPS IN SIS BUILDING WITH 360 CELLS. | AC UPS IN SIS BUILDING WITH 360 CELLS. |  | INVRT_UP | M410BATT | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410UPSAC001A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/12/18 | ME-PM-017-M6
969175410 | M410UPSAC001B | AC UPS | AC UPS IN SIS BUILDING WITH 360 CELLS. |  | INVRT_UP | M410BATT | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410UPSAC001B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/12/18 | ME-PM-017-M6
969175411 | M410UPSAC002A | AC UPS | AC UPS IN ECR BUILDING WITH 360 CELLS. |  | INVRT_UP | M410BATT | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410UPSAC002A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/12/18 | ME-PM-017-M6
969175412 | M410UPSAC002B | AC UPS | AC UPS |  | INVRT_UP | M410BATT | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410UPSAC002B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/12/18 | ME-PM-017-M6
969175413 | M410UPSDC001A | DC UPS | DC UPS IN SS410 170 CELS (SLM850-1). |  | INVRT_UP | M410BATT | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410UPSDC001A-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/12/18 | ME-PM-017-M6
969175414 | M410UPSDC001B | DC UPS | DC UPS IN SS410 170 CELS (SLM850-1). |  | INVRT_UP | M410BATT | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410UPSDC001B-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/12/18 | ME-PM-017-M6
969175415 | M410CCTV001 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera NW OF Tank 11 |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175416 | M410CCTV002 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera East of Warehouse. |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175417 | M410CCTV003 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera SW of Tank 15 |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175418 | M410CCTV004 | Outdoor CCTV Camera | Outdoor PAN/TILT Camera SE of Tank 14 |  | CCTV_SYS | M410CCTV | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175980 | M410SYS2314001 | FLOATING ROOF ACCESSORY | FLOATING ROOF ACCESSORY |  | PACKAGE | M410MISC | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175981 | M410SYS2315001 | JET MIXER | JET MIXER |  | PACKAGE | M410MISC | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175630 | M410MOV0709 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0709-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/12/18 | ME-PM-002-M6
969175631 | M410MOV0710 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0710-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/12/18 | ME-PM-002-M6
969175632 | M410MOV0711 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0711-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969175633 | M410MOV0712 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0712-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969175634 | M410MOV0801 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0801-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/12/18 | ME-PM-002-M6
969175635 | M410MOV0802 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0802-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/12/18 | ME-PM-002-M6
969175636 | M410MOV0803 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0803-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 31/12/18 | ME-PM-002-M6
969175637 | M410MOV0804 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0804-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/01/19 | ME-PM-002-M6
969175638 | M410MOV0805 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0805-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175639 | M410MOV0806 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0806-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175640 | M410MOV0807 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0807-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175641 | M410MOV0808 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0808-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175642 | M410MOV0809 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0809-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175643 | M410MOV0810 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0810-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175644 | M410MOV0811 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0811-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175645 | M410MOV0812 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-008 |  | MOV | M410T008 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0812-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175646 | M410MOV0901 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0901-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175647 | M410MOV0902 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0902-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175648 | M410MOV0903 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0903-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175649 | M410MOV0904 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0904-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175650 | M410MOV0905 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0905-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175651 | M410MOV0906 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0906-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175652 | M410MOV0907 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0907-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175653 | M410MOV0908 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0908-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175654 | M410MOV0909 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0909-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
969175655 | M410MOV0910 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0910-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/01/19 | ME-PM-002-M6
969175656 | M410MOV0911 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0911-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/01/19 | ME-PM-002-M6
969175657 | M410MOV0912 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-009 |  | MOV | M410T009 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0912-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/01/19 | ME-PM-002-M6
969175658 | M410MOV1001 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1001-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 31/01/19 | ME-PM-002-M6
969175659 | M410MOV1002 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1002-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 31/01/19 | ME-PM-002-M6
969175660 | M410MOV1003 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1003-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/02/19 | ME-PM-002-M6
969175661 | M410MOV1004 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1004-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/02/19 | ME-PM-002-M6
969175662 | M410MOV1005 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1005-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/02/19 | ME-PM-002-M6
969175663 | M410MOV1006 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1006-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/02/19 | ME-PM-002-M6
969175664 | M410MOV1007 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1007-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/02/19 | ME-PM-002-M6
969175665 | M410MOV1008 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1008-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/02/19 | ME-PM-002-M6
969175666 | M410MOV1009 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1009-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/02/19 | ME-PM-002-M6
969175667 | M410MOV1010 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1010-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/02/19 | ME-PM-002-M6
969175668 | M410MOV1011 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1011-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/02/19 | ME-PM-002-M6
969175669 | M410MOV1012 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-010 |  | MOV | M410T010 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1012-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/02/19 | ME-PM-002-M6
969175670 | M410MOV1101 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1101-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/02/19 | ME-PM-002-M6
969175671 | M410MOV1102 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1102-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/02/19 | ME-PM-002-M6
969175672 | M410MOV1103 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1103-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/02/19 | ME-PM-002-M6
969175673 | M410MOV1104 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1104-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/02/19 | ME-PM-002-M6
969175674 | M410MOV1105 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1105-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/02/19 | ME-PM-002-M6
969175675 | M410MOV1106 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1106-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/02/19 | ME-PM-002-M6
969175676 | M410MOV1107 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1107-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/02/19 | ME-PM-002-M6
969175677 | M410MOV1108 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1108-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/02/19 | ME-PM-002-M6
969175678 | M410MOV1109 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1109-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969175679 | M410MOV1110 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | M410T011 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1110-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969175680 | M410MOV1201 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1201-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969175681 | M410MOV1202 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1202-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/02/19 | ME-PM-002-M6
969175682 | M410MOV1203 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1203-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/09/18 | ME-PM-002-M6
969175683 | M410MOV1204 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1204-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/09/18 | ME-PM-002-M6
969175684 | M410MOV1205 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1205-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/09/18 | ME-PM-002-M6
969175685 | M410MOV1206 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1206-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/09/18 | ME-PM-002-M6
969175686 | M410MOV1207 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1207-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/09/18 | ME-PM-002-M6
969175687 | M410MOV1208 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1208-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/09/18 | ME-PM-002-M6
969175688 | M410MOV1209 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1209-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175689 | M410MOV1210 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | M410T012 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1210-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
969175690 | M410MOV1301 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1301-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
969175691 | M410MOV1302 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1302-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/09/18 | ME-PM-002-M6
969175692 | M410MOV1303 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1303-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/09/18 | ME-PM-002-M6
969175693 | M410MOV1304 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1304-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969175694 | M410MOV1305 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1305-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969175695 | M410MOV1306 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1306-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
969175696 | M410MOV1307 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1307-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/09/18 | ME-PM-002-M6
969175697 | M410MOV1308 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1308-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/09/18 | ME-PM-002-M6
969175698 | M410MOV1309 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1309-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969175699 | M410MOV1310 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | M410T013 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1310-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969175700 | M410MOV1401 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1401-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
969175701 | M410MOV1402 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1402-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/09/18 | ME-PM-002-M6
969175702 | M410MOV1403 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1403-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/10/18 | ME-PM-002-M6
969175703 | M410MOV1404 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1404-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969175704 | M410MOV1405 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1405-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969175705 | M410MOV1406 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1406-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/10/18 | ME-PM-002-M6
969175706 | M410MOV1407 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1407-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/10/18 | ME-PM-002-M6
969175707 | M410MOV1408 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1408-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/10/18 | ME-PM-002-M6
969175708 | M410MOV1409 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1409-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969175709 | M410MOV1410 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | M410T014 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1410-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969175710 | M410MOV1451A | SUCTION Motor Operated Valve(Ball) OF 410-P014A | SUCTION Motor Operated Valve(Ball) OF 410-P-014A |  | MOV | M410P014A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1451A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/10/18 | ME-PM-002-M6
969175711 | M410MOV1452A | DISCHARGE Motor Operated Valve(Ball) OF 410-P014A | DISCHARGE Motor Operated Valve(Ball) OF 410-P-014A |  | MOV | M410P014A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1452A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
969175712 | M410MOV1453B | SUCTION Motor Operated Valve(Ball) OF 410-P014B | SUCTION Motor Operated Valve(Ball) OF 410-P-014B |  | MOV | M410P014B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1453B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/10/18 | ME-PM-002-M6
969166702 | M410P007A | MECHANICAL SEAL FOR ULG 91/95 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP | 969147446 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-7-Y1
969166703 | M410P007B | MECHANICAL SEAL FOR ULG 91/96 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP | 969147447 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 11/11/18 | MM-PM-7-Y1
969166704 | M410P007C | MECHANICAL SEAL FOR ULG 91/97 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP | 969147448 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007C-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 20/11/18 | MM-PM-7-Y1
969166705 | M410P008A | MECHANICAL SEAL(DE) FOR GAS OIL INTER-TANK TRANSFER PUMP MOTOR | GAS OIL INTER-TANK TRANSFER PUMP | 969147449 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-4-Y1
969166706 | M410P008B | MECHANICAL SEAL(DE) FOR GAS OIL INTER-TANK TRANSFER PUMP | GAS OIL INTER-TANK TRANSFER PUMP | 969147450 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 11/11/18 | MM-PM-4-Y1
969281610 | M410TSV099 | THERMAL RELIEF VALVE | THERMAL RELIEF VALVE |  | PSV | M410VALVE | 1 | PSV | 616101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281611 | M410P041A | DILUENT PUMP | DILUENT PUMP |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281612 | M410P041B | DILUENT PUMP | DILUENT PUMP |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281613 | M410PG621 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281614 | M410PG622 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281615 | M410PG623 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281616 | M410PG624 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281617 | M410PG625 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281618 | M410PG626 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281619 | M410PG631 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281620 | M410PG632 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363430 | M410FD655 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-024A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363431 | M410FD676 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363432 | M410FD677 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-03A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-03A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363433 | M410FD678 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363434 | M410FD679 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-003A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-003A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363435 | M410FD684 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363436 | M410FD685 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023C SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023C SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363437 | M410FD600 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-209 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-209 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363438 | M410FD601 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001D SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001D SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363439 | M410FD602 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-009 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-009 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363440 | M410FD603 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-209 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-209 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363441 | M410FD604 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363442 | M410FD605 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001D SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001D SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363443 | M410FD606 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001D NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-001D NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363444 | M410FD607 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-008 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-008 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363445 | M410FD608 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-008 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-008 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363446 | M410FD609 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-008 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-008 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363447 | M410FD610 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-206 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-206 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363448 | M410FD611 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-009 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-009 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363449 | M410FD612 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-009 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-009 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363450 | M410FD613 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-203 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-203 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363451 | M410FD614 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-0114 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-0114 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363452 | M410FD615 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-211 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-211 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363453 | M410FD616 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-401 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-401 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363454 | M410FD617 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-211 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-211 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363455 | M410FD618 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-005 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-005 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363456 | M410FD619 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-401 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-401 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363457 | M410FD620 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-401 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-401 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363458 | M410FD621 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-011B NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-011B NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363459 | M410FD622 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-005 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-005 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363460 | M410FD623 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-400 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-400 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363461 | M410FD624 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-400 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-400 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363462 | M410FD625 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-400 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-FT-400 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363463 | M410FD648 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-010 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-010 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363464 | M410FD649 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-002 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-002 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363465 | M410FD650 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-002 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-002 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363466 | M410FD651 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-010 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-ME-010 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363467 | M410FD656 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-040A WEST SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-040A WEST SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363468 | M410FD657 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-040B EAST SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-040B EAST SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363469 | M410FD658 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-002 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-002 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363470 | M410FD659 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-002 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-002 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363471 | M410FD660 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-001 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-001 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363472 | M410FD661 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-001 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-001 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363473 | M410FD662 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-006 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-006 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363474 | M410FD663 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-003 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-003 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363475 | M410FD664 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-003 NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-003 NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363476 | M410FD665 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-006 SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-PLR-006 SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363477 | M410FD674 | FLAME DETECTOR (UV/IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-005A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-L-005A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363478 | M410FD680 | FLAME DETECTOR (UV/IR TYPE) FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-001 NW SIDE | FLAME DETECTOR FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-001 NW SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363479 | M410FD681 | FLAME DETECTOR (UV/IR TYPE) FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-001 NE SIDE | FLAME DETECTOR FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-001 NE SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363480 | M410FD682 | FLAME DETECTOR (UV/IR TYPE) FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-003 SW SIDE | FLAME DETECTOR FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-003 SW SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363481 | M410FD683 | FLAME DETECTOR (UV/IR TYPE) FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-003 SE SIDE | FLAME DETECTOR FOR CHEMICAL INJECTION PACKAGE AREA ZONE-33 NEAR 410-ME-003 SE SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363482 | M410XGC601 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-FT-203 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-FT-203 |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363483 | M410XGC603 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-FT-211 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-FT-211 |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363484 | M410XGC604 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-ME-010 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-ME-010 |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363485 | M410XGC605 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-FT-400 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-FT-400 |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363486 | M410XGC606 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-005A | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-005A |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363487 | M410XGC607 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-005B | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-005B |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363488 | M410XGC608 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-005C | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-005C |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363489 | M410XGC609 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-001A | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-001A |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363490 | M410XGC610 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-001B | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-001B |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363491 | M410XGC613 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-023A | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-023A |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969418063 | PL300HPU3 | VALVE,SEQUENCIAL CONTROL/ESD, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE | HYDROLIC POWER UNIT IN SVS3 USED TO OPERATE 3 BALL VALVES,MP16"X900LB, NR10"X600LB, SRR12"X600LB. |  | SD_VLV | PL300SVS3 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969418061 | PL300HPU1 | VALVE,SEQUENCIAL CONTROL/ESD, GP-130C-485A/C3 (ROTORK), 89 - 126 KGF/CM2-G, 45 DEG C, ESD VLV MUSSAFFAH-TIE IN MP P/L, ASTM A182 F51, PNEUMATIC-PISTON, SPRING RETURN, BALL / ROTARY, ASTM A 694 F60, 10 INCH, 1500, TORMENE | HYDROLIC POWER UNIT IN SVS1 USED TO OPERATE 3 BALL VALVES,MP16"X900LB, NR10"X600LB, SRR12"X600LB. |  | SD_VLV | PL300SVS1 | 3 | VALVE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 1 | 50 | 50 | 5.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532786 | M400RVRV14A | RIM VENT RELIEF VALVE FOR TANK T-114 | RIM VENT RELIEF VALVE FOR TANK T-114 |  | PSV | M400T114 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532787 | M400RVRV14B | RIM VENT RELIEF VALVE FOR TANK T-114 | RIM VENT RELIEF VALVE FOR TANK T-114 |  | PSV | M400T114 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532788 | M400RVRV14C | RIM VENT RELIEF VALVE FOR TANK T-114 | RIM VENT RELIEF VALVE FOR TANK T-114 |  | PSV | M400T114 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532789 | M400RVRV14D | RIM VENT RELIEF VALVE FOR TANK T-114 | RIM VENT RELIEF VALVE FOR TANK T-114 |  | PSV | M400T114 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532790 | M400RVRV14E | RIM VENT RELIEF VALVE FOR TANK T-114 | RIM VENT RELIEF VALVE FOR TANK T-114 |  | PSV | M400T114 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532791 | M400RVRV15A | RIM VENT RELIEF VALVE FOR TANK T-115 | RIM VENT RELIEF VALVE FOR TANK T-115 |  | PSV | M400T115 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532792 | M400RVRV15B | RIM VENT RELIEF VALVE FOR TANK T-115 | RIM VENT RELIEF VALVE FOR TANK T-115 |  | PSV | M400T115 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532793 | M400RVRV15C | RIM VENT RELIEF VALVE FOR TANK T-115 | RIM VENT RELIEF VALVE FOR TANK T-115 |  | PSV | M400T115 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532794 | M400RVRV15D | RIM VENT RELIEF VALVE FOR TANK T-115 | RIM VENT RELIEF VALVE FOR TANK T-115 |  | PSV | M400T115 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532795 | M400RVRV15E | RIM VENT RELIEF VALVE FOR TANK T-115 | RIM VENT RELIEF VALVE FOR TANK T-115 |  | PSV | M400T115 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532796 | M400RVRV16A | RIM VENT RELIEF VALVE FOR TANK T-116 | RIM VENT RELIEF VALVE FOR TANK T-116 |  | PSV | M400T116 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532797 | M400RVRV16B | RIM VENT RELIEF VALVE FOR TANK T-116 | RIM VENT RELIEF VALVE FOR TANK T-116 |  | PSV | M400T116 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175713 | M410MOV1454B | DISCHARGE Motor Operated Valve(Ball) OF 410-P014B | DISCHARGE Motor Operated Valve(Ball) OF 410-P-014B |  | MOV | M410P014B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1454B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
969175714 | M410MOV1455 | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1455-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
969175715 | M410MOV1456 | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1456-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/10/18 | ME-PM-002-M6
969175716 | M410MOV1457 | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM | Motor Operated Valve(Ball) JET A-1 ITT SYSTEM |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1457-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/10/18 | ME-PM-002-M6
969175717 | M410MOV1501 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1501-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/10/18 | ME-PM-002-M6
969175718 | M410MOV1502 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1502-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969175719 | M410MOV1503 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1503-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969175720 | M410MOV1504 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1504-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/10/18 | ME-PM-002-M6
969175721 | M410MOV1505 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1505-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/10/18 | ME-PM-002-M6
969175722 | M410MOV1506 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1506-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/10/18 | ME-PM-002-M6
969175723 | M410MOV1507 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1507-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969175724 | M410MOV1508 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1508-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969175725 | M410MOV1509 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1509-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/11/18 | ME-PM-002-M6
969195410 | M410FLX001 | RUBBER FLEXIBLE HOSE(3” X 750L) | RUBBER FLEXIBLE HOSE(3” X 750L) |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195411 | M410HOS001 | RUBBER FLEXIBLE HOSE(1” X 15000L) | RUBBER FLEXIBLE HOSE(1” X 15000L) |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195412 | M410HOS010 | RUBBER FLEXIBLE HOSE(1” X 15000L) | RUBBER FLEXIBLE HOSE(1” X 15000L) |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195413 | M410HC001 | HOSE CONNECTOR(1") | HOSE CONNECTOR(1") |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195414 | M410HC010 | HOSE CONNECTOR(1") | HOSE CONNECTOR(1") |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195415 | M410QC001 | FLANGE HOSE CONNECTOR(3”X4” 150#) | FLANGE HOSE CONNECTOR(3”X4” 150#) |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195416 | M410QC029 | FLANGE HOSE CONNECTOR(3”X3” 150#) | FLANGE HOSE CONNECTOR(3”X3” 150#) |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195417 | M410EXP001 | 14" * 500L METALIC EXPANSION JOINT | 14" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195418 | M410EXP010 | 12" * 500L METALIC EXPANSION JOINT | 12" * 500L METALIC EXPANSION JOINT |  | VESSEL | M410MISC | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195420 | M410TEL001 | Telephone (Outdoor) | Telephone (Outdoor) |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195421 | M410TEL002 | Telephone (Outdoor) | Telephone (Outdoor) |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195422 | M410TEL003 | Telephone (Outdoor) | Telephone (Outdoor) |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195423 | M410TEL004 | Telephone (Outdoor) | Telephone (Outdoor) |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195424 | M410TEL005 | Telephone (Outdoor) | Telephone (Outdoor) |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195425 | M410TEL006 | Telephone (Outdoor) | Telephone (Outdoor) |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195426 | M410TEL007 | Telephone (Outdoor) | Telephone (Outdoor) |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195434 | M410TEL001BO | Booth | FIELD TELEPHONE -#1 |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195435 | M410TEL002BO | Booth | FIELD TELEPHONE -#2 |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195436 | M410TEL003BO | Booth | FIELD TELEPHONE -#3 |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195437 | M410TEL004BO | Booth | FIELD TELEPHONE -#4 |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195438 | M410TEL005BO | Booth | FIELD TELEPHONE -#5 |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195439 | M410TEL006BO | Booth | FIELD TELEPHONE -#6 |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195440 | M410TEL007BO | Booth | FIELD TELEPHONE -#7 |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195441 | M410TEL011 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195442 | M410TEL012 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195443 | M410TEL013 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195444 | M410TEL014 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195445 | M410TEL020 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195446 | M410TEL021 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195447 | M410TEL022 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195448 | M410TEL023 | Indoor Telephone | Indoor Telephone |  |  | M410TEL | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195449 | M410XJBS001 | Junction Box - Signal | Junction Box - Signal |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195450 | M410XJBS004 | Junction Box - Signal | Junction Box - Signal |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195451 | M410TO001 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195452 | M410TO002 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195453 | M410TO003 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195454 | M410TO004 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195455 | M410TO005 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195456 | M410TO006 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195457 | M410TO007 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195458 | M410TO008 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195459 | M410TO009 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195460 | M410TO010 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195461 | M410TO011 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195462 | M410TO012 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195463 | M410TO013 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195464 | M410TO014 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195465 | M410TO015 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195466 | M410TO016 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195467 | M410TO017 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195468 | M410TO018 | Telephone/Lan Outlet | Telephone/Lan Outlet |  |  | M410MISC | 3 | TELEPHON | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195469 | M410IDF001 | IDF | IDF |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195599 | M410ESDSC001 | SIS-001 ESD SYSTEM CABINET | SIS-001 ESD SYSTEM CABINET |  |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195600 | M410FACP001 | FIRE ALARM CONTROL PANEL | FIRE ALARM CONTROL PANEL IN THE SIS BUILDING. |  | F&G_PNL | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195601 | M410FACP002 | FIRE ALARM CONTROL PANEL | FIRE ALARM CONTROL PANEL IN IRP2 SUB STATION. |  | F&G_PNL | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195602 | M410FOPPSC001 | SIS-001 NETWORK CABINET | SIS-001 NETWORK CABINET |  |  | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195603 | M410GAP001 | GAS ALARM PANEL | GAS ALARM PANEL SIS BUILDING |  | BLDGS | M410SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195604 | M410GAV2353001 | 1/2" Class 800 Gate Valve | 1/2" Class 800 Gate Valve |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195507 | M410FU412 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195508 | M410FU413 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195509 | M410FU414 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195510 | M410FU415 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969486631 | M410PSV31E | PRESSURE SAFETY VALVE 18KG. | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P031E | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969486632 | M410PSV31F | PRESSURE SAFETY VALVE 18KG. | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P031F | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969486633 | M410PSV31G | PRESSURE SAFETY VALVE 18KG. | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P031G | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365164 | M410XHD657B | LINEAR HEAT DETECTOR FOR PUMP-007A AT ITTP AREA, ZONE-27 | LINEAR HEAT DETECTOR FOR PUMP-007A AT ITTP AREA, ZONE-27 |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969364632 | M410XHD604A | LINEAR HEAT DETECTOR FOR TANK-011 | LINEAR HEAT DETECTOR FOR TANK-015 |  | FGBHFD | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351354 | M410MP045A | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-045A | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-045A |  | MOTOR | M410P045B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP045A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969351355 | M410MP045B | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-045B | MOTOR FOR DYE (RED) DILUTED CHEMICAL INJECTION PUMPS 410-P-045B |  | MOTOR | M410P045B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP045B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969351356 | M410MP046A | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-046A | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-046A |  | MOTOR | M410P046A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP046A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969351357 | M410MP046B | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-046B | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-046B |  | MOTOR | M410P046B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP046B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969351358 | M410MP041A | MOTOR FOR CORROSION INHIBITOR (DILUTED CHEMICAL) INJECTION PUMPS 410-P-041A | MOTOR FOR CORROSION INHIBITOR (DILUTED CHEMICAL) INJECTION PUMPS 410-P-041A |  | MOTOR | M410P041A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP041A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969351359 | M410MP041B | MOTOR FOR CORROSION INHIBITOR (DILUTED CHEMICAL) INJECTION PUMPS 410-P-041B | MOTOR FOR CORROSION INHIBITOR (DILUTED CHEMICAL) INJECTION PUMPS 410-P-041B |  | MOTOR | M410P041B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP041B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969351367 | PL312EOV31203 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-03 | ELECTRO HYDRAULIC VALVE, SV STATION-3 | 969275348 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351368 | PL312EOV31204 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-04 | ELECTRO HYDRAULIC VALVE, SV STATION-4 | 969275349 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351369 | PL312EOV31205 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-05 | ELECTRO HYDRAULIC VALVE, SV STATION-5 | 969275350 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351370 | PL312EOV31206 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-06 | ELECTRO HYDRAULIC VALVE, SV STATION-6 | 969275351 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351371 | PL312EOV31301 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-01 | ELECTRO HYDRAULIC VALVE, SV STATION-1 | 969275352 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351372 | PL312EOV31302 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-02 | ELECTRO HYDRAULIC VALVE, SV STATION-2 | 969275353 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351373 | PL312EOV31303 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-03 | ELECTRO HYDRAULIC VALVE, SV STATION-3 | 969275354 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351374 | PL312EOV31304 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-04 | ELECTRO HYDRAULIC VALVE, SV STATION-4 | 969275355 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351375 | PL312EOV31305 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-05 | ELECTRO HYDRAULIC VALVE, SV STATION-5 | 969275356 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351376 | PL312EOV31306 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-313-06 | ELECTRO HYDRAULIC VALVE, SV STATION-6 | 969275357 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351377 | PL315EOV31513 | HPU FOR ELECTRO HYDRAULIC VALVE 315-EOV-315-13 | ELECTRO HYDRAULIC VALVE, SV STATION-13 | 969275358 | PACKAGE | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969361523 | M400FACP007 | WWTP PANEL,FIRE ALARM GENT VIGILON. | FIRE ALARM CONTROL PANEL GENT VAGILON WWTP. |  | F&G_PNL | M400WWTP | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 |  | M400FACP007-MFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 14/08/18 | MFPS-PM01.M6
969351378 | PL315EOV31613 | HPU FOR ELECTRO HYDRAULIC VALVE 315-EOV-316-13 | ELECTRO HYDRAULIC VALVE, SVSTATION-13 | 969275359 | PACKAGE | PL315VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351379 | PL318EOV31808 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | 969275360 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351380 | PL318EOV31809 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | 969275361 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351381 | PL318EOV31810 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | 969275362 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351382 | PL318EOV31811 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | 969275363 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351383 | PL318EOV31812 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | 969275364 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351384 | PL318EOV31908 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | 969275365 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351385 | PL318EOV31909 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | 969275366 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351386 | PL318EOV31910 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | 969275367 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351387 | PL318EOV31911 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | 969275368 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351388 | PL318EOV31912 | HPU FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | 969275369 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351389 | PL325EOV32507 | HPU FOR ELECTRO HYDRAULIC VALVE 325-EOV-325-07 | ELECTRO HYDRAULIC VALVE, SV STATION-07 | 969275370 | PACKAGE | PL325TELM | 2 | TELECOM | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969364583 | M410MP050AA | MOTOR FOR LUB OIL PUMP FOR 410P002A ALAIN. | MOTOR FOR LUB OIL PUMP FOR 410P002A ALAIN. |  | MOTOR | M410P050AA | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP050AA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364584 | M410MP050AB | MOTOR FOR LUB OIL PUMP FOR 410P002A ALAIN. | MOTOR FOR LUB OIL PUMP FOR 410P002A ALAIN. |  | MOTOR | M410P050AB | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP050AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364585 | M410MP050BA | MOTOR FOR LUB OIL PUMP FOR 410-P-002B PUMP | MOTOR FOR LUB OIL PUMP FOR 410-P-002B PUMP |  | MOTOR | M410P050BA | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP050BA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364586 | M410MP050BB | MOTOR FOR LUB OIL PUMP FOR 410-P-002B PUMP | MOTOR FOR LUB OIL PUMP FOR 410-P-002B PUMP |  | MOTOR | M410P050BB | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP050BB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364587 | M410MP051AA | MOTOR FOR LUB OIL PUMP FOR 410-P-004A PUMP | MOTOR FOR LUB OIL PUMP FOR 410-P-004A PUMP |  | MOTOR | M410P051AA | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP051AA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364588 | M410MP051AB | MOTOR FOR LUB OIL PUMP FOR 410-P-004A PUMP | MOTOR FOR LUB OIL PUMP FOR 410-P-004A PUMP |  | MOTOR | M410P051AB | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP051AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364589 | M410MP051BA | MOTOR FOR LUB OIL PUMP FOR 410-P-004B PUMP | MOTOR FOR LUB OIL PUMP FOR 410-P-004B PUMP |  | MOTOR | M410P051BA | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP051BA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364590 | M410MP051BB | MOTOR FOR LUB OIL PUMP FOR 410-P-004B PUMP | MOTOR FOR LUB OIL PUMP FOR 410-P-004B PUMP |  | MOTOR | M410P051BB | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP051BB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969364650 | M400XAC026 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT MAIN GUARD HOUSE ENTERANCE. |  | PB_HS-MC | M400FACP004 | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969364652 | M410XGC220 | DETECTOR, FLAMMABLE GAS, PORTABLE | FLAMMABLE GAS DETECTORS AT ITTP M400-P-025A |  | FG_DET | M400GACP001B | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969364653 | M410XGC221 | DETECTOR, FLAMMABLE GAS, PORTABLE | FLAMMABLE GAS DETECTORS AT ITTP M400-P-025A |  | FG_DET | M400GACP001B | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175167 | M410LT132 | JET A1 TANK 410-T-013 | EMERSON JET A1 LEVEL TRANSMITTER OF TANK 410-T-013 |  | LVL_TX | M410T013 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175168 | M410LT142 | JET A1 TANK 410-T-014 | EMERSON JET A1 LEVEL TRANSMITTER OF TANK 410-T-014 |  | LVL_TX | M410T014 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175169 | M410LT152 | JET A1 TANK 410-T-015 | EMERSON JET A1 LEVEL TRANSMITTER OF TANK 410-T-015 |  | LVL_TX | M410T015 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175170 | M410LT162 | JET A1 TANK 410-T-016 | EMERSON JET A1 LEVEL TRANSMITTER OF TANK 410-T-016 |  | LVL_TX | M410T016 | 1 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175568 | M410MOV0207 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0207-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
969175569 | M410MOV0208 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0208-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
969175570 | M410MOV0209 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0209-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/10/18 | ME-PM-002-M6
969175571 | M410MOV0210 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0210-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969175572 | M410MOV0211 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0211-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969175278 | M410PG001 | JET A1 FROM 410-T-011~016TO 410-P-005A/B | JET A1 FROM 410-T-011~016TO 410-P-005A/B |  | INDICATR | M410T011 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175279 | M410PG003 | JET A1 FROM 410-T-011~016TO AL DHAFRA BOOSTER PUMPS | JET A1 FROM 410-T-011~016TO AL DHAFRA BOOSTER PUMPS |  | INDICATR | M410T012 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175280 | M410PG004 | ULG 91 FROM PIPELINE MANIFOLDTO 410-T-001~004 | ULG 91 FROM PIPELINE MANIFOLDTO 410-T-001~004 |  | INDICATR | M410T001 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175281 | M410PG005 | ULG 95 FROM 410-T-005~008TO 410-P-001A/B | ULG 95 FROM 410-T-005~008TO 410-P-001A/B |  | INDICATR | M410T005 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175282 | M410PG006 | JET A1 FROM PIPELINE TO410-T-011~016 | JET A1 FROM PIPELINE TO410-T-011~016 |  | INDICATR | M410T013 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175283 | M410PG011 | ULG 95 FROM PIPELINE MANIFOLDTO 410-T-005~008 | ULG 95 FROM PIPELINE MANIFOLDTO 410-T-005~008 |  | INDICATR | M410T006 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175284 | M410PG012 | ULG 91 FROM 410-T-001~004TO 410-P-001A/B | ULG 91 FROM 410-T-001~004TO 410-P-001A/B |  | INDICATR | M410T002 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175285 | M410PG013 | ULG 91 FROM 410-T-001~004TO ROAD TANKER LOADING PUMP | ULG 91 FROM 410-T-001~004TO ROAD TANKER LOADING PUMP |  | INDICATR | M410T003 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175286 | M410PG015 | ULG 95 FROM 410-T-005~008TO ROAD TANKER LOADING PUMP | ULG 95 FROM 410-T-005~008TO ROAD TANKER LOADING PUMP |  | INDICATR | M410T006 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175287 | M410PG016 | GAS OIL FROM 410-T-009/010TO 410-P-003A/B | GAS OIL FROM 410-T-009/010TO 410-P-003A/B |  | INDICATR | M410T009 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175114 | M410LT154B | LEVEL TRANSMITTER JET A1 TANK 410T015 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T015 |  | LVL_TX | M410T015 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175115 | M410LT164A | LEVEL TRANSMITTER JET A1 TANK 410T016 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T016 |  | LVL_TX | M410T016 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175116 | M410LT164B | LEVEL TRANSMITTER JET A1 TANK 410T016 | AGAR LEVEL TRANSMITTER JET A1 TANK 410T016 |  | LVL_TX | M410T016 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175124 | M410FT450C | 410-L-004C OUTLET | JET A1 INTER-TANK TRANSFER FILTER 410-L-004C OUTLET |  | DP_TXTR | M410L004C | 3 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175125 | M410FT701A | 410-P-007A DISCHARGE | FLOW TX ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007A DISCHARGE |  | DP_TXTR | M410P007A | 3 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175126 | M410FT702B | 410-P-007B DISCHARGE | FLOW TX ULG 91/95 INTER-TANK TRANSFER PUMP 410-P-007B DISCHARGE |  | DP_TXTR | M410P007B | 3 | DP_TXTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195256 | M410ELP001 | Small Power Distribution Board | Small Power Distribution Board |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410ELP001-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 12/01/19 | ME-PNL1-PM-M6
969175128 | M410LT155 | KROHNE ULG/GAS OIL SUMP VESSEL 410-V-003 | ULG/GAS OIL SUMP VESSEL 410V003 |  | LVL_TX | M410V003 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175129 | M410LT156 | ULG/GAS OIL SUMP VESSEL 410-V-003 | ULG/GAS OIL SUMP VESSEL 410V003 |  | LVL_TX | M410V003 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175130 | M410LT157 | JET A1 SUMP VESSEL 410-V-004 | JET A1 SUMP VESSEL 410V004 |  | LVL_TX | M410V004 | 3 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195488 | M410FU333 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195489 | M410FU334 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195490 | M410FU335 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195491 | M410FU336 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195492 | M410FU337 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195493 | M410FU338 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195494 | M410FU339 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195495 | M410FU340 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195496 | M410FU401 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR OF 410T012. |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195497 | M410FU402 | HYDRANT WITH MONITOR | HYDRANT WITH MONITOR |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195470 | M410FU315 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195471 | M410FU316 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195713 | M410FG080 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195714 | M410FG081 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195715 | M410FG083 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195716 | M410FG084 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195717 | M410FG085 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195718 | M410FG086 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195719 | M410FG087 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195720 | M410FG088 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195721 | M410FG089 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195722 | M410FG090 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195723 | M410FG091 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195724 | M410FG092 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195725 | M410FG093 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195726 | M410FG094 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195727 | M410FG095 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195728 | M410FG096 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195729 | M410FG097 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195730 | M410FG098 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195731 | M410FG099 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195732 | M410FG100 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195733 | M410FG101 | 3" 150# RF Flow Glass | 3" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195734 | M410FG102 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195735 | M410FG103 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195736 | M410FG104 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195737 | M410FG105 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195738 | M410FG106 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195739 | M410FG107 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195740 | M410FG108 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195741 | M410FG109 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195742 | M410FG110 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195743 | M410FG111 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195744 | M410FG112 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195745 | M410FG113 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195746 | M410FG114 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195747 | M410FG115 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195748 | M410FG116 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195749 | M410FG117 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195750 | M410FG118 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195751 | M410FG119 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195752 | M410FG120 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195753 | M410FG121 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195754 | M410FG122 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195755 | M410FG123 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195756 | M410FG124 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195757 | M410FG125 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195758 | M410FG126 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195759 | M410FG127 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195760 | M410FG128 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195761 | M410FG129 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195762 | M410FG130 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195763 | M410FG131 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195764 | M410FG132 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195765 | M410FG133 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195766 | M410FG134 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195767 | M410FG135 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195768 | M410FG136 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195769 | M410FG137 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195770 | M410FG138 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195771 | M410FG139 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195772 | M410FG140 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195773 | M410FG141 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195774 | M410FG142 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195775 | M410FG143 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195776 | M410FG144 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195777 | M410FG145 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195778 | M410FG146 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195779 | M410FG147 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195780 | M410FG148 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195781 | M410FG149 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195782 | M410FG150 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195783 | M410FG151 | 1" 150# RF Flow Glass | 1" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195784 | M410FG152 | 2" 150# RF Flow Glass | 2" 150# RF Flow Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195785 | M410PACB001 | PAGA CABINET | PUBLIC ADDRESS GENERAL ALARM CABINET MCR TELECOM ROOM |  |  | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184871 | M410MS00117A | 3.3KV Switchgear Panel | SPARE MOTOR FEEDER PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410MS00117A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184872 | M410MS00118A | 3.3KV Switchgear Panel | SPARE NON MOTOR FEEDER PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410MS00118A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184873 | M410MS001AB | 3.3KV Switchgear Panel | BUS SECTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS001AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184874 | M410MS0011AB | 3.3KV Switchgear Panel | BUS RISER PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0011AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184875 | M410MS0011B | 3.3KV Switchgear Panel | MAIN INCOMING PANEL-B |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0011B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184876 | M410MS001B | 3.3KV Switchgear Panel | BUS-B VT PANEL(3.3KV/SQRT3/110/SQRT3) |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS001B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184877 | M410MS0012B | 3.3KV Switchgear Panel | PANEL FOR MUS-ALAIN ULG MAINLINE PUMP-B(410-MP-002B)-950KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0012B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184878 | M410MS0013B | 3.3KV Switchgear Panel | PANEL FOR MUS-ALN GAS OIL MAINLINE PUMP-B(410-MP-004B)-950KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0013B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184879 | M410MS0014B | 3.3KV Switchgear Panel | DUMMY PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410MS0014B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184880 | M410MS0015B | 3.3KV Switchgear Panel | PANEL FOR MUS-ADIA JET A1 MAINLINE PUMP-B(410-MP-006B)-550KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0015B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184881 | M410MS0016B | 3.3KV Switchgear Panel | PANEL FOR MUS-ALD JET A1 LINE PUMP-B(410-MP-024B)-160KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0016B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184882 | M410MS0017B | 3.3KV Switchgear Panel | PANEL FOR MUS-ADIA JET A1 BOOSTER PUMP-B(410-MP-005B)-250KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0017B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184883 | M410MS0018B | 3.3KV Switchgear Panel | PANEL FOR ULG 91/95 INTER-TANK TRANSFER PUMP-B(410-MP-007B)-150KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0018B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184884 | M410MS0019B | 3.3KV Switchgear Panel | PANEL FOR GAS OIL INTER-TANK TRANSFER PUMP-B(410-MP-008B)-200KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS0019B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184885 | M410MS00110B | 3.3KV Switchgear Panel | PANEL FOR JET A1 INTER-TANK TRANSFER PUMP-B(410-MP-014B)-200KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00110B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184886 | M410MS00111B | 3.3KV Switchgear Panel | DUMMY PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00111B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184887 | M410MS00112B | 3.3KV Switchgear Panel | PANEL FOR FIRE WATER PUMP MOTOR DRIVEN-B(410-FWCP-032B)-450KW |  | SWBOARD | M410SCB | 1 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MS00112B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184888 | M410MS00113B | 3.3KV Switchgear Panel | PANEL FOR 3.3KV POWER CAPACITOR BANK-B(410-PFI-001B) |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00113B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184889 | M410MS00114B | 3.3KV Switchgear Panel | PANEL FOR MUS-ALDHAFRA JET A1 MAINLINE PUMP-C(410-MP-024C)-160KW |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MS00114B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184890 | M410MS00115B | 3.3KV Switchgear Panel | SPARE NON MOTOR FEEDER PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410MS00115B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184891 | M410PC0011A | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC0011A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184892 | M410PC0012A | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC0012A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184893 | M410PC0013A | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC0013A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184894 | M410PC001AB | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC001AB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184895 | M410PC0011B | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC0011B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184896 | M410PC0012B | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC0012B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184897 | M410PC0013B | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC0013B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184898 | M410PC001BE | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC001BE-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184899 | M410PC0011E | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC0011E-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184900 | M410PC001MCCA | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC001MCCA-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184901 | M410PC001MCCB | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC001MCCB-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184902 | M410PC001MCCE | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PC001MCCE-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184903 | M410HVAC001 | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410HVAC001-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184904 | M410HVAC002 | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410HVAC002-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184905 | M410HVAC003 | 415V Switchgear and MCC | 415V Switchgear and MCC |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410HVAC003-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969184906 | M410CPTCPT001 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT001-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 07/12/18 | ME-PM-008-Y1
969184907 | M410CPTCPT002 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT002-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 08/12/18 | ME-PM-008-Y1
969184908 | M410CPTCPT003 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT003-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 09/12/18 | ME-PM-008-Y1
969184909 | M410CPTCPT004 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT004-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 10/12/18 | ME-PM-008-Y1
969184910 | M410CPTCPT005 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT005-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 11/12/18 | ME-PM-008-Y1
969184911 | M410CPTCPT006 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT006-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 12/12/18 | ME-PM-008-Y1
969184912 | M410CPTCPT007 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT007-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 13/12/18 | ME-PM-008-Y1
969184913 | M410CPTCPT008 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT008-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 14/12/18 | ME-PM-008-Y1
969184914 | M410CPTCPT009 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT009-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 15/12/18 | ME-PM-008-Y1
969184915 | M410CPTCPT010 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT010-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 16/12/18 | ME-PM-008-Y1
969184916 | M410CPTCPT011 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT011-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 17/12/18 | ME-PM-008-Y1
969184917 | M410CPTCPT012 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT012-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 18/12/18 | ME-PM-008-Y1
969184918 | M410CPTCPT013 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT013-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 19/12/18 | ME-PM-008-Y1
969184919 | M410CPTCPT014 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT014-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 20/12/18 | ME-PM-008-Y1
969184920 | M410CPTCPT015 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT015-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 21/12/18 | ME-PM-008-Y1
969184921 | M410CPTCPT016 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT016-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 22/12/18 | ME-PM-008-Y1
969184922 | M410CPTCPT051A | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT051A-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 23/12/18 | ME-PM-008-Y1
969184923 | M410CPTCPT051B | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT051B-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 24/12/18 | ME-PM-008-Y1
969184924 | M410CPTCPT052A | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT052A-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 25/12/18 | ME-PM-008-Y1
969184925 | M410CPTCPT052B | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPT052B-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 26/12/18 | ME-PM-008-Y1
969184926 | M410CPTCPU001 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPU001-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 27/12/18 | ME-PM-008-Y1
969184927 | M410CPTCPU002 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPU002-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 28/12/18 | ME-PM-008-Y1
969184928 | M410CPTCPU003 | Cathodic Protection System | Cathodic Protection System |  | CATHPRO | M410CPRX | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410CPTCPU003-ME1 | ACTIVE | ELEC | PM | FIC | 1 | YEARS | 29/12/18 | ME-PM-008-Y1
969185917 | M410PSV002 | VALVE,SAFETY RELIEF | Jet A1 Inter-Tank Transfer Filter Coalescers |  | PSV | M410L004B | 1 | PSV | 617101-310600 | IRPMTERMINAL | NOT READY | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969184929 | M410AHU101A | HVAC SYSTEM | HVAC SYSTEM |  | HVAC_FLT | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969185916 | M410PSV001 | VALVE,SAFETY RELIEF | Jet A1 Inter-Tank Transfer Filter Coalescers |  | PSV | M410L004A | 1 | PSV | 617101-310600 | IRPMTERMINAL | NOT READY | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265911 | PL100MOV401 | Ruwais Shweihat Gas oil Scrapper Receiver 100-PL-002 | Ruwais Shweihat Gas oil Scrapper Receiver 100-PL-002 |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV401-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265912 | PL100MOV402 | Ruwais Shweihat Gas oil Scrapper Receiver 100-PL-002 | Ruwais Shweihat Gas oil Scrapper Receiver 100-PL-002 |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV402-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265913 | PL100MOV403A | Gas oil P/L From Scrapper Receiver 100-V-001A Inlet | Gas oil P/L From Scrapper Receiver 100-V-001A Inlet |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV403A-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265914 | PL100MOV403B | Gas oil P/L From Scrapper Receiver 100-V-001B Inlet | Gas oil P/L From Scrapper Receiver 100-V-001B Inlet |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV403B-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265915 | PL100MOV404A | Gas oil P/L From Scrapper Receiver 100-V-001A Outlet | Gas oil P/L From Scrapper Receiver 100-V-001A Outlet |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV404A-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265916 | PL100MOV404B | Gas oil P/L From Scrapper Receiver 100-V-001B Outlet | Gas oil P/L From Scrapper Receiver 100-V-001B Outlet |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV404B-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265917 | PL100PA00120A | SPLIT TYPE AIR CONDITIONER | SPLIT TYPE AIR CONDITIONER |  | HVAC | PL100HVAC | 3 | HVAC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265923 | PL100PDT400B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265924 | PL100PDT405A | DIFF.PRESSURE TRANSMITTER | DIFF.PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265925 | PL100PDT405B | DIFF.PRESSURE TRANSMITTER | DIFF.PRESSURE TRANSMITTER |  | PRES_TX | PL100PRESS | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265926 | PL100PG150 | PRESSURE GAUGE -1~2kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE -1~2kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265927 | PL100PG151 | PRESSURE GAUGE -1~2kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE -1~2kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265928 | PL100PG400AA | Pressure Gauge | Pressure Gauge |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265929 | PL100PG400AB | Pressure Gauge | Pressure Gauge |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265930 | PL100PG400BA | Pressure Gauge | Pressure Gauge |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265931 | PL100PG400BB | Pressure Gauge | Pressure Gauge |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265932 | PL100PG406 | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265934 | PL100PG408 | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS | PRESSURE GAUGE 0~15kg/cm2g, 100mm, Direct reading, 316SS |  | INDICATR | PL100PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969527924 | PL100HSSD701 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HIGHLY SENSITIVE SMOKE DETECTION SYSTEM AT SHUWEIHAT, INST. EQUIPMENT ROOM |  | FGBFFD | PL100FACP620 | [14 empty] | High Critical | Y | High Critical | Y |  | 6 | g
969527925 | PL100HSSD702 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HIGHLY SENSITIVE SMOKE DETECTION SYSTEM AT SHUWEIHAT, UPS ROOM |  | FGBFFD | PL100FACP620 | [14 empty] | High Critical | Y | High Critical | Y |  | 6 | g
969527921 | M410FU009ICP | FIRE SUPPRESSION PANEL AT MCM ROOM - S/S-II | FIRE SUPPRESSION PANEL AT MCM ROOM - S/S-II |  | F&G_PNL | M410SS | [14 empty] | High Critical | Y | High Critical | Y |  | 6 | g
969195472 | M410FU317 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195473 | M410FU318 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195474 | M410FU319 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195475 | M410FU320 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195476 | M410FU321 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195477 | M410FU322 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195478 | M410FU323 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195479 | M410FU324 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195480 | M410FU325 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269694 | M410MP035B | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-035B | MOTOR FOR DYE(GREEN) DILUTED CHEMICAL INJECTION PUMPS 410-P-035B |  | MOTOR | M410P035B | 3 | MOTOR | 615101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP035B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269695 | M410P037 | 95 OCT GREEN DYE INJECTION RECIPROCATING PUMP. | 95 OCT PUMP GREEN DYE INJECTION 400ME002. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269696 | M410PSV701 | PRESSURE SAFETY VALVE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 | PRESSURE SAFETY VALVE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 |  | PACKAGE | M400ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269697 | M410PSV702 | PRESSURE SAFETY VALVE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 | PRESSURE SAFETY VALVE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 |  | PACKAGE | M400ME002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269698 | M410XV701 | PNEUMATIC VAVLE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 | PNEUMATIC VAVLE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 |  | PACKAGE | M400ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269699 | M410XV702 | PNEUMATIC VAVLE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 | PNEUMATIC VAVLE FOR DYE(GREEN) INJECTION PACKAGE 400-ME-002 FOR ULG 95 |  | PACKAGE | M400ME002 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269700 | M410PSV711 | PRESSURE SAFETY VALVE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 | PRESSURE SAFETY VALVE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 |  | PACKAGE | M400ME003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269701 | M410PSV712 | PRESSURE SAFETY VALVE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 | PRESSURE SAFETY VALVE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 |  | PACKAGE | M400ME003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269702 | M410XV711 | PNEUMATIC VAVLE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 | PNEUMATIC VAVLE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 |  | PACKAGE | M400ME003 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269703 | M410XV712 | PNEUMATIC VAVLE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 | PNEUMATIC VAVLE FOR DYE(RED) INJECTION PACKAGE 400-ME-003 FOR ULG 91 |  | PACKAGE | M400ME003 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269704 | M410P038 | DIAPHRAGM RECIPROCATING PUMP. | OFF LOADING RED DYE DIAPHRAGM PUMP ON 400ME003. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269705 | M410MP001A | ELECTRIC MOTOR LOW VOLTAGE CAGE-INDUCTION FOR ULG 98 ROAD TANKER LOADING PUMPS | ELECTRIC MOTOR LOW VOLTAGE CAGE-INDUCTION FOR ULG 98 ROAD TANKER LOADING PUMPS |  | MOTOR | M410P001A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP001A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269706 | M410MP001B | ELECTRIC MOTOR LOW VOLTAGE CAGE-INDUCTION FOR ULG 98 ROAD TANKER LOADING PUMPS | ELECTRIC MOTOR LOW VOLTAGE CAGE-INDUCTION FOR ULG 98 ROAD TANKER LOADING PUMPS |  | MOTOR | M410P001B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP001B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269707 | M410ELP102 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP102-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269708 | M410SSW001 | Emergency Safety Shower & Eyewash | Emergency Safety Shower & Eyewash |  | F&G_PNL | M410MISC | 1 | F&G_PNL | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269709 | M410VH004 | EOT Crane & Monorail Hoist | EOT Crane & Monorail Hoist |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH004-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269710 | M410VH005 | EOT Crane & Monorail Hoist | EOT Crane & Monorail Hoist |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH005-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269711 | M410ESDMC003 | ESD MARSHALLING CABINET FOR SIS-001 ESD SYSTEM | ESD MARSHALLING CABINET FOR SIS-001 ESD SYSTEM |  | BLDGS | M410MISC | 1 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269712 | M410ESDMC004 | ESD MARSHALLING CABINET FOR SIS-001 ESD SYSTEM | ESD MARSHALLING CABINET FOR SIS-001 ESD SYSTEM |  | BLDGS | M410MISC | 1 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269713 | M410ESDSC002 | CORROSION PROBE | ESD SYSTEM CABINET FOR SIS-001 ESD SYSTEM |  | BLDGS | M410MISC | 1 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269714 | M410LP101 | Ex Lighting Distribution Panel | Ex Lighting Distribution Panel |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410LP101-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269715 | M410LP102 | Ex Lighting Distribution Panel | Ex Lighting Distribution Panel |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410LP102-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269716 | M410LP103 | Ex Lighting Distribution Panel | Ex Lighting Distribution Panel |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410LP103-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269717 | M410PP101 | Ex Lighting Distribution Panel | Ex Lighting Distribution Panel |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410PP101-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269718 | M410MVP030 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP030-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269719 | M410MVP031 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP031-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269720 | M410MVP032 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP032-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269721 | M410MVP033 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP033-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269722 | M410MVP034 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP034-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269723 | M410MVP035 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP035-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269724 | M410MVP036 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP036-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269725 | M410MVP037 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP037-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269726 | M410MVP038 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP038-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269727 | M410MVP039 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP039-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269728 | M410MVP040 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP040-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269729 | M410MVP041 | EX MOV PANEL | EX MOV PANEL |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MVP041-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269730 | M410COP101 | Ex Power Distribution Panel | Ex Power Distribution Panel |  | BLDGS | M410SCB | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410COP101-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PNL1-PM-M6
969269731 | M410FGMC006 | F&G MARSHALLING CABINET, MUSSAFAH F&G SYSTEM | F&G MARSHALLING CABINET, MUSSAFAH F&G SYSTEM |  | BLDGS | M410MISC | 1 | F&G_PNL | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269732 | M410FGMC007 | F&G MARSHALLING CABINET, MUSSAFAH F&G SYSTEM | F&G MARSHALLING CABINET, MUSSAFAH F&G SYSTEM |  | BLDGS | M410MISC | 1 | F&G_PNL | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269733 | M410FGSC002 | FGS System Panel | FIRE and GAS SYSTEM, TMR PANEL IRP-II - SIS BUILDING |  | BLDGS | M410SCB | 1 | F&G_PNL | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269734 | M410FFE2101303 | Fire hose reel with cabinet(Out door) | Fire hose reel with cabinet(Out door) |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269735 | M410HYD2101301 | Fire Hydrant | Fire Hydrant |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269736 | M410FFE2101301 | Fire Monitor | Fire Monitor |  | F&G_PNL | M410MISC | 1 | F&G_PNL | 617101-310510 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269737 | M410FFE2101304 | Fire Point | Fire Point |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269738 | M410T053 | FIRE WATER Storage Tanks | FIRE WATER Storage Tanks |  | VESSEL | M410FIRE | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 50 | 5 | 50 | 10 | 5 | 6.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269739 | M410FHL2150 | FIXTURE HID LIGHT | FIXTURE HID LIGHT |  | LIGHT | M410SCB | 3 | LIGHT | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269740 | M410FD626 | FLAME DETECTOR (IR TYPE) | FLAME DETECTOR FOR MAIN PUMP HOUSE and SCRAPPER AREA NEAR 410-P-005A NORTH SIDE |  | FGBFFD | M410GD | 1 | FGBFFD | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269923 | M410VH007 | Monorail Hoist for Instrument Air Dryer | Monorail Hoist for Instrument Air Dryer |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH007-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269924 | M410VH008 | Monorail Hoist for DyeInjection Package | Monorail Hoist for DyeInjection Package |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH008-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269925 | M410VH009A | Monorail Hoists for Chemical Injection Packages | Monorail Hoists for Chemical Injection Packages |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH009A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269926 | M410VH009B | Monorail Hoists for Chemical Injection Packages | Monorail Hoists for Chemical Injection Packages |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH009B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269927 | M410VH009C | Monorail Hoists for Chemical Injection Packages | Monorail Hoists for Chemical Injection Packages |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH009C-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269928 | M410VH006A | Monorail Hoists for Instrument Air Compressor | Monorail Hoists for Instrument Air Compressor. |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH006A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269929 | M410VH006B | Monorail Hoists for Instrument Air Compressor | Monorail Hoists for Instrument Air Compressor |  | CRANE | M410AUTO | 3 | CRANE | 617101-310600 | MTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410VH006B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-007-M6
969269930 | M410MP003A | Electric Motor LV Cage-Induction - Hazardous Area | MOTOR FOR MUSSAFAH-ALAIN GAS OIL BOSSTER PUMP 3-A |  | MOTOR | M410P003A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP003A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269931 | M410MP003B | Electric Motor LV Cage-Induction - Hazardous Area | MOTOR FOR MUSSAFAH-ALAIN GAS OIL BOSSTER PUMP 3-B |  | MOTOR | M410P003B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP003B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269932 | M410MOV115 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV115-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269933 | M410MOV125 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV125-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/06/19 | ME-PM-002-M6
969269934 | M410MOV161A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV161A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269935 | M410MOV161B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV161B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269936 | M410MOV162A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P001A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV162A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269937 | M410MOV162B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P001B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV162B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269938 | M410MOV163A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P005A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV163A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269939 | M410MOV163B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P005B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV163B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269940 | M410MOV163C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P005C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV163C-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269941 | M410MOV164A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P005A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV164A-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269942 | M410MOV164B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P005B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV164B-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269943 | M410MOV164C | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P005C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV164C-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269944 | M410MOV184 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV184-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269945 | M410MOV190 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV190-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269946 | M410MOV203AA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT203A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV203AA-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
969269947 | M410MOV203AB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT203A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269948 | M410MOV203BA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT203B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269949 | M410MOV203BB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT203B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269950 | M410MOV206AA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT206A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269951 | M410MOV206AB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT206A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269952 | M410MOV206BA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT206B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269953 | M410MOV206BB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT206B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269954 | M410MOV209AA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT209A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269955 | M410MOV209AB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT209A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269956 | M410MOV209BA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT209B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269957 | M410MOV209BB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT209B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269958 | M410MOV211AA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT211A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269959 | M410MOV211AB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT211A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269960 | M410MOV211BA | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT211B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269961 | M410MOV211BB | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410FT211B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269962 | M410MOV218 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269963 | M410MOV219 | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 4 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269964 | M410MOV222A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P002A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269965 | M410MOV222B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P002B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269966 | M410MOV223A | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P002A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269967 | M410MOV223B | MOTOR OPERATED VALVE | MOTOR OPERATED VALVE |  | MOV | M410P002B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270157 | M410PG275 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L008A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270158 | M410PG284 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P002A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270159 | M410PG285 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P002A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270160 | M410PG286 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P002B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270161 | M410PG287 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P002B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270162 | M410PG294 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P003A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270163 | M410PG295 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P003A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270164 | M410PG296 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P003B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270165 | M410PG297 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P003B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270166 | M410PG298 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L009A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270167 | M410PG299 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L009A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270168 | M410PG307 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P004A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270169 | M410PG308 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P004A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270170 | M410PG309 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P004B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270171 | M410PG310 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P004B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270172 | M410PG317 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270173 | M410PG318 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270174 | M410PG319 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270175 | M410PG320 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270176 | M410PG321 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270177 | M410PG322 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270178 | M410PG329 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P006A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270179 | M410PG330 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P006A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270180 | M410PG331 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P006B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270181 | M410PG332 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P006B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270182 | M410PG340 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270183 | M410PG341 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270184 | M410PG342 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270185 | M410PG343 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270186 | M410PG344 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270187 | M410PG345 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270188 | M410PG346 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270189 | M410PG347 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270190 | M410PG348 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P023A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270191 | M410PG386 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P024A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270192 | M410PG387 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P024A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270193 | M410PG388 | PRESSURE GAUGE | PRESSURE GAUGE OF PUMP 410-P-24B. |  | INDICATR | M410P024B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270194 | M410PG389 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P024B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270195 | M410PG390 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L008A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270196 | M410PG391 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P001A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270197 | M410PG392 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P003A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270198 | M410PG393 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270199 | M410PG394 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P024C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270200 | M410PG395 | PRESSURE GAUGE | PRESSURE GAUGE OF PUMP 410-P-24C |  | INDICATR | M410P024C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270201 | M410PG396 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P006C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270202 | M410PG397 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P006C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270203 | M410PG399 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P005C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270204 | M410PG404 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PT412 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270205 | M410PG405 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270206 | M410PG406 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270207 | M410PG407 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270208 | M410PG408 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270209 | M410PG409 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270210 | M410PG410 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270211 | M410PG417 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PT412 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270212 | M410PG418 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PT412 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270213 | M410PG419 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PT412 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270214 | M410PG420 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PT412 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270215 | M410PG422 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L006A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270216 | M410PG423 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L006A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270217 | M410PG428 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR005 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270218 | M410PG429 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR005 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270219 | M410PG430 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR005 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270220 | M410PG431 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR005 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270221 | M410PG434 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR006 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270222 | M410PG436 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR006 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270223 | M410PG437 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR006 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270224 | M410PG438 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR006 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270225 | M410PG444 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270226 | M410PG445 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270227 | M410PG446 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270228 | M410PG447 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270229 | M410PG451 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P040A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270230 | M410PG452 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P040A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270231 | M410PG453 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P040B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270232 | M410PG454 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410P040B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270233 | M410PG459A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L011A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270234 | M410PG459B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L011B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270235 | M410PG464 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR007 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270236 | M410PG465 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR007 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270237 | M410PG466 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR007 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270238 | M410PG467 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PLR007 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270239 | M410PG477 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270240 | M410PG478 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270241 | M410PG479 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270242 | M410PG480 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270243 | M410PG481 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270244 | M410PG482 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L001A | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270245 | M410PG483 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L001B | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270246 | M410PG484 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L001C | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270247 | M410PG485 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410L001D | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270248 | M410PG101A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270249 | M410PG101B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270250 | M410PG102A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270251 | M410PG102B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410PRESS | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270252 | M410PG103A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270253 | M410PG103B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270254 | M410PG104A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270255 | M410PG104B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270256 | M410PG105A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270257 | M410PG105B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR |  | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270258 | M410PG106A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410ME106 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270259 | M410PG106B | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410ME106 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270260 | M410PG107A | PRESSURE Gauge FOR DELUGE VALVE SKID | PRESSURE Gauge FOR DELUGE VALVE SKID |  | INDICATR | M410ME107 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932906 | AT800BD0311051XV | INDICATOR SIGHT FLOW | SIGHT FLOW INDICATOR, SIZE-2" |  |  | AT800FLOW | 3 | SIGHT_GL | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932907 | PL301CCP001 | SYSTEM | CORROSION MONITORING SYSTEM- NAPHTHA / REFORMATE |  |  | PL301SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932908 | PL301CCP002 | SYSTEM | CORROSION MONITORING SYSTEM-NAPHTHA / REFORMATE |  |  | PL301SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932909 | PL301CP001 | SYSTEM | CORROSION MONITORING SYSTEM-NAPHTHA / REFORMATE |  |  | PL301SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932910 | PL301CP002 | SYSTEM | CORROSION MONITORING SYSTEM-NAPHTHA / REFORMATE |  |  | PL301SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932911 | PL302CCP001 | SYSTEM | CORROSION MONITORING SYSTEM-SRR |  |  | PL302SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932912 | PL302CCP002 | SYSTEM | CORROSION MONITORING SYSTEM-SRR |  |  | PL302SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932913 | PL302CP001 | SYSTEM | CORROSION MONITORING SYSTEM-SRR |  |  | PL302SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932914 | PL302CP002 | SYSTEM | CORROSION MONITORING SYSTEM-SRR |  |  | PL302SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932915 | PL303CCP001 | SYSTEM | CORROSION MONITORING SYSTEM-MP |  |  | PL303SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932916 | PL303CP001 | SYSTEM | CORROSION MONITORING SYSTEM-MP |  |  | PL303SYS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932917 | PL304CCP001 | SYSTEM | CORROSION MONITORING SYSTEM-MP |  |  | PL304SYS | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932918 | PL304CP001 | SYSTEM | CORROSION MONITORING SYSTEM-MP |  |  | PL304SYS | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932919 | PL305CCP001 | SYSTEM | CORROSION MONITORING SYSTEM-JET A1 |  |  | PL305SYS | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932920 | PL305CP001 | SYSTEM | CORROSION MONITORING SYSTEM-JET A1 |  |  | PL305SYS | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932921 | AA136BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 6" |  | VALVE | AA13VALVE | 3 | VALVE | 617101-310600 | IRPALAIN | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932924 | M40010BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 10" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932925 | M40012BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 12" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932926 | M40016BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 16" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932927 | M40018BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 18" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932928 | M40020BU392 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 20" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932929 | M40024BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 24" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932930 | M40026BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 26" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932931 | M4008BU391 | VALVE, BUTTERFLY | FIRE WATER BUTTERFLY VALVE 8" |  | VALVE | M400VALVE | 1 | VALVE | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 10 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932932 | M400ME001 | ANTISTATIC CHEMICAL DOSING PACKAGE FOR JET A1 – SKID | ANTISTATIC CHEMICAL DOSING PACKAGE FOR JET A1 – SK |  | PACKAGE | M400CINJ | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932933 | M400ME002 | DYE INJECTION SKID PACKAGE FOR ULG-95 | TANK GREEN DYE INJECTION IN ULG-95. |  | PACKAGE | M400CINJ | 3 | PACKAGE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933554 | M400MOV552 | ACTUATOR,ELECTRIC MOTOR, OFF SPEC. JET A1, 143, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 900, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR 400-P-019 DISCHARGE LINE (OFF SPEC. JET A1, 10" X 8" CL 900) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV552-ME1 | INACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/07/18 | ME-PM-002-M6
933555 | M400MOV566 | ACTUATOR,ELECTRIC MOTOR, SRR / GO, 94, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 34 SEC, 12" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR BATTERY LIMIT RECEIVER (SRR / GO, 12" CL 600 WITH STEM EXTENSION) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV566-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
933556 | M400MOV567 | ACTUATOR,ELECTRIC MOTOR, SRR / GO, 94, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 34 SEC, 12" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR ISOLATION VALVE RECEIVER(SRR / GO, 12" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV567-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
933557 | M400MOV568 | ACTUATOR,ELECTRIC MOTOR, SRR / GO, 94, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 12" x 10" CL 600, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR BYPASS VALVE RECEIVER (SRR / GO, 12" X 10" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV568-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/12/18 | ME-PM-002-M6
933558 | M400MOV569 | ACTUATOR,ELECTRIC MOTOR, SRR / GO, 94, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 12" x 10" CL 600, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV SRR, BYPASS VALVE LAUNCHER (SRR / GO, 12" X 10" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV569-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/12/18 | ME-PM-002-M6
933559 | M400MOV570 | ACTUATOR,ELECTRIC MOTOR, SRR / GO, 94, MOTORISED, AUDCO, 415V, 3, 50HZ, 96RPM, 34 SEC, 12" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR ISOLATION VALVE RECEIVER (SRR / GO, 12" CL 600) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV570-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
933560 | M400MOV571 | ACTUATOR,ELECTRIC MOTOR, SRR / GO, 94, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 34 SEC, 12" CL 600, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV SRR, BATTERY LIMIT VALVE LAUNCHER (SRR / GO, 12" CL 600 WITH STEM EXTENSION) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV571-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/12/18 | ME-PM-002-M6
933561 | M400MOV651 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 102, MOTORISED, ADUCO, 415V, 3, 50HZ, 144RPM, 44 SEC, 16" CL 900, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR BATTERY LIMIT (ULG95/ULG98/JETA1/GO,16" CL 900 WITH STEM EXTN) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV651-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/11/18 | ME-PM-002-M6
933562 | M400MOV652 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 102, MOTORISED, ADUCO, 415V, 3, 50HZ, 144RPM, 44 SEC, 16" CL 900, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR ISOLATION VALVE RECEIVER (ULG 95 / ULG 98 / JET A1 / GO, 16" CL 900) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV652-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933563 | M400MOV654 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 102, MOTORISED, ADUCO, 415V, 3, 50HZ, 144RPM, 44 SEC, 16" X 14" CL 900, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE 80 EP, IQ25F14B4, IP68, 203Nm | MOV FOR BYPASS VALVE RECEIVER (ULG 95 / ULG 98 / JET A1 / GO, 16" X 14" CL 900) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV654-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/11/18 | ME-PM-002-M6
933564 | M400MOV655 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR INLET TO FT-620 (ULG 95 / ULG 98 / JET A1 / GO, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV655-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933565 | M400MOV656 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR OUTLET TO FT-620 (ULG 95 / ULG 98 / JET A1 / GO, 16" X 14" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 2 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV656-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/01/19 | ME-PM-002-M6
933566 | M400MOV659 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / SS304, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR JET A1 MANIFOLD (JET A1, 16" X 14" CL 3000 |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV659-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/10/18 | ME-PM-002-M6
933567 | M400MOV660 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR GAS OIL MANIFOLD (GAS OIL, 16" X14" CL 300 WITH EXTN LG 1730MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV660-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/10/18 | ME-PM-002-M6
933568 | M400MOV661 | ACTUATOR,ELECTRIC MOTOR, ULG 98, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR ULG-91 MANIFOLD (ULG 98, 16" X14" CL 300 WITH EXTN LG 1730MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV661-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/10/18 | ME-PM-002-M6
933569 | M400MOV662 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR ULG-95 MANIFOLD (ULG 95, 16" X14" CL 300 WITH EXTN LG 1730MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV662-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/10/18 | ME-PM-002-M6
933570 | M400MOV663 | ACTUATOR,ELECTRIC MOTOR, GAS OIL / JET A1 / SLOP, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR JET-A1 SLOP MANIFOLD (GASOIL/JETA1/SLOP,16" X14" CL300 W/ EXTN LG 1730MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV663-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
933571 | M400MOV664 | ACTUATOR,ELECTRIC MOTOR, ULG RICH SLOP, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 48RPM, 39 SEC, 16" X 14" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | IDB MOV FOR ULG RICH MANIFOLD (ULG RICH SLOP, 16" X14" CL 300 WITH EXTN LG 1730MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV664-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
933572 | M400MOV751 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR 400-P-017A SUCTION LINE (JET A1, 14" X 12" CL 150 |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV751-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/11/18 | ME-PM-002-M6
933573 | M400MOV752 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR 400-P-017B SUCTION LINE (JET A1, 14" X 12" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV752-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/11/18 | ME-PM-002-M6
933574 | M400MOV753 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR M400-P-17A DISCHARGE LINE(JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV753-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/01/19 | ME-PM-002-M6
933575 | M400MOV754 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-017B DISCHARGE LINE (JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV754-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/11/18 | ME-PM-002-M6
933576 | M400MOV755 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT-771 INLET (JET A1, 10" X 8" CL 150 WITH EXTN LG 1470MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV755-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/12/18 | ME-PM-002-M6
933577 | M400MOV756 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE 80 EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT-771 OUTLET (JET A1, 10" X 8" CL 150 WITH EXTN LG 1470MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV756-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/12/18 | ME-PM-002-M6
933578 | M400MOV757 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR INLET TO 400-L-004A (JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV757-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933579 | M400MOV758 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR OUTLET TO 400-L-0O4A (JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV758-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/01/19 | ME-PM-002-M6
933580 | M400MOV759 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR INLET TO 400-L-004B (JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV759-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933581 | M400MOV760 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR OUTLET TO 400-L-004B (JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV760-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/01/19 | ME-PM-002-M6
933582 | M400MOV761 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR JET-A1 TANK TO P-17A (JET A1, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV761-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/10/18 | ME-PM-002-M6
933583 | M400MOV762 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR MANIFOLD TO PUMP 400-P-017A(JET A1, 14" X 12" CL 150 WITH EXTN LG 1750MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV762-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/10/18 | ME-PM-002-M6
933584 | M400MOV763 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR JET-A1 TANK TO 400-P-017B (JET A1, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV763-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/10/18 | ME-PM-002-M6
933585 | M400MOV764 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 24RPM, 42 SEC, 14" X 12" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ18F10B4, IP68, 203Nm | MOV FOR JET-A1 MANIFOLD TO PUMP 400-P-017B (JET A1, 14" X 12" CL 150 WITH EXTN LG 1750MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV764-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/10/18 | ME-PM-002-M6
933586 | M400MOV765 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 12 SEC, 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-017A DISCHARGE (JET A1, 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV765-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/11/18 | ME-PM-002-M6
933587 | M400MOV766 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 12 SEC, 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-017B DISCHARGE (JET A1, 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV766-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/11/18 | ME-PM-002-M6
933588 | M400MOV767 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR COMMON FCS (JET A1, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV767-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/12/18 | ME-PM-002-M6
933589 | M400MOV768 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 12 SEC, 6" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR COMMON DISCHARGE HEADER TO PUMP 400-P-017B (JET A1, 6" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV768-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/12/18 | ME-PM-002-M6
933590 | M400MOV801 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR 400-P-018A SUCTION LINE (JET A1, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M400MOV801-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/11/18 | ME-PM-002-M6
933591 | M400MOV802 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR 400-P-018B SUCTION LINE (JET A1, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV802-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/11/18 | ME-PM-002-M6
933592 | M400MOV803 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR 400P018A DISCHARGE LINE (JET A1, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 3 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV803-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/09/18 | ME-PM-002-M6
933593 | M400MOV804 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR 400-P-018 A DISCHARGE LINE(JET A1, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV804-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/09/18 | ME-PM-002-M6
933594 | M400MOV805 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 72RPM, 15 SEC, 10" X 8" CL 300, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR TERMINAL OUTPUT (JET A1, 10" X 8" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV805-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/10/18 | ME-PM-002-M6
933595 | M400MOV806 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" CL 300, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR ISOLATION VALVE LAUNCHER (JET A1, 10" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV806-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933596 | M400MOV807 | ACTUATOR,ELECTRIC MOTOR, JET A1, 47, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 10" CL 300, BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR BATTERY LIMIT (JET A1, 10" CL 300) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV807-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/12/18 | ME-PM-002-M6
933597 | M400MOV851 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR ULG 95 MANIFOLD (ULG 95, 16" X 14" CL 150 WITH EXTN LG 1740MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV851-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/09/18 | ME-PM-002-M6
933598 | M400MOV852 | ACTUATOR,ELECTRIC MOTOR, ULG 95, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR ULG 91 MANIFOLD (ULG 98, 16" X 14" CL 150 WITH EXTN LG 1740MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV852-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/09/18 | ME-PM-002-M6
933599 | M400MOV853 | ACTUATOR,ELECTRIC MOTOR, GAS OIL, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR GAS OIL MANIFOLD (GAS OIL, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV853-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
933600 | M400MOV854 | ACTUATOR,ELECTRIC MOTOR, KEROSENE, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR KEROSENE MANIFOLD (KEROSENE, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV854-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/09/18 | ME-PM-002-M6
933601 | M400MOV855 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 29 SEC, 12" X 10" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR JET A1 MANIFOLD (JET A1, 12" X 10" CL 150 WITH EXTN LG 1780MM) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV855-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/01/19 | ME-PM-002-M6
933602 | M400MOV856 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR 400-P-015A SUCTION LINE (ULG 95 / ULG 98 / JET A1 / GO, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV856-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/11/18 | ME-PM-002-M6
933603 | M400MOV857 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-015A DISCHARGE LINE (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV857-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/11/18 | ME-PM-002-M6
933604 | M400MOV858 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 24RPM, 44 SEC, 16" X 14" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ20F14B4, IP68, 203Nm | MOV FOR 400-P-015B SUCTION LINE (PUMP15B SUCTION ULG 95/JET A1/GO, 16" X 14" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV858-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/11/18 | ME-PM-002-M6
933605 | M400MOV859 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR 400-P-015B DISCHARGE LINE (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 150) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV859-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/11/18 | ME-PM-002-M6
933606 | M400MOV860 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT-861 INLET (ULG95/ULG98/JET A1/GO,10" X 8" CL150 W/EXT LG 1470) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV860-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933607 | M400MOV861 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 18.4, MOTORISED, AUDCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE / PTFE, SS 316, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT-861 OUTLET (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 150 |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV861-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
933608 | M400MOV862 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT-861 (JET A1, 10" X 8" CL 150 WITH EXTN LG 1470) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV862-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/12/18 | ME-PM-002-M6
933609 | M400MOV863 | ACTUATOR,ELECTRIC MOTOR, JET A1, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR OUTLET FCS 004 TO AL AIN PUMP (JET A1, 10" X 8" CL 150 WITH EXTN LG 1470) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV863-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/01/19 | ME-PM-002-M6
933610 | M400MOV864 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 18.4, MOTORISED, ADUCO, 415V, 3, 50HZ, 36RPM, 22 SEC, 10" X 8" CL 150, FLANGED, CAST, A 216 GR WCB, GRAPHITE, PTFE, ELECTRICAL, SAE80EP, IQ12F10B4, IP68, 203Nm | MOV FOR FT 861 FCS (ULG95/ULG98/JETA1/GO,10" X 8" CL150 W/EXTN LG 1470) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV864-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/12/18 | ME-PM-002-M6
933611 | M400MOV881 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 239, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" X 8" CL 1500, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR 400-P-016A SUCTION LINE (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 1500) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV881-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/11/18 | ME-PM-002-M6
933612 | M400MOV882 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 239, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" X 8" CL 1500, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR 400-P-016A DISCHARG LINE (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 1500) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV882-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
933613 | M400MOV883 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 239, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" X 8" CL 1500, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR 400-P-016B SUCTION LINE (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 1500) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV883-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/11/18 | ME-PM-002-M6
933614 | M400MOV884 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 239, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" X 8" CL 1500, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR 400-P-016B DISCHARGE LINE (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 1500) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV884-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/11/18 | ME-PM-002-M6
933615 | M400MOV888 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 28 SEC, 10" X 8" CL 900, FLANGED, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR BYPASS VALVE LAUNCHER (ULG 95 / ULG 98 / JET A1 / GO, 10" X 8" CL 900) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV888-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/12/18 | ME-PM-002-M6
933616 | M400MOV889 | ACTUATOR,ELECTRIC MOTOR, ULG 95 / ULG 98 / JET A1 / GO, 143, MOTORISED, ADUCO, 415V, 3, 50HZ, 96RPM, 29 SEC, 10" CL 900, FLANGED / BW, CAST, A 216 GR WCB, GRAPHITE, NYLON, ELECTRICAL, SAE80EP, IQ25F14B4, IP68, 203Nm | MOV FOR ISOLATION VALVE LAUNCHER (ULG 95 / ULG 98 / JET A1 / GO, 10" CL 900) |  | MOV | M400MOV | 2 | MOV | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M400MOV889-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/01/19 | ME-PM-002-M6
934241 | M400PG817 | GAUGE, PRESSURE, BOURDON TUBE , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. at Muss. Adia Jet A1 P/L from 400-P-018A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934242 | M400PG820 | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pressure at 400-PLR-016 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934243 | M400PG821 | GAUGE, PRESSURE, INDICATION , -1 TO 3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Pressure at 400-PLR-016 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934244 | M400PG822 | GAUGE, PRESSURE, INDICATION , 0-40 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. at Mussafah Adia Jet A1 P/L from 400-PLR-016 |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934245 | M400PG851 | GAUGE, PRESSURE, INDICATION , -1-+3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 | Pr. Mussafah-Al Ain MP Tie-In P/L to 400-P-015A/B |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934246 | M400PG855 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Booster Pump 400-P-015A Discharge Pr. | 933874 |  | M400P015A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934247 | M400PG856 | GAUGE, PRESSURE, INDICATION , 0-10 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Booster Pump 400-P-015B Discharge Pr. | 933875 |  | M400P015B | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934248 | M400PG859 | GAUGE, PRESSURE, INDICATION , 0-6 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 316 , | Pr. Mussafah-Al Ain MP Tie-In P/L to 400-P-016A/B/ |  |  | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934249 | M400PG861 | GAUGE, PRESSURE, BOURDON TUBE , -1-+3 KG/CM2 , 100MM , ½" NPTM , SS 316L , SS 31 | Booster Pump 400-P-015A Suction Pr. | 933874 |  | M400P015A | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934597 | M20TSV407 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M20VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934598 | M20TSV408 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M20VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934599 | AA213TSV147 | VALVE RELIEF | AL AIN RECEIVING STATION GAS OIL,THERMAL RLF VALVE |  | PSV | AA13VALVE | 3 | PSV | 617101-310600 | IRPALAIN | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934600 | AA213TSV148 | VALVE RELIEF | AL AIN RECEIVING STATION GAS OIL,THERMAL RLF VALVE |  | PSV | AA13VALVE | 3 | PSV | 617101-310600 | IRPALAIN | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934610 | U29TSV745 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | U2902L | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934611 | U29TSV746 | VALVE RELIEF | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | U2902L | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934619 | U29TSV756 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | U2903L | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934620 | U29TSV757 | VALVE RELIEF | SRR, THERMAL RELIEF VALVE |  | PSV | U2903L | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934623 | M30TSV423 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M30VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934624 | M30TSV425 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M30VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934625 | M30TSV426 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M30VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934626 | M30TSV427 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M30VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934627 | M30TSV428 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M30VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934628 | M30TSV429 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M30VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934629 | AA313TSV149 | VALVE RELIEF | AL AIN RECEIVING STATION ULG 95,THERMAL RLF VALVE |  | PSV | AA13VALVE | 1 | PSV | 617101-310600 | IRPALAIN | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934630 | AA313TSV150 | VALVE RELIEF | AL AIN RECEIVING STATION ULG 95,THERMAL RLF VALVE |  | PSV | AA13VALVE | 1 | PSV | 617101-310600 | IRPALAIN | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934631 | M400TSV301 | VALVE RELIEF | ULG 95 TRANSFERRING 18.58BAR, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934632 | M400TSV302 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934633 | M400TSV303 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934634 | M400TSV304 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934635 | M400TSV305 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934636 | M400TSV306 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934637 | M400TSV307 | VALVE RELIEF | SR # 323570 ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934638 | M400TSV308 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934639 | M400TSV309 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934640 | M400TSV310 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934641 | M400TSV311 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934642 | M400TSV312 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934643 | M400TSV313 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934644 | M400TSV314 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934645 | M400TSV315 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934646 | M400TSV316 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934647 | M400TSV317 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934648 | M400TSV318 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934649 | M400TSV319 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934650 | M400TSV320 | VALVE RELIEF | ULG 95, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934651 | M400TSV321 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934652 | M400TSV322 | VALVE RELIEF | GAS OIL LOWERING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934653 | M400TSV323 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934654 | M400TSV324 | VALVE RELIEF | GAS OIL LOWERING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934655 | M400TSV325 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934656 | M400TSV326 | VALVE RELIEF | GAS OIL FILLING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934657 | M400TSV327 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934658 | M400TSV328 | VALVE RELIEF | GAS OIL,THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934659 | M400TSV329 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934660 | M400TSV330 | VALVE RELIEF | GAS OIL,THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934661 | M400TSV331 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934662 | M400TSV332 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934663 | M400TSV333 | VALVE RELIEF | GAS OIL, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934664 | M400TSV336 | VALVE RELIEF | ULG 98 , THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934665 | M400TSV337 | VALVE RELIEF | ULG 98 , THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934666 | M400TSV338 | VALVE RELIEF | ULG 98 , THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934667 | M400TSV339 | VALVE RELIEF | ULG 98, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934668 | M400TSV340 | VALVE RELIEF | ULG 98 , THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934669 | M400TSV341 | VALVE RELIEF | ULG 98 , THERMAL RELIEF VALVE |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934670 | M400TSV342 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934671 | M400TSV343 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE, LOWERING. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934672 | M400TSV344 | VALVE RELIEF | JET A1, THERMAL RELIEF VALVE 16" COMMON FILLING. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269465 | M410FFE2101307 | CO2 Extinguisher | CO2 Extinguisher |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269466 | M410AT200 | Colour Analyzer | Colour Analyzer ON 410P200 DISC. AFTER 410FT203. |  | ANALYSER | M410SYS | 3 | ANALYSER | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938792 | M400WOV837 | DELUGE VALVE | Transfer Pumps Deluge Valve |  |  | M400VALVE | 1 | SOL_VLV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269468 | M410AT001 | Conductivity Analyzer | Conductivity Analyzer JET A1 FROM IRP2 AT 400T111 AREA. |  | ANALYSER | M410SYS | 3 | ANALYSER | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269469 | M410AT400 | Conductivity Analyzer | Conductivity Analyzer JET A1 RUWS MSFH AFTER 410L005A,B,C,D,E. |  | ANALYSER | M410P006A | 3 | ANALYSER | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269470 | M410AT408 | Conductivity Analyzer | Conductivity Analyzer ON JP8 AFTER 410L011A,B. |  | ANALYSER | M410L011A | 3 | ANALYSER | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269226 | M410FV402A | 8" GLOBE VALVE, CLASS 300, 410-L-001A OUTLET | 8" GLOBE VALVE, CLASS 300, 410-L-001A OUTLET |  | CNTR_VLV | M410L001A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269227 | M410FV402B | 8" GLOBE VALVE, CLASS 300, 410-L-001B OUTLET | 8" GLOBE VALVE, CLASS 300, 410-L-001B OUTLET |  | CNTR_VLV | M410L001B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269228 | M410FV402C | 8" GLOBE VALVE, CLASS 300, 410-L-001C OUTLET | 8" GLOBE VALVE, CLASS 300, 410-L-001C OUTLET |  | CNTR_VLV | M410L001C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269229 | M410FV402D | 8" GLOBE VALVE, CLASS 300, 410-L-001D OUTLET | 8" GLOBE VALVE, CLASS 300, 410-L-001D OUTLET |  | CNTR_VLV | M410L001D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269230 | M410FV403A | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 |  | CNTR_VLV | M410L005A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269231 | M410FV403B | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 |  | CNTR_VLV | M410L005B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269232 | M410FV403C | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 |  | CNTR_VLV | M410L005C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269233 | M410FV403D | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 |  | CNTR_VLV | M410L005D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269234 | M410FV403E | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 |  | CNTR_VLV | M410L005E | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269235 | M410LV401A | 1" GLOBE VALVE, CLASS 300, 410-L-005A DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-005A DRAIN |  | CNTR_VLV | M410L005A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269236 | M410LV401B | 1" GLOBE VALVE, CLASS 300, 410-L-005B DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-005B DRAIN |  | CNTR_VLV | M410L005B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269237 | M410LV401C | 1" GLOBE VALVE, CLASS 300, 410-L-005C DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-005C DRAIN |  | CNTR_VLV | M410L005C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269238 | M410LV401D | 1" GLOBE VALVE, CLASS 300, 410-L-005D DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-005D DRAIN |  | CNTR_VLV | M410L005D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269239 | M410LV401E | 1" GLOBE VALVE, CLASS 300, 410-L-005E DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-005E DRAIN |  | CNTR_VLV | M410L005E | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269240 | M410LV403A | 1" GLOBE VALVE, CLASS 300, 410-L-001A DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-001A DRAIN |  | CNTR_VLV | M410L001A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269241 | M410LV403B | 1" GLOBE VALVE, CLASS 300, 410-L-001B DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-001B DRAIN |  | CNTR_VLV | M410L001B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269242 | M410LV403C | 1" GLOBE VALVE, CLASS 300, 410-L-001C DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-001C DRAIN |  | CNTR_VLV | M410L001C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269243 | M410LV403D | 1" GLOBE VALVE, CLASS 300, 410-L-001D DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-001D DRAIN |  | CNTR_VLV | M410L001D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269244 | M410LV407A | 1" GLOBE VALVE, CLASS 300, 410-L-011A DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-011A DRAIN |  | CNTR_VLV | M410L011A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269245 | M410LV407B | 1" GLOBE VALVE, CLASS 300, 410-L-011B DRAIN | 1" GLOBE VALVE, CLASS 300, 410-L-011B DRAIN |  | CNTR_VLV | M410L011B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269246 | M410PV002 | 1" GLOBE VALVE, CLASS 300, UTILITY AIR FROM COMPRESSOR PACKAGE | 1" GLOBE VALVE, CLASS 300, UTILITY AIR FROM COMPRESSOR PACKAGE |  | CNTR_VLV | M410V006 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269247 | M410PV245 | 12X8" GLOBE VALVE, CLASS 300, TO MUSSAFAH-AIDA JET A1 PIPELINE | 12X8" GLOBE VALVE, CLASS 300, TO MUSSAFAH-AIDA JET A1 PIPELINE |  | CNTR_VLV | M410P006A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269248 | M410PV277 | 8X6" GLOBE VALVE, CLASS 900, TO MUSSAFAH AIN ULG PIPELINE | 8X6" GLOBE VALVE, CLASS 900, TO MUSSAFAH AIN ULG PIPELINE |  | CNTR_VLV | M410P002B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269249 | M410PV300 | 8X6" GLOBE VALVE, CLASS 900, TO MUSSAFAH-AL AIN AS OIL PIPELINE | 8X6" GLOBE VALVE, CLASS 900, TO MUSSAFAH-AL AIN AS OIL PIPELINE |  | CNTR_VLV | M410P004B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269250 | M410PV402 | 16" GLOBE VALVE, CLASS 300, TO JET A1 METERING | 16" GLOBE VALVE, CLASS 300, TO JET A1 METERING |  | CNTR_VLV | M410PLR001 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269251 | M410PV413 | 24X20" GLOBE VALVE, CLASS 600, GAS OIL TO METERING | 24X20" GLOBE VALVE, CLASS 600, GAS OIL TO METERING |  | CNTR_VLV | M410PT412 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269252 | M410PV462 | 6" GLOBE VALVE, CLASS 300, FROM MUSSAFAH AL-DHAFRA MAIN LINE PUMPS | 6" GLOBE VALVE, CLASS 300, FROM MUSSAFAH AL-DHAFRA MAIN LINE PUMPS |  | CNTR_VLV | M410PLR007 | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269471 | M410MK001ACF1 | COOLING MOTOR FOR COMPRESSOR | COOLING MOTOR FOR COMPRESSOR |  | MOTOR | M410K001A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MK001ACF1-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269472 | M410MK001ACF2 | COOLING MOTOR FOR COMPRESSOR | COOLING MOTOR FOR COMPRESSOR |  | MOTOR | M410K001A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MK001ACF2-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269473 | M410MK001BCF1 | COOLING MOTOR FOR COMPRESSOR | COOLING MOTOR FOR COMPRESSOR |  | MOTOR | M410K001B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MK001BCF1-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269474 | M410MK001BCF2 | COOLING MOTOR FOR COMPRESSOR | COOLING MOTOR FOR COMPRESSOR |  | MOTOR | M410K001B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MK001BCF2-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269475 | M410CCP401 | CORROSION COUPON | CORROSION COUPON |  | CATHPRO | M410CPRX | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269476 | M410CCP402 | CORROSION COUPON | CORROSION COUPON |  | CATHPRO | M410CPRX | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269477 | M410CCP403 | CORROSION COUPON | CORROSION COUPON |  | CATHPRO | M410CPRX | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269478 | M410CCP404 | CORROSION COUPON | CORROSION COUPON |  | CATHPRO | M410CPRX | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269479 | M410CCP405 | CORROSION COUPON | CORROSION COUPON |  | CATHPRO | M410CPRX | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269480 | M410CCP407 | CORROSION COUPON | CORROSION COUPON |  | CATHPRO | M410CPRX | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269481 | M410P030A | AL DHAFRA JP-8 CORROSION INHIBITOR RECIPROCATING INJECTION PUMP. | CORROSION INHIBITOR (NEAT) INJECTION PUMP 410ME010. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269482 | M410P030B | AL DHAFRA JP-8 CORROSION INHIBITOR RECIPROCATING INJECTION PUMP. | CORROSION INHIBITOR (NEAT) INJECTION PUMP 410ME010. |  | PURE | M410PUMP | 3 | PURE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269485 | M410MP030A | CORROSION INHIBITOR (NEAT CHEMICAL) INJECTION PUMPS MOTOR | CORROSION INHIBITOR (NEAT CHEMICAL) INJECTION PUMPS MOTOR |  | MOTOR | M410P030A | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP030A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269486 | M410MP030B | CORROSION INHIBITOR (NEAT CHEMICAL) INJECTION PUMPS MOTOR | CORROSION INHIBITOR (NEAT CHEMICAL) INJECTION PUMPS MOTOR |  | MOTOR | M410P030B | 3 | MOTOR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP030B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969269487 | M410FT741 | FLOW TRANSMITTER FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | FLOW TRANSMITTER FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269488 | M410PSV741 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269489 | M410PSV742 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269490 | M410PSV743 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269491 | M410PSV744 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | PRESSURE SAFETY VALVE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269492 | M410XV741 | PNEUMATIC VAVLE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | PNEUMATIC VAVLE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269493 | M410XV742 | PNEUMATIC VAVLE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 | PNEUMATIC VAVLE FOR CORROSION INHIBITOR INJECTION PACKAGE 410-ME-010 |  | PACKAGE | M410ME010 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269494 | M410LT741 | CORROSION INHIBITOR(NEAT CHEMICAL) STORAGE TANK | CORROSION INHIBITOR(NEAT CHEMICAL) STORAGE TANK |  | LVL_TX | M410ME010 | 3 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269495 | M410AT401 | CORROSION PROBE | CORROSION PROBE |  | CATHPRO | M410PLR001 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269496 | M410AT402 | CORROSION PROBE | CORROSION PROBE |  | CATHPRO | M410PT412 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269497 | M410AT403 | CORROSION PROBE | CORROSION PROBE |  | CATHPRO | M410PLR005 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269498 | M410AT404 | CORROSION PROBE | CORROSION PROBE |  | CATHPRO | M410PLR006 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269499 | M410AT405 | CORROSION PROBE | CORROSION PROBE |  | CATHPRO | M410PLR003 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269500 | M410AT407 | CORROSION PROBE | CORROSION PROBE |  | CATHPRO | M410PLR007 | 3 | CATHPRO | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269501 | M410FT203A | CORIOLIS FLOW TRANSMITTER FOR 410-FT-203, MUSSAFAH TERMINAL, ULG | ULG CUSTODY TRANSFER FLOWMETER A. |  | FL_MTR | M410FT203 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269502 | M410FT203B | CORIOLIS FLOW TRANSMITTER FOR 410-FT-203, MUSSAFAH TERMINAL, ULG | ULG CUSTODY TRANSFER FLOWMETER B. |  | FL_MTR | M410FT203 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269503 | M410FT206A | CORIOLIS FLOW TRANSMITTER FOR 410-FT-206, MUSSAFAH TERMINAL, GAS OIL | GAS OIL CUSTODY TRANSFER FLOWMETER A. |  | FL_MTR | M410FT206 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269504 | M410FT206B | CORIOLIS FLOW TRANSMITTER FOR 410-FT-206, MUSSAFAH TERMINAL, GAS OIL | GAS OIL CUSTODY TRANSFER FLOWMETER B. |  | FL_MTR | M410FT206 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269505 | M410FT209A | CORIOLIS FLOW TRANSMITTER FOR 410-FT-209, MUSSAFAH TERMINAL, JET A1 | JET A1 CUSTODY TRANSFER FLOWMETER A. |  | FL_MTR | M410FT209 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269506 | M410FT209B | CORIOLIS FLOW TRANSMITTER FOR 410-FT-209, MUSSAFAH TERMINAL, JET A1 | JET A1 CUSTODY TRANSFER FLOWMETER B. |  | FL_MTR | M410FT209 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269507 | M410FT211A | CORIOLIS FLOW TRANSMITTER FOR 410-FT-211, MUSSAFAH TERMINAL, JP-8 | JP-8 CUSTODY TRANSFER FLOWMETER A. |  | FL_MTR | M410FT211 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269508 | M410FT211B | CORIOLIS FLOW TRANSMITTER FOR 410-FT-211, MUSSAFAH TERMINAL, JP-8 | JP-8 CUSTODY TRANSFER FLOWMETER B. |  | FL_MTR | M410FT211 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269509 | M410FT400A | CORIOLIS FLOW TRANSMITTER FOR 410-FT-400, MUSSAFAH TERMINAL, JET A1 | FLOW TRANSMITTER FOR 410-FT-400, MUSSAFAH TERMINAL, JET A1 |  | FL_MTR | M410FT400 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269510 | M410FT400B | CORIOLIS FLOW TRANSMITTER FOR 410-FT-400, MUSSAFAH TERMINAL, JET A1 | FLOW TRANSMITTER FOR 410-FT-400, MUSSAFAH TERMINAL, JET A1 |  | FL_MTR | M410FT400 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269511 | M410FT400C | CORIOLIS FLOW TRANSMITTER FOR 410-FT-400, MUSSAFAH TERMINAL, JET A1 | FLOW TRANSMITTER FOR 410-FT-400, MUSSAFAH TERMINAL, JET A1 |  | FL_MTR | M410FT400 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269512 | M410FT401A | CORIOLIS FLOW TRANSMITTER FOR 410-FT-401, MUSSAFAH TERMINAL, GAS OIL | FLOW TRANSMITTER FOR 410-FT-401, MUSSAFAH TERMINAL, GAS OIL |  | FL_MTR | M410FT401 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269513 | M410FT401B | CORIOLIS FLOW TRANSMITTER FOR 410-FT-401, MUSSAFAH TERMINAL, GAS OIL | FLOW TRANSMITTER FOR 410-FT-401, MUSSAFAH TERMINAL, GAS OIL |  | FL_MTR | M410FT401 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269514 | M410FT401C | CORIOLIS FLOW TRANSMITTER FOR 410-FT-401, MUSSAFAH TERMINAL, GAS OIL | FLOW TRANSMITTER FOR 410-FT-401, MUSSAFAH TERMINAL, GAS OIL |  | FL_MTR | M410FT401 | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269516 | M410DCSMC003 | ESD MARSHALLING CABINET | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269517 | M410DCSMC004 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269518 | M410DCSMC005 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269519 | M410DCSMC006 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269520 | M410DCSMC007 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269521 | M410DCSMC008 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269522 | M410DCSSC003 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269523 | M410DCSSC004 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269524 | M410DCSSC005 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE4 | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269525 | M410DCSSC006 | Colour Analyzer | DCS SYSTEM CABINET FOR SIS-001DCS SYSTEM |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205030 | M410P032A | FIRE WATER PUMP- MOTOR | FIRE WATER PUMP- MOTOR DRIVEN(2 DUTY) | 969147473 | MOTOR | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | e | 0 | Y | Y | 0 | 0 | 0 | M410P032A-MM1 | ACTIVE | MECH | PM | FT | 2 | WEEKS | 05/08/18 | MM-PM-026-W1
936415 | M400P201A | PANEL | FIRE WATER PUMPS-MAIN DIESEL DRIVEN | 936404 |  | M400PUMP | 1 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M400P201A-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 24/05/19 | MC-PM-027-Y1
936416 | M400P201B | PANEL | FIRE WATER PUMP (MAIN) | 936405 |  | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M400P201B-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 06/06/19 | MC-PM-027-Y1
936417 | M400P201C | PANEL | FIRE WATER PUMP (MAIN) | 936406 |  | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M400P201C-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 14/07/19 | MC-PM-027-Y1
936418 | M400P201D | PANEL | FIRE WATER PUMPS-MAIN DIESEL DRIVEN | 936407 |  | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M400P201D-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 15/08/18 | MC-PM-027-Y1
936419 | M400P202 | PANEL | FIRE WATER PUMPS STANDBY MOTOR DRIVEN | 936408 |  | M400PUMP | 1 | PUCE | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M400P202-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 18/04/19 | MC-PM-028-Y1
969205040 | M410P031A | Pressure differential Indicator | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | 969147466 | INDICATR | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | Low | Y | 1 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P031A-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969205041 | M410P033A | Pressure Switch | JOCKEY PUMP ELECTRIC MOTOR DRIVEN | 969147475 | PRES_SWT | M410PUMP | 1 | EMACFF | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P033A-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 25/11/18 | MC-PM-02-M6
969205042 | M410P031A | Level gauge | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | 969147466 | INDICATR | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | Low | Y | 1 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P031A-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969205043 | M410P031A | Level switch | FIRE WATER PUMP- DIESEL ENGINE DRIVEN(4 DUTY+ 3 STANDBY) | 969147466 | LVL_SWT | M410PUMP | 3 | CEDEFF | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | Low | Y | 1 | 12 | c | 0 | Y | Y | 0 | 0 | 0 | M410P031A-MC1 | ACTIVE | CONT | PM | FIC | 2 | WEEKS | 05/08/18 | MC-PM-027-W1
969269526 | M410ME101 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE3 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE3 |  | PACKAGE |  | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269527 | M410ME102 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE3 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE3 |  | PACKAGE |  | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269528 | M410ME106 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE3 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE3 |  | PACKAGE | M410MISC | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270288 | M410PSV403A | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270289 | M410PSV403B | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270290 | M410PSV403C | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L001C | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270291 | M410PSV403D | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L001D | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270292 | M410PSV404A | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L011A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270293 | M410PSV404B | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L011B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270294 | M410TSV132 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE NORTH OF 400T104 AREA. |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270295 | M410TSV133 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE IN WEST OF 10T104 AREA. |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270296 | M410TSV212 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410P002A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270297 | M410TSV218 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410P004A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270298 | M410TSV220 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410P004A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270299 | M410TSV400 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270300 | M410TSV401 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270301 | M410TSV402 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270302 | M410TSV403 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270303 | M410TSV404 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270304 | M410TSV406 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270305 | M410TSV407 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PT412 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270306 | M410TSV408 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PT412 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270307 | M410TSV409 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PT412 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270308 | M410TSV410 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PT412 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270309 | M410TSV423 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR006 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270310 | M410TSV424 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR006 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270311 | M410TSV425 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR006 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270312 | M410TSV426 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L001A | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270313 | M410TSV427 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270314 | M410TSV428 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270315 | M410TSV429 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270316 | M410TSV437 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR007 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270317 | M410TSV438 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR007 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270318 | M410TSV439 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR007 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270319 | M410TSV442 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR006 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270320 | M410TSV443 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270321 | M410TSV445 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410PLR007 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270322 | M410TSV446 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270323 | M410TSV447 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE NORTH OF 10T102 AREA. |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270324 | M410TSV449 | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410L001B | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270325 | M410PSV761A | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270326 | M410PSV761B | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270327 | M410PSV762A | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270328 | M410PSV762B | PRESSURE SAFETY VALVE | PRESSURE SAFETY VALVE |  | PSV | M410VALVE | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270329 | M410PT203A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT203 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT203A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270330 | M410PT203B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT203 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT203B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270331 | M410PT206A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT206 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT206A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270332 | M410PT206B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT206 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT206B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270333 | M410PT209A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT209 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT209A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270334 | M410PT209B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT209 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT209B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270335 | M410PT211A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT211 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT211A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270336 | M410PT211B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT211 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT211B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270337 | M410PT400A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT400 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT400A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270338 | M410PT400B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT400 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT400B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270339 | M410PT400C | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT400 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT400C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270340 | M410PT401A | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT401 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT401A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270341 | M410PT401B | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT401 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT401B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270342 | M410PT401C | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410FT401 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT401C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270343 | M410PT721 | PRESSURE TRANSMITTER | BLUE DYE PRESSURE TRANSMITTER |  | PRES_TX | M410ME001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT721-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270344 | M410PT722 | PRESSURE TRANSMITTER | BLUE DYE PRESSURE TRANSMITTER |  | PRES_TX | M410ME001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT722-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270345 | M410PT723 | PRESSURE TRANSMITTER | BLUE DYE PRESSURE TRANSMITTER |  | PRES_TX | M410ME001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT723-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270346 | M410PT724 | PRESSURE TRANSMITTER | BLUE DYE PRESSURE TRANSMITTER |  | PRES_TX | M410ME001 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT724-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270347 | M410PT731 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT731-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270348 | M410PT732 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT732-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270349 | M410PT733 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT733-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270350 | M410PT734 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT734-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270351 | M410PT735 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT735-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270352 | M410PT736 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT736-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270353 | M410PT737 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT737-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270354 | M410PT738 | PRESSURE TRANSMITTER | ANTI-STATIC PRESSURE TRANSMITTER |  | PRES_TX | M410ME002 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT738-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270355 | M410PT751 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME011 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT751-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270356 | M410PT752 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME011 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT752-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270357 | M410PT753 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME011 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT753-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270358 | M410PT754 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME011 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT754-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270359 | M410PT741 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME010 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT741-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270360 | M410PT742 | PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | PRES_TX | M410ME010 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT742-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270519 | M410P005C | SEAL SYSTEM(NDE) FOR 410-P-005C | ADIA NORTH JET A1 BOOSTER PUMP. | 969269219 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270520 | M410P006A | SEAL SYSTEM(NDE) FOR 410-P-006A | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269220 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270521 | M410P006B | SEAL SYSTEM(NDE) FOR 410-P-006A | ADIA NORTH JET A1 MAIN LINE PUMP | 969269221 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270522 | M410P006C | SEAL SYSTEM(NDE) FOR 410-P-006C | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269222 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270523 | M410P024A | SEAL SYSTEM(NDE) FOR 410-P-024A | AL DHAFRA JP-8 MAIN LINE PUMP | 969269223 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270524 | M410P024B | SEAL SYSTEM(NDE) FOR 410-P-024B | AL DHAFRA JP-8 MAIN LINE PUMP | 969269224 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270525 | M410P024C | SEAL SYSTEM(NDE) FOR 410-P-024C | AL DHAFRA JP-8 MAIN LINE PUMP | 969269225 | SYSTEM | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270526 | M410FG211 | Sight Glass | Sight Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270527 | M410FG3411 | Sight Glass | Sight Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270528 | M410FG311 | Sight Glass | Sight Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270529 | M410FG411 | Sight Glass | Sight Glass |  | INDICATR | M410FLOW | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270530 | M410TE400 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | M410PLR001 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270531 | M410TE402 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | M410PT412 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270532 | M410TE404 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | M410PLR005 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270533 | M410TE407 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | M410PLR006 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270534 | M410TE409 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | M410PLR003 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270535 | M410TE413 | SKIN TEMPERATURE ELEMENT (RTD) | SKIN TEMPERATURE ELEMENT (RTD) |  | TEMP_ELE | M410PLR007 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270536 | M410MX101 | STATIC MIXER | BLUE DYE STATIC MIXER |  | VESSEL | M410ME001 | 3 | MIX | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 1 | 5 | 1 | 2.0969 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270537 | M410MX102 | STATIC MIXER | STATIC MIXER FOR ANTI-STATIC |  | VESSEL | M410ME002 | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 10 | 5 | 50 | 10 | 5 | 6.0969 | High | Medium | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270538 | M410MX103 | STATIC MIXER | STATIC MIXER |  | VESSEL | M410ME010 | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 10 | 5 | 50 | 10 | 5 | 6.0969 | High | Medium | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270539 | M410MX104 | STATIC MIXER | STATIC MIXER |  | VESSEL | M410ME011 | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 10 | 5 | 50 | 10 | 5 | 6.0969 | High | Medium | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270540 | M410MX105 | STATIC MIXER | STATIC MIXER |  | VESSEL | M400ME002 | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 10 | 5 | 50 | 10 | 5 | 6.0969 | High | Medium | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270541 | M410MX106 | STATIC MIXER | STATIC MIXER |  | VESSEL | M400ME003 | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 10 | 5 | 50 | 10 | 5 | 6.0969 | High | Medium | Medium | N | Medium | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270543 | M410L091A | SUCTION AIR FILTER FOR COMPRESSOR | SUCTION AIR FILTER FOR COMPRESSOR |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270544 | M410L091B | SUCTION AIR FILTER FOR COMPRESSOR | SUCTION AIR FILTER FOR COMPRESSOR |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270545 | M410B050A | TANK HEATER | LUBE OIL COOLER OUTLET TEMPERATURE |  | TEMP_ELE | M410P002A | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410B050A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-HTR1-PM-M6
969270546 | M410B050B | TANK HEATER | LUBE OIL COOLER OUTLET TEMPERATURE |  | TEMP_ELE | M410P002B | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410B050B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-HTR1-PM-M6
969270547 | M410B051A | TANK HEATER | LUBE OIL COOLER OUTLET TEMPERATURE |  | TEMP_ELE | M410TEMP | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410B051A-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-HTR1-PM-M6
969270548 | M410B051B | TANK HEATER | LUBE OIL COOLER OUTLET TEMPERATURE |  | TEMP_ELE | M410TEMP | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410B051B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-HTR1-PM-M6
934673 | M400TSV345 | VALVE RELIEF | JET A1 FILLING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934674 | M400TSV346 | VALVE RELIEF | JET A1 LOWERING, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 1 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353281 | M410JBE751A | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001A- | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001A |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353282 | M410JBE752A | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001A | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001A |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353283 | M410JBE753A | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001A | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001A |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353284 | M410JBE751B | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001B | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001B |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516461 | PL315GDH1306 | FLAMMABLE GAS DETECTOR AT SV STATION-13 | FLAMMABLE GAS DETECTOR AT SV STATION-13 |  | FG_DET | PL315SV13 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516462 | PL315GDH1307 | FLAMMABLE GAS DETECTOR AT SV STATION-13 | FLAMMABLE GAS DETECTOR AT SV STATION-13 |  | FG_DET | PL315SV13 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516463 | PL315GDH1308 | FLAMMABLE GAS DETECTOR AT SV STATION-13 | FLAMMABLE GAS DETECTOR AT SV STATION-13 |  | FG_DET | PL315SV13 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516468 | PL315XAC1313 | MANUAL CALL POINT AT SV STATION - 13 | MANUAL CALL POINT AT SV STATION - 13 |  | PA_SYS | PL315SV13 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516469 | PL315XAC1314 | MANUAL CALL POINT AT SV STATION - 13 | MANUAL CALL POINT AT SV STATION - 13 |  | PA_SYS | PL315SV13 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516470 | PL315XAC1315 | MANUAL ALARM CALL POINT AT SV STATION - 13 | MANUAL ALARM CALL POINT AT SV STATION - 13 |  | PA_SYS | PL315SV13 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516471 | PL315XAC1316 | MANUAL ALARM CALL POINT AT SV STATION - 13 | MANUAL ALARM CALL POINT AT SV STATION - 13 |  | PA_SYS | PL315SV13 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516472 | PL315XAC1317 | MANUAL CALL POINT AT SV STATION - 13 | MANUAL CALL POINT AT SV STATION - 13 |  | PA_SYS | PL315SV13 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516473 | PL315XHE1316 | HEAT DETECTOR AT SV Station-13 | HEAT DETECTOR AT SV Station-13 |  | FGBHFD | PL315SV13 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516474 | PL315XSP1315 | SMOKE DETECTOR AT SV Station-13 | SMOKE DETECTOR AT SV Station-13 |  | FGBHFD | PL315SV13 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516475 | PL318GDH1002 | FLAMMABLE GAS DETECTOR AT SV STATION-10 | FLAMMABLE GAS DETECTOR AT SV STATION-10 |  | FG_DET | PL318SV10 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516476 | PL318GDH1003 | FLAMMABLE GAS DETECTOR AT SV STATION-10 | FLAMMABLE GAS DETECTOR AT SV STATION-10 |  | FG_DET | PL318SV10 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516477 | PL318GDH1004 | FLAMMABLE GAS DETECTOR AT SV STATION-10 | FLAMMABLE GAS DETECTOR AT SV STATION-10 |  | FG_DET | PL318SV10 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516482 | PL318GDH1101 | FLAMMABLE GAS DETECTOR AT SV STATION-11 | FLAMMABLE GAS DETECTOR AT SV STATION-11 |  | FG_DET | PL318SV11 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516483 | PL318GDH1102 | FLAMMABLE GAS DETECTOR AT SV STATION-11 | FLAMMABLE GAS DETECTOR AT SV STATION-11 |  | FG_DET | PL318SV11 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516484 | PL318GDH1103 | FLAMMABLE GAS DETECTOR AT SV STATION-11 | FLAMMABLE GAS DETECTOR AT SV STATION-11 |  | FG_DET | PL318SV11 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516485 | PL318GDH1104 | FLAMMABLE GAS DETECTOR AT SV STATION-11 | FLAMMABLE GAS DETECTOR AT SV STATION-11 |  | FG_DET | PL318SV11 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516490 | PL318GDH1201 | FLAMMABLE GAS DETECTOR AT SV STATION-12 | FLAMMABLE GAS DETECTOR AT SV STATION-12 |  | FG_DET | PL318SV12 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516491 | PL318GDH1202 | FLAMMABLE GAS DETECTOR AT SV STATION-12 | FLAMMABLE GAS DETECTOR AT SV STATION-12 |  | FG_DET | PL318SV12 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516492 | PL318GDH1203 | FLAMMABLE GAS DETECTOR AT SV STATION-12 | FLAMMABLE GAS DETECTOR AT SV STATION-12 |  | FG_DET | PL318SV12 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516493 | PL318GDH1204 | FLAMMABLE GAS DETECTOR AT SV STATION-12 | FLAMMABLE GAS DETECTOR AT SV STATION-12 |  | FG_DET | PL318SV12 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516498 | PL318GDH801 | FLAMMABLE GAS DETECTOR AT SV STATION-8 | FLAMMABLE GAS DETECTOR AT SV STATION-8 |  | FG_DET | PL318SV8 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516499 | PL318GDH802 | FLAMMABLE GAS DETECTOR AT SV STATION-8 | FLAMMABLE GAS DETECTOR AT SV STATION-8 |  | FG_DET | PL318SV8 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516500 | PL318GDH803 | FLAMMABLE GAS DETECTOR AT SV STATION-8 | FLAMMABLE GAS DETECTOR AT SV STATION-8 |  | FG_DET | PL318SV8 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516501 | PL318GDH804 | FLAMMABLE GAS DETECTOR AT SV STATION-8 | FLAMMABLE GAS DETECTOR AT SV STATION-8 |  | FG_DET | PL318SV8 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516514 | PL318XAC1013 | MANUAL CALL POINT AT SV STATION - 10 | MANUAL CALL POINT AT SV STATION - 10 |  | PA_SYS | PL318SV10 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516515 | PL318XAC1014 | MANUAL CALL POINT AT SV STATION - 10 | MANUAL CALL POINT AT SV STATION - 10 |  | PA_SYS | PL318SV10 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516516 | PL318XAC1015 | MANUAL ALARM CALL POINT AT SV STATION - 10 | MANUAL ALARM CALL POINT AT SV STATION - 10 |  | PA_SYS | PL318SV10 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516517 | PL318XAC1016 | MANUAL ALARM CALL POINT AT SV STATION - 10 | MANUAL ALARM CALL POINT AT SV STATION - 10 |  | PA_SYS | PL318SV10 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516518 | PL318XAC1017 | MANUAL CALL POINT AT SV STATION - 10 | MANUAL CALL POINT AT SV STATION - 10 |  | PA_SYS | PL318SV10 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516519 | PL318XAC1113 | MANUAL CALL POINT AT SV STATION - 11 | MANUAL CALL POINT AT SV STATION - 11 |  | PA_SYS | PL318SV11 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516531 | PL318XAC815 | MANUAL ALARM CALL POINT AT SV STATION - 8 | MANUAL ALARM CALL POINT AT SV STATION - 8 |  | PA_SYS | PL318SV8 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516532 | PL318XAC816 | MANUAL ALARM CALL POINT AT SV STATION - 8 | MANUAL ALARM CALL POINT AT SV STATION - 8 |  | PA_SYS | PL318SV8 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516533 | PL318XAC817 | MANUAL CALL POINT AT SV STATION - 8 | MANUAL CALL POINT AT SV STATION - 8 |  | PA_SYS | PL318SV8 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516534 | PL318XAC913 | MANUAL CALL POINT AT SV STATION - 9 | MANUAL CALL POINT AT SV STATION - 9 |  | PA_SYS | PL318SV9 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516535 | PL318XAC914 | MANUAL CALL POINT AT SV STATION - 9 | MANUAL CALL POINT AT SV STATION - 9 |  | PA_SYS | PL318SV9 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516536 | PL318XAC915 | MANUAL ALARM CALL POINT AT SV STATION - 9 | MANUAL ALARM CALL POINT AT SV STATION - 9 |  | PA_SYS | PL318SV9 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516537 | PL318XAC916 | MANUAL ALARM CALL POINT AT SV STATION - 9 | MANUAL ALARM CALL POINT AT SV STATION - 9 |  | PA_SYS | PL318SV9 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516538 | PL318XAC917 | MANUAL CALL POINT AT SV STATION - 9 | MANUAL CALL POINT AT SV STATION - 9 |  | PA_SYS | PL318SV9 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516539 | PL318XGH1101 | HYDROGEN GAS DETECTOR AT SV STATION-11 | HYDROGEN GAS DETECTOR AT SV STATION-11 |  | FG_DET | PL318SV11 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516540 | PL318XGH1201 | HYDROGEN GAS DETECTOR AT SV STATION-12 | HYDROGEN GAS DETECTOR AT SV STATION-12 |  | FG_DET | PL318SV12 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516541 | PL318XGH801 | HYDROGEN GAS DETECTOR AT SV STATION-8 | HYDROGEN GAS DETECTOR AT SV STATION-8 |  | FG_DET | PL318SV8 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516542 | PL318XGH901 | HYDROGEN GAS DETECTOR AT SV STATION-9 | HYDROGEN GAS DETECTOR AT SV STATION-9 |  | FG_DET | PL318SV9 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516543 | PL318XHE1016 | HEAT DETECTOR AT SV Station-10 | HEAT DETECTOR AT SV Station-10 |  | FGBHFD | PL318SV10 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516544 | PL318XHE1116 | HEAT DETECTOR AT SV Station-11 | HEAT DETECTOR AT SV Station-11 |  | FGBHFD | PL318SV11 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516545 | PL318XHE1216 | HEAT DETECTOR AT SV Station-12 | HEAT DETECTOR AT SV Station-12 |  | FGBHFD | PL318SV12 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516546 | PL318XHE816 | HEAT DETECTOR AT SV Station-8 | HEAT DETECTOR AT SV Station-8 |  | FGBHFD | PL318SV8 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516547 | PL318XHE916 | HEAT DETECTOR AT SV Station-9 | HEAT DETECTOR AT SV Station-9 |  | FGBHFD | PL318SV9 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516548 | PL318XSP1015 | SMOKE DETECTOR AT SV Station-10 | SMOKE DETECTOR AT SV Station-10 |  | FGBHFD | PL318SV10 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516549 | PL318XSP1115 | SMOKE DETECTOR AT SV Station-11 | SMOKE DETECTOR AT SV Station-11 |  | FGBHFD | PL318SV11 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516550 | PL318XSP1215 | SMOKE DETECTOR AT SV Station-12 | SMOKE DETECTOR AT SV Station-12 |  | FGBHFD | PL318SV12 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516551 | PL318XSP815 | SMOKE DETECTOR AT SV Station-8 | SMOKE DETECTOR AT SV Station-8 |  | FGBHFD | PL318SV8 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516552 | PL318XSP915 | SMOKE DETECTOR AT SV Station-9 | SMOKE DETECTOR AT SV Station-9 |  | FGBHFD | PL318SV9 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516553 | PL325GDH702 | FLAMMABLE GAS DETECTOR AT SV STATION-7 | FLAMMABLE GAS DETECTOR AT SV STATION-7 |  | FG_DET | PL325SV7 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516554 | PL325XAC704 | MANUAL CALL POINT AT SV Station - 7 | MANUAL CALL POINT AT SV Station - 7 |  | PA_SYS | PL325SV7 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516555 | PL325XAC706 | MANUAL CALL POINT AT SV Station - 7 | MANUAL CALL POINT AT SV Station - 7 |  | PA_SYS | PL325SV7 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516556 | PL325XAC707 | MANUAL CALL POINT AT SV Station - 7 | MANUAL CALL POINT AT SV Station - 7 |  | PA_SYS | PL325SV7 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516557 | PL325XHE701 | HEAT DETECTOR AT SV Station-7 | HEAT DETECTOR AT SV Station-7 |  | FGBHFD | PL325SV7 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516558 | PL325XSP701 | SMOKE DETECTOR AT SV Station-7 | SMOKE DETECTOR AT SV Station-7 |  | FGBHFD | PL325SV7 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516581 | M410XHE655 | HEAT DETECTOR AT S/S BUILDING TRANSFORMER | HEAT DETECTOR AT S/S BUILDING TRANSFORMER |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516582 | M410XHE656 | HEAT DETECTOR AT S/S BUILDING TRANSFORMER | HEAT DETECTOR AT S/S BUILDING TRANSFORMER |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516583 | M410XHE657 | HEAT DETECTOR AT S/S BUILDING TRANSFORMER | HEAT DETECTOR AT S/S BUILDING TRANSFORMER |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516584 | M410XHE658 | HEAT DETECTOR AT S/S BUILDING TRANSFORMER | HEAT DETECTOR AT S/S BUILDING TRANSFORMER |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516585 | M410XHE659 | HEAT DETECTOR AT S/S BUILDING TRANSFORMER | HEAT DETECTOR AT S/S BUILDING TRANSFORMER |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516586 | M410XHE660 | HEAT DETECTOR AT S/S BUILDING TRANSFORMER | HEAT DETECTOR AT S/S BUILDING TRANSFORMER |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516587 | M410XHE661 | HEAT DETECTOR AT S/S CAPACITY BANK | HEAT DETECTOR AT S/S CAPACITY BANK |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516588 | M410XHE662 | HEAT DETECTOR AT S/S CAPACITY BANK | HEAT DETECTOR AT S/S CAPACITY BANK |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516589 | M410XHE663 | HEAT DETECTOR AT S/S BATTERY ROOM | HEAT DETECTOR AT S/S BATTERY ROOM |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516590 | M410XHE664 | HEAT DETECTOR AT S/S BATTERY ROOM | HEAT DETECTOR AT S/S BATTERY ROOM |  | FGBHFD | M410FACP002 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516591 | M410XHE739 | HEAT DETECTOR AT SIS BUILDING BATTERY ROOM | HEAT DETECTOR AT SIS BUILDING BATTERY ROOM |  | FGBHFD | M410FACP001 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516592 | M410XHE740 | HEAT DETECTOR AT SIS BUILDING BATTERY ROOM | HEAT DETECTOR AT SIS BUILDING BATTERY ROOM |  | FGBHFD | M410FACP001 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516593 | M410XYLDA031A | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031A | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031A |  | FGBFFD | M410FWCP031A | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516594 | M410XYLDA031B | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031B | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031B |  | FGBFFD | M410FWCP031B | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516595 | M410XYLDA031C | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031C | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031C |  | FGBFFD | M410FWCP031C | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516596 | M410XYLDA031D | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031D | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031D |  | FGBFFD | M410FWCP031D | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516597 | M410XYLDA031E | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031E | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031E |  | FGBFFD | M410FWCP031E | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516598 | M410XYLDA031F | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031F | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031F |  | FGBFFD | M410FWCP031F | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516599 | M410XYLDA031G | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031G | FLAME DETECTOR (UV/IR TYPE) AT 410-P-031G |  | FGBFFD | M410FWCP031G | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516600 | M410XYLDB031A | HEAT DETECTOR AT 410-P-031A | HEAT DETECTOR AT 410-P-031A |  | FGBHFD | M410FWCP031A | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516601 | M410XYLDB031B | HEAT DETECTOR AT 410-P-031B | HEAT DETECTOR AT 410-P-031B |  | FGBHFD | M410FWCP031B | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969516602 | M410XYLDB031C | HEAT DETECTOR AT 410-P-031C | HEAT DETECTOR AT 410-P-031C |  | FGBHFD | M410FWCP031C | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FFP57541 | M50XMC013 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-105 |  | PB_HS-MC | M10T105 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC013-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 17/10/18 | MFPS-PM07.M3
FFP57542 | M50XMC031 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-108 |  | PB_HS-MC | M10T108 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC031-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 26/08/18 | MFPS-PM07.M3
FFP57544 | M50XMC032 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-109 |  | PB_HS-MC | M10T109 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC032-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 17/10/18 | MFPS-PM07.M3
FFP57545 | M50XMC033 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-108 |  | PB_HS-MC | M10T108 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC033-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
FFP57546 | M50XMC034 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-109 |  | PB_HS-MC | M10T109 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC034-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
FFP57548 | M50XMC021 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-106 |  | PB_HS-MC | M10T106 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC021-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 17/10/18 | MFPS-PM07.M3
FFP57549 | M50XHD021 | DETECTOR, FIRE PROTECTION, HEAT , 24VDC , EXPLOSION PROOF , YES | LINEAR HEAT DETECTOR FOR TANK T-106 |  | FG_DET | M10T106 | 1 | FG_DET | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XHD021-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 24/09/18 | MFPS-PM05.M3
FFP57553 | M50XMC023 | CALL POINT, BREAK GLASS MANUAL , 15V MIN/30V MAX , 5MA ALARM CONTACT , IP66 & IP | MANUAL CALL POINT FOR TANK T-107 |  | PB_HS-MC | M10T107 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | M50XMC023-UFPS | ACTIVE | ELEC | PM | FIC | 3 | MONTHS | 17/10/18 | MFPS-PM07.M3
969175141 | M410PDT203 | 410-P-007B SUCTION STRAINER 410-STR-007B | 410-P-007B SUCTION STRAINER 410-STR-007B |  | PRES_TX | M410P007B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT203-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/11/18 | MC-PM-PT1-M6
969175142 | M410PDT206 | 410-P-007C SUCTION STRAINER 410-STR-007C | 410-P-007C SUCTION STRAINER 410-STR-007C |  | PRES_TX | M410P007C | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT206-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/11/18 | MC-PM-PT1-M6
969175143 | M410PDT215 | 410-P-008A SUCTION STRAINER 410-STR-008A | 410-P-008A SUCTION STRAINER 410-STR-008A |  | PRES_TX | M410P008A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT215-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/11/18 | MC-PM-PT1-M6
969175144 | M410PDT218 | 410-P-008B SUCTION STRAINER 410-STR-008B | 410-P-008B SUCTION STRAINER 410-STR-008B |  | PRES_TX | M410P008B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT218-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 11/11/18 | MC-PM-PT1-M6
969175145 | M410PDT250 | 410-P-014A SUCTION STRAINER 410-STR-014A | 410-P-014A SUCTION STRAINER 410-STR-014A |  | PRES_TX | M410P014A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT250-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 14/12/18 | MC-PM-PT1-M6
969175146 | M410PDT255 | 410-P-014B SUCTION STRAINER 410-STR-014B | 410-P-014B SUCTION STRAINER 410-STR-014B |  | PRES_TX | M410P014B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT255-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 15/12/18 | MC-PM-PT1-M6
969175147 | M410PDT450A | 410-L-004A JET A1 INTER-TANK TRANSFER FILTER COALESCER | 410-L-004A JET A1 INTER-TANK TRANSFER FILTER COALESCER |  | PRES_TX | M410L004A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT450A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/08/18 | MC-PM-PT1-M6
969175148 | M410PDT450B | 410-L-004B JET A1 INTER-TANK TRANSFER FILTER COALESCER | 410-L-004B JET A1 INTER-TANK TRANSFER FILTER COALESCER |  | PRES_TX | M410L004B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT450B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 06/08/18 | MC-PM-PT1-M6
969175149 | M410PDT450C | 410-L-004C JET A1 INTER-TANK TRANSFER FILTER COALESCER | 410-L-004C JET A1 INTER-TANK TRANSFER FILTER COALESCER |  | PRES_TX | M410L004C | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT450C-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 07/08/18 | MC-PM-PT1-M6
969175150 | M410PDT451A | 410-L-014A JET A1 PRE-FILTER | 410-L-014A JET A1 PRE-FILTER |  | PRES_TX | M410L014A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT451A-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 09/08/18 | MC-PM-PT1-M6
969175151 | M410PDT451B | 410-L-014B JET A1 PRE-FILTER | 410-L-014B JET A1 PRE-FILTER |  | PRES_TX | M410L014B | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT451B-MC1 | ACTIVE | CONT | PM | FIC | 6 | MONTHS | 10/08/18 | MC-PM-PT1-M6
969175298 | M410PG211 | 410-P-007B SUCTION | 410-P-007B SUCTION |  | INDICATR | M410P007B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175299 | M410PG212 | 410-P-007B DISCHARGE | 410-P-007B DISCHARGE |  | INDICATR | M410P007B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175300 | M410PG213 | 410-P-007C SUCTION | 410-P-007C SUCTION |  | INDICATR | M410P007C | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175301 | M410PG214 | 410-P-007C DISCHARGE | 410-P-007C DISCHARGE |  | INDICATR | M410P007C | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175302 | M410PG224 | 410-P-008A SUCTION | 410-P-008A SUCTION |  | INDICATR | M410P008A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175303 | M410PG225 | 410-P-008A DISCHARGE | 410-P-008A DISCHARGE |  | INDICATR | M410P008A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175304 | M410PG226 | 410-P-008B SUCTION | 410-P-008B SUCTION |  | INDICATR | M410P008B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175305 | M410PG227 | 410-P-008B DISCHARGE | 410-P-008B DISCHARGE |  | INDICATR | M410P008B | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175306 | M410PG252 | 410-P-014A SUCTION | 410P014A SUCTION |  | INDICATR | M410P014A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175307 | M410PG253 | 410-P-014A DISCHARGE | 410-P-014A DISCHARGE |  | INDICATR | M410P014A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175573 | M410MOV0212 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-002 |  | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0212-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969175574 | M410MOV0301 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0301-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/10/18 | ME-PM-002-M6
969175575 | M410MOV0302 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0302-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/10/18 | ME-PM-002-M6
969175576 | M410MOV0303 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0303-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/10/18 | ME-PM-002-M6
969175577 | M410MOV0304 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0304-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969175578 | M410MOV0305 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0305-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969175579 | M410MOV0306 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0306-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/10/18 | ME-PM-002-M6
969175580 | M410MOV0307 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0307-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 14/10/18 | ME-PM-002-M6
969175581 | M410MOV0308 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0308-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/10/18 | ME-PM-002-M6
969175582 | M410MOV0309 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0309-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
969175583 | M410MOV0310 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0310-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/10/18 | ME-PM-002-M6
969175584 | M410MOV0311 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0311-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/10/18 | ME-PM-002-M6
969175585 | M410MOV0312 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-003 |  | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0312-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 21/10/18 | ME-PM-002-M6
969175586 | M410MOV0401 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0401-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/10/18 | ME-PM-002-M6
969175587 | M410MOV0402 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0402-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969175588 | M410MOV0403 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0403-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/10/18 | ME-PM-002-M6
969175589 | M410MOV0404 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0404-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/10/18 | ME-PM-002-M6
969175590 | M410MOV0405 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0405-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/10/18 | ME-PM-002-M6
969175591 | M410MOV0406 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0406-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/10/18 | ME-PM-002-M6
969175592 | M410MOV0407 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0407-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969175593 | M410MOV0408 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0408-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969175594 | M410MOV0409 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0409-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/11/18 | ME-PM-002-M6
969175595 | M410MOV0410 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0410-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/11/18 | ME-PM-002-M6
969175596 | M410MOV0411 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0411-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969175597 | M410MOV0412 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-004 |  | MOV | M410T004 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0412-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969175598 | M410MOV0501 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0501-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/11/18 | ME-PM-002-M6
969175599 | M410MOV0502 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0502-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/11/18 | ME-PM-002-M6
969175600 | M410MOV0503 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0503-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/11/18 | ME-PM-002-M6
969175601 | M410MOV0504 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0504-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969175602 | M410MOV0505 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0505-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969175603 | M410MOV0506 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0506-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/11/18 | ME-PM-002-M6
969175604 | M410MOV0507 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0507-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/11/18 | ME-PM-002-M6
969175605 | M410MOV0508 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0508-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 19/11/18 | ME-PM-002-M6
969175606 | M410MOV0509 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0509-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/11/18 | ME-PM-002-M6
969175607 | M410MOV0510 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0510-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/11/18 | ME-PM-002-M6
969175608 | M410MOV0511 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0511-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/11/18 | ME-PM-002-M6
969175609 | M410MOV0512 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-005 |  | MOV | M410T005 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0512-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 22/11/18 | ME-PM-002-M6
969175610 | M410MOV0601 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0601-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 26/11/18 | ME-PM-002-M6
969175611 | M410MOV0602 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0602-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/11/18 | ME-PM-002-M6
969175612 | M410MOV0603 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0603-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/11/18 | ME-PM-002-M6
969175613 | M410MOV0604 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0604-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/11/18 | ME-PM-002-M6
969175614 | M410MOV0605 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0605-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/11/18 | ME-PM-002-M6
969175615 | M410MOV0606 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0606-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/12/18 | ME-PM-002-M6
969175616 | M410MOV0607 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0607-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/12/18 | ME-PM-002-M6
969175617 | M410MOV0608 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0608-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969175618 | M410MOV0609 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0609-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969175619 | M410MOV0610 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0610-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969175620 | M410MOV0611 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0611-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/12/18 | ME-PM-002-M6
969175621 | M410MOV0612 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-006 |  | MOV | M410T006 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0612-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/12/18 | ME-PM-002-M6
969175622 | M410MOV0701 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0701-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969175623 | M410MOV0702 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0702-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969175624 | M410MOV0703 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0703-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
969175625 | M410MOV0704 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0704-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969175626 | M410MOV0705 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0705-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
969175627 | M410MOV0706 | Motor Operated Valve(Ball) | Motor Operated Valve(Ball) OF 410-T-007 |  | MOV | M410T007 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0706-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969175785 | M410TSV006 | ULG 91 TANK 410-T-002 INLET MANIFOLD | ULG 91 TANK 410-T-002 INLET MANIFOLD |  | PSV | M410T002 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175786 | M410TSV007 | ULG 91 TANK 410-T-002 OUTLET MANIFOLD | ULG 91 TANK 410-T-002 OUTLET MANIFOLD |  | PSV | M410T002 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175787 | M410TSV008 | ULG 91 TANK 410-T-002 OUTLET MANIFOLD | ULG 91 TANK 410-T-002 OUTLET MANIFOLD |  | PSV | M410T002 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175788 | M410TSV009 | ULG 91 TANK 410-T-003 INLET MANIFOLD | ULG 91 TANK 410-T-003 INLET MANIFOLD |  | PSV | M410T003 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175789 | M410TSV010 | ULG 91 TANK 410-T-003 INLET MANIFOLD | ULG 91 TANK 410-T-003 INLET MANIFOLD |  | PSV | M410T003 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175790 | M410TSV011 | ULG 91 TANK 410-T-003 OUTLET MANIFOLD | ULG 91 TANK 410-T-003 OUTLET MANIFOLD |  | PSV | M410T003 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175791 | M410TSV012 | ULG 91 TANK 410-T-003 OUTLET MANIFOLD | ULG 91 TANK 410-T-003 OUTLET MANIFOLD |  | PSV | M410T003 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175792 | M410TSV013 | ULG 91 TANK 410-T-004 INLET MANIFOLD | ULG 91 TANK 410-T-004 INLET MANIFOLD |  | PSV | M410T004 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175793 | M410TSV014 | ULG 91 TANK 410-T-004 INLET MANIFOLD | ULG 91 TANK 410-T-004 INLET MANIFOLD |  | PSV | M410T004 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175794 | M410TSV015 | ULG 91 TANK 410-T-004 OUTLET MANIFOLD | ULG 91 TANK 410-T-004 OUTLET MANIFOLD |  | PSV | M410T004 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175795 | M410TSV016 | ULG 91 TANK 410-T-004 OUTLET MANIFOLD | ULG 91 TANK 410-T-004 OUTLET MANIFOLD |  | PSV | M410T004 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175796 | M410TSV017 | GAS OIL TANK 410-T-009 INLET MANIFOLD | GAS OIL TANK 410-T-009 INLET MANIFOLD |  | PSV | M410T009 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175797 | M410TSV018 | GAS OIL TANK 410-T-009 INLET MANIFOLD | GAS OIL TANK 410-T-009 INLET MANIFOLD |  | PSV | M410T009 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175798 | M410TSV019 | GAS OIL TANK 410-T-009 OUTLET MANIFOLD | GAS OIL TANK 410-T-009 OUTLET MANIFOLD |  | PSV | M410T009 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175799 | M410TSV020 | GAS OIL TANK 410-T-009 OUTLET MANIFOLD | GAS OIL TANK 410-T-009 OUTLET MANIFOLD |  | PSV | M410T009 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175800 | M410TSV021 | GAS OIL TANK 410-T-010 INLET MANIFOLD | GAS OIL TANK 410-T-010 INLET MANIFOLD |  | PSV | M410T010 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175801 | M410TSV022 | GAS OIL TANK 410-T-010 INLET MANIFOLD | GAS OIL TANK 410-T-010 INLET MANIFOLD |  | PSV | M410T010 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175802 | M410TSV023 | GAS OIL TANK 410-T-010 OUTLET MANIFOLD | GAS OIL TANK 410-T-010 OUTLET MANIFOLD |  | PSV | M410T010 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175803 | M410TSV024 | GAS OIL TANK 410-T-010 OUTLET MANIFOLD | GAS OIL TANK 410-T-010 OUTLET MANIFOLD |  | PSV | M410T010 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175804 | M410TSV025 | ULG 95 TANK 410-T-005 INLET MANIFOLD | ULG 95 TANK 410-T-005 INLET MANIFOLD |  | PSV | M410T005 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175805 | M410TSV026 | ULG 95 TANK 410-T-005 INLET MANIFOLD | ULG 95 TANK 410-T-005 INLET MANIFOLD |  | PSV | M410T005 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175806 | M410TSV027 | ULG 95 TANK 410-T-005 OUTLET MANIFOLD | ULG 95 TANK 410-T-005 OUTLET MANIFOLD |  | PSV | M410T005 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175807 | M410TSV028 | ULG 95 TANK 410-T-005 OUTLET MANIFOLD | ULG 95 TANK 410-T-005 OUTLET MANIFOLD |  | PSV | M410T005 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175808 | M410TSV029 | ULG 95 TANK 410-T-006 INLET MANIFOLD | ULG 95 TANK 410-T-006 INLET MANIFOLD |  | PSV | M410T006 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175809 | M410TSV030 | ULG 95 TANK 410-T-006 INLET MANIFOLD | ULG 95 TANK 410-T-006 INLET MANIFOLD |  | PSV | M410T006 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175810 | M410TSV031 | ULG 95 TANK 410-T-006 OUTLET MANIFOLD | ULG 95 TANK 410-T-006 OUTLET MANIFOLD |  | PSV | M410T006 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175811 | M410TSV032 | ULG 95 TANK 410-T-006 OUTLET MANIFOLD | ULG 95 TANK 410-T-006 OUTLET MANIFOLD |  | PSV | M410T006 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175812 | M410TSV033 | ULG 95 TANK 410-T-007 INLET MANIFOLD | ULG 95 TANK 410-T-007 INLET MANIFOLD |  | PSV | M410T007 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175813 | M410TSV034 | ULG 95 TANK 410-T-007 INLET MANIFOLD | ULG 95 TANK 410-T-007 INLET MANIFOLD |  | PSV | M410T007 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175814 | M410TSV035 | ULG 95 TANK 410-T-007 OUTLET MANIFOLD | ULG 95 TANK 410-T-007 OUTLET MANIFOLD |  | PSV | M410T007 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175815 | M410TSV036 | ULG 95 TANK 410-T-007 OUTLET MANIFOLD | ULG 95 TANK 410-T-007 OUTLET MANIFOLD |  | PSV | M410T007 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175816 | M410TSV037 | ULG 95 TANK 410-T-008 INLET MANIFOLD | ULG 95 TANK 410-T-008 INLET MANIFOLD |  | PSV | M410T008 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175817 | M410TSV038 | ULG 95 TANK 410-T-008 INLET MANIFOLD | ULG 95 TANK 410-T-008 INLET MANIFOLD |  | PSV | M410T008 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175818 | M410TSV039 | ULG 95 TANK 410-T-008 OUTLET MANIFOLD | ULG 95 TANK 410-T-008 OUTLET MANIFOLD |  | PSV | M410T008 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175819 | M410TSV040 | ULG 95 TANK 410-T-008 OUTLET MANIFOLD | ULG 95 TANK 410-T-008 OUTLET MANIFOLD |  | PSV | M410T008 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175820 | M410TSV041 | GAS OIL TANK 410-T-009 INLET MANIFOLD | GAS OIL TANK 410-T-009 INLET MANIFOLD |  | PSV | M410T009 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175821 | M410TSV042 | GAS OIL TANK 410-T-010 INLET MANIFOLD | GAS OIL TANK 410-T-010 INLET MANIFOLD |  | PSV | M410T010 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175822 | M410TSV050 | JET A1 TANK 410-T-011 INLET MANIFOLD | JET A1 TANK 410-T-011 INLET MANIFOLD |  | PSV | M410T011 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175823 | M410TSV051 | JET A1 TANK 410-T-011 OUTLET MANIFOLD | JET A1 TANK 410-T-011 OUTLET MANIFOLD |  | PSV | M410T011 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175824 | M410TSV052 | JET A1 TANK 410-T-011 INLET MANIFOLD | JET A1 TANK 410-T-011 INLET MANIFOLD |  | PSV | M410T011 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175825 | M410TSV053 | JET A1 TANK 410-T-011 OUTLET MANIFOLD | JET A1 TANK 410-T-011 OUTLET MANIFOLD |  | PSV | M410T011 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175826 | M410TSV054 | JET A1 TANK 410-T-012 INLET MANIFOLD | JET A1 TANK 410-T-012 INLET MANIFOLD |  | PSV | M410T012 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175827 | M410TSV055 | JET A1 TANK 410-T-012 OUTLET MANIFOLD | JET A1 TANK 410-T-012 OUTLET MANIFOLD |  | PSV | M410T012 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175828 | M410TSV056 | JET A1 TANK 410-T-012 INLET MANIFOLD | JET A1 TANK 410-T-012 INLET MANIFOLD |  | PSV | M410T012 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175829 | M410TSV057 | JET A1 TANK 410-T-012 OUTLET MANIFOLD | JET A1 TANK 410-T-012 OUTLET MANIFOLD |  | PSV | M410T012 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175830 | M410TSV058 | JET A1 TANK 410-T-013 INLET MANIFOLD | JET A1 TANK 410-T-013 INLET MANIFOLD |  | PSV | M410T013 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175831 | M410TSV059 | JET A1 TANK 410-T-013 INLET MANIFOLD | JET A1 TANK 410-T-013 INLET MANIFOLD |  | PSV | M410T013 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175832 | M410TSV060 | JET A1 TANK 410-T-013 OUTLET MANIFOLD | JET A1 TANK 410-T-013 OUTLET MANIFOLD |  | PSV | M410T013 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969175833 | M410TSV061 | JET A1 TANK 410-T-013 OUTLET MANIFOLD | JET A1 TANK 410-T-013 OUTLET MANIFOLD |  | PSV | M410T013 | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275656 | PL312V001 | ULG / GAS OIL SUMP VESSEL | ULG / GAS OIL SUMP VESSEL |  | VESSEL | PL312VESSEL | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 10 | 50 | 5 | 50 | 10 | 5 | 6.7959 | High | Medium | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275657 | PL312XGH101 | HC GAS DETECTOR | HC GAS DETECTOR |  | FG_DET | PL312GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275658 | PL312XHE117 | HEAT DETECTOR | HEAT DETECTOR |  | FG_DET | PL312GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275659 | PL312XSP116 | SMOKE DETECTOR | SMOKE DETECTOR |  | FG_DET | PL312GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275660 | PL312YYIS001 | MONITOR PIG PASSAGE INDICATOR | MONITOR PIG PASSAGE INDICATOR |  | PIPING | PL312MISC | 2 | PIPING | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275744 | PL318CCTV001 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Explosion Proof PTZ | CAMERA FOR CLOSE CIRCUIT TELEVISION/Explosion Proof PTZ |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275745 | PL318CCTV004 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) | CAMERA FOR CLOSE CIRCUIT TELEVISION/Short range Thermal Fixed (50mm) |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275746 | PL318CCTV005 | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) | CAMERA FOR CLOSE CIRCUIT TELEVISION/Medium range Thermal Fixed (100mm) |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275748 | PL318CPPSM001 | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE |  | TRANSFMR | PL318SCB | 3 | TRANSFMR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275749 | PL318CPPSM002 | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE | TRANSFOMER / RECTIFIER REMOTE MONITORING AND CONTROL TYPE |  | TRANSFMR | PL318SCB | 3 | TRANSFMR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275360 | PL318EOV31808 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275750 | PL318EOV31808 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | 969275360 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275361 | PL318EOV31809 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275751 | PL318EOV31809 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | 969275361 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275362 | PL318EOV31810 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275752 | PL318EOV31810 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | 969275362 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275363 | PL318EOV31811 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275753 | PL318EOV31811 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | 969275363 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275364 | PL318EOV31812 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275754 | PL318EOV31812 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-318-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | 969275364 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275365 | PL318EOV31908 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275755 | PL318EOV31908 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | 969275365 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275366 | PL318EOV31909 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275756 | PL318EOV31909 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | 969275366 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275367 | PL318EOV31910 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275757 | PL318EOV31910 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | 969275367 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275368 | PL318EOV31911 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275758 | PL318EOV31911 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | 969275368 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275369 | PL318EOV31912 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 |  | CONTHNDV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275759 | PL318EOV31912 | ACTUATOR FOR ELECTRO HYDRAULIC VALVE 318-EOV-319-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | 969275369 | MOV | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275760 | PL318GAV21223001 | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275761 | PL318GAV21223002 | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 800, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275762 | PL318GAV21223003 | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275763 | PL318GAV21223004 | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 0.5" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275764 | PL318GAV21223005 | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge | 1" Gate Valve, ISO 15761, Class 1500, Socket Weld End x Female Threaded End, Bolted Bonnet OS&Y, Handwheel Operator, ASTM A105, Trim 13Cr w/Stellite Seats & Disc, Solid Wedge |  | CONTHNDV | PL318VALVE | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275765 | PL318GDH1001 | HC GAS DETECTOR | HC GAS DETECTOR |  | FG_DET | PL318GD | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275781 | PL318PG31808A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275782 | PL318PG31808B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275783 | PL318PG31809A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275784 | PL318PG31809B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275785 | PL318PG31810A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275786 | PL318PG31810B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275787 | PL318PG31811A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275788 | PL318PG31811B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275789 | PL318PG31812A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275790 | PL318PG31812B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275791 | PL318PG31908A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275792 | PL318PG31908B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275793 | PL318PG31909A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275794 | PL318PG31909B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275795 | PL318PG31910A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275796 | PL318PG31910B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275797 | PL318PG31911A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275798 | PL318PG31911B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275799 | PL318PG31912A | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275800 | PL318PG31912B | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | PL318PRESS | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275801 | PL318PT31808A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275802 | PL318PT31808B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275803 | PL318PT31809A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275804 | PL318PT31809B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275805 | PL318PT31810A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275806 | PL318PT31810B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275807 | PL318PT31811A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275808 | PL318PT31811B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275809 | PL318PT31812A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275810 | PL318PT31812B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275811 | PL318PT31908A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275812 | PL318PT31908B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275813 | PL318PT31909A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275814 | PL318PT31909B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275815 | PL318PT31910A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275816 | PL318PT31910B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275817 | PL318PT31911A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275818 | PL318PT31911B | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275819 | PL318PT31912A | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | PL318PRESS | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275983 | M400VS917 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 117 | 939610 | VALCH | M400T117 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275985 | M400VS919 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 119 | 939612 | VALCH | M400T119 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417842 | PL300BATT006C | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-C =38 Nos FOR SV-6. |  | BATTERY | PL300BAT006 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417843 | PL300BATT006D | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-D =38 Nos FOR SV-6. |  | BATTERY | PL300BAT006 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417844 | PL300BATT005C | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-C =38 Nos FOR SV-5. |  | BATTERY | PL300BAT005 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417845 | PL300BATT005D | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-D =38 Nos FOR SV-5. |  | BATTERY | PL300BAT005 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417846 | PL300BATT004C | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-C =38 Nos FOR SV-4. |  | BATTERY | PL300BAT004 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417847 | PL300BATT004D | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-D =38 Nos FOR SV-4. |  | BATTERY | PL300BAT004 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417848 | PL300BATT003C | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-C =38 Nos FOR SV-3. |  | BATTERY | PL300BAT003 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417849 | PL300BATT003D | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-D =38 Nos FOR SV-3. |  | BATTERY | PL300BAT003 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417850 | PL300BATT001C | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-C =38 Nos FOR SV-1. |  | BATTERY | PL300BAT001 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417851 | PL300BATT001D | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-D =38 Nos FOR SV-1. |  | BATTERY | PL300BAT001 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417852 | PL300BATT002C | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-C =38 Nos FOR SV-2. |  | BATTERY | PL300BAT002 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417853 | PL300BATT002D | BATTERY,BANK, Ni-Cd, 1650 AH, 48 V. | BATTERY BANK-D =38 Nos FOR SV-2. |  | BATTERY | PL300BAT002 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195323 | M410BAV2351007 | 8" TBV SS316 150#, RF, GEAR OPERATED | 8" TBV SS316 150#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195324 | M410BAV2351008 | 10" TBV SS316 150#, RF, GEAR OPERATED | 10" TBV SS316 150#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195325 | M410BAV2351009 | 12" TBV SS316 150#, RF, GEAR OPERATED | 12" TBV SS316 150#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195326 | M410BAV2351010 | 14" TBV SS316 150#, RF, GEAR OPERATED | 14" TBV SS316 150#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195327 | M410BAV2351011 | 16" TBV SS316 150#, RF, GEAR OPERATED | 16" TBV SS316 150#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195328 | M410BAV2351012 | 18" TBV SS316 150#, RF, GEAR OPERATED | 18" TBV SS316 150#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195329 | M410BAV2351013 | 1" FBV SS316L 150#, RF, LEVER OPERATED | 1" FBV SS316L 150#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195330 | M410BAV2351014 | 2" FBV SS316 150#, RF, LEVER OPERATED | 2" FBV SS316 150#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195331 | M410BAV2351015 | 28" TBV SS316 150#, RF, GEAR OPERATED | 28" TBV SS316 150#, RF, GEAR OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195332 | M410BAV2351016 | 2" FBV SS316 300#, RF, LEVER OPERATED | 2" FBV SS316 300#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195333 | M410BAV2351017 | 3" FBV SS316 300#, RF, LEVER OPERATED | 3" FBV SS316 300#, RF, LEVER OPERATED |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IIP97814 | U51PT145 | TRANSMITTER, PRESSURE, DIAPHRAGM , 4-20MADC , 24VDC , 1/2" NPT , M20 X 1.5 , NEM | LPG TO MUSSAFFAH PRESSURE TRANSMITTER | IIP97807 | PRES_TX | U51PI145 | 2 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD58270 | S15PSLL151 | SWITCH, PRESSURE, DIAPHRAGM , 110/250VAC 5A, 30VDC 2A , 4-28 BAR , SPDT , IP66 , | PRESSURE SWITCH LOW AFTER 15MOV116 | ISD58269 | PRES_SWT | S15R03 | 1 | PRES_SWT | 623101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59015 | M41ESD541 | VALVE, SEQUENCIAL CONTROL/ESD, HC PRODUCT , 10.5 BAR , -30 TO +100 DEG.C , BIFFI | ESD VALVE FOR MULTIPRODUCT INLET METERING |  | EMERSDD | M10INLETMET | 1 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59042 | M10HZL011.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-101 | TNK56513 | PB_HS-MC | M10T101 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59064 | M10HZL011.2 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-102 | TNK56531 | PB_HS-MC | M10T102 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59086 | M10HZL011.3 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-103 | TNK56547 | PB_HS-MC | M10T103 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59106 | M10HZL041.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-104 | TNK56565 | PB_HS-MC | M10T104 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59126 | M10HZL051.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-105 | TNK56585 | PB_HS-MC | M10T105 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59146 | M10HZL061.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-106 | TNK56600 | PB_HS-MC | M10T106 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59166 | M10HZL071.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTON FOR TANK T-107 | TNK56616 | PB_HS-MC | M10T107 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59188 | M10HZL081.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-108 | TNK56634 | PB_HS-MC | M10T108 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59205 | M10HZL091.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD PUSH BUTTON FOR TANK T-109 | TNK56645 | PB_HS-MC | M10T109 | 1 | PB_HS-MC | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59223 | M41ESD601 | VALVE,SEQUENCIAL CONTROL/ESD | OUTLET ESD VALVE FOR TANK T-110 | TNK56656 | EMERSDD | M10T110 | 1 | EMERSDD | 616101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISD59224 | M10HZL101.1 | SWITCH, PUSH BUTTON, SPDT , 1NC , AMBER YELLOW , PANEL | ESD FOR TANK T-110 | TNK56656 | PB_HS-MC | M10T110 | 1 | SD_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969424803 | M410BATT001A | 170 CELLS (SLM 850-1) FOR DC UPS 410UPSDC001A IN SS410. | 170 CELLS (SLM 850-1) FOR DC UPS 410UPSDC001A IN SS410. |  | BATTERY | M410UPSDC001A | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410BATT001A-ME1 | ACTIVE | ELEC | PM | EDS | 3 | MONTHS | 20/10/18 | ME-PM-001-M6
969424804 | M410BATT001B | 170 CELLS (SLM 850-1) FOR DC UPS 410UPSDC001B IN SS410. | 170 CELLS (SLM 850-1) FOR DC UPS 410UPSDC001B IN SS410. |  | BATTERY | M410UPSDC001B | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969424805 | M410BATT002A | 360 CELLS (SLM 710-1) FOR AC UPS 410AUPSAC001A IN SIS BUILDING. | 360 CELLS (SLM 710-1) FOR AC UPS 410AUPSAC001A IN SIS BUILDING. |  | BATTERY | M410UPSAC001A | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969424806 | M410BATT002B | 360 CELLS (SLM 710-1) FOR AC UPS 410AUPSAC001B IN SIS BUILDING. | 360 CELLS (SLM 710-1) FOR AC UPS 410AUPSAC001B IN SIS BUILDING. |  | BATTERY | M410UPSAC001B | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969424807 | M410BATT003A | 360 CELLS (SLM 710-1) FOR AC UPS 410AUPSAC002A IN SIS BUILDING. | 360 CELLS (SLM 710-1) FOR AC UPS 410UPSAC002A IN ECR BUILDING. |  | BATTERY | M410UPSAC002A | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969424808 | M410BATT003B | 360 CELLS (SLM 710-1) FOR AC UPS 410AUPSAC002B IN SIS BUILDING. | 360 CELLS (SLM 710-1) FOR AC UPS 410UPSAC002B IN ECR BUILDING. |  | BATTERY | M410UPSAC002B | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56159 | S15PSV135 | VALVE, SAFETY RELIEF, RELIEF/CONVENTIONAL , PIG LAUNCHER , 1" X 1" , 300 LB , 47 | PSV ON PIG LAUNCHER LINE. |  | PSV | S15R03 | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56160 | S15PSV136 | VALVE, SAFETY RELIEF, RELIEF/CONVENTIONAL , DISCH FROM LAUNCHER , 1" X 1" , 300 | PSV ON PIG LAUNCHER LINE. |  | PSV | S15R03 | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56164 | S21PSV104 | VALVE, SAFETY RELIEF, DIRECT SPRING LOADED /CONVENTIONAL(CLOSED) , RELIEF V / V | MAIN LINE TO ADIA AFTER MOV109. |  | PSV | S21R02 | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56167 | S21PSV106 | SAFETY RELIEF VALVE, 3/4" MNPT X 1" FNPT, SET PRESSURE 44.10BAR | PIG LAUNCHER LINE. |  | PSV | S21R02 | 1 | PSV | 623101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56501 | M10PSV301 | VALVE, SAFETY RELIEF, THERMAL RELIEF , MULTIPRD , 1" X 1" , 300 LB , 30 KG/CM2 , | PSV MULTIPRODUCT INLET METERING |  | PSV | M10INLETMET | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56502 | M10PSV302 | VALVE, SAFETY RELIEF, THERMAL RELIEF , MULTIPRD , 1" X 1" , 300 LB , 30 KG/CM2 , | PSV MULTIPRODUCT INLET METERING |  | PSV | M10INLETMET | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56507 | M10PSV303 | VALVE, SAFETY RELIEF, THERMAL RELIEF , MULTIPRD , 1" X 1" , 300 LB , 30 KG/CM2 , | PSV FOR MULTI PRODUCT INLET MANIFOLD |  | PSV | M10INLETMAN | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56508 | M10PSV304 | VALVE, SAFETY RELIEF, THERMAL , MULTIPRD , 1" X 1" , 300 LB , 30 KG/CM2 , N/A KG | PRESSURE RELIEF VALVE FOR MANIFOLD |  | PSV | M10INLETMAN | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56509 | M10PSV305 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 KG/CM2 , | PRESSURE RELIEF VALVE FOR MANIFOLD |  | PSV | M10INLETMAN | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56510 | M10PSV306 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 97 OCTANE , 1" X 1" , 300 LB , 30 KG/CM | PRESSURE RELIEF VALVE FOR MANIFOLD |  | PSV | M10INLETMAN | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56511 | M10PSV307 | VALVE, SAFETY RELIEF, THERMAL RELIEF , 90 OCTANE , 1" X 1" , 300 LB , 30 KG/CM2 | PRESSURE RELIEF VALVE FOR MANIFOLD |  | PSV | M10INLETMAN | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56512 | M10PSV308 | VALVE, SAFETY RELIEF, THERMAL RELIEF , KEROSENE , 1" X 1" , 300 LB , 30 KG/CM2 , | PRESSURE RELIEF VALVE FOR MANIFOLD |  | PSV | M10INLETMAN | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56514 | M10PSV011 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 BAR , N/A | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56515 | M10PSV012 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 KG/CM2 , N | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56516 | M10PSV013 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56517 | M10PSV014 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 KG/CM2 , N | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56518 | M10PRV015 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF VALVE FOR OUTLET TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56519 | M10VRV011A | VALVE, SAFETY RELIEF, FIG 121 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING | VACUUM RELIEF VALVE FOR TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56520 | M10VRV011B | VALVE, SAFETY RELIEF, GASOIL , FLANGED , SS AISI 316 , MR-01-75 | VACUUM RELIEF VALVE FOR TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56521 | M10VRV011C | VALVE, SAFETY RELIEF, FIG 301 , GASOIL , FLANGED , SS AISI 316 , PLAIN LIFTING L | VACUUM RELIEF VALVE FOR TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56522 | M10VRV011D |  | VACUUM RELIEF VALVE FOR TANK T-101 |  | PSV | M10T101 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56532 | M10PSV021 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 KG/CM2 , N | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56533 | M10PSV022 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 300 LB , 30 KG/CM2 , N | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56534 | M10PSV023 | VALVE, SAFETY RELIEF, THERMAL RELIEF , GASOIL , 1" X 1" , 150 LB , 5.0 KGF/CM2 , | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVS56535 | M10PSV024 | VALVE SAFETY RELIEF | PRESSURE RELIEF SAFETY VALVE FOR INLET TANK T-102 |  | PSV | M10T102 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477036 | PL318HCU90101 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-9 |  | PACKAGE | PLPL318SVS9 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477037 | PL318HCU90102 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-9 |  | PACKAGE | PLPL318SVS9 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132712 | M400TT257 | TRANSMITTER,TEMPERATURE | OUTFLOW QUALITY CONTROL - T |  | TEMP_TX | M400TEMP | 2 | TEMP_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132713 | M400AT714 | PH ANALYZER | CHAIN-1 QUALITY CONTROL - PH ANALYZER. |  | ANALYSER | M400WWTPANALZ | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132714 | M400AT715 | PH ANALYZER | CHAIN-1 QUALITY CONTROL-PH ANALYZER. |  | ANALYSER | M400WWTPANALZ | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132715 | M400AT741 | AIR QUALITY ANALYZER | EXHAUST GAS QUALITY CONTROL ANALYZER OF AC ABSORBER B |  | ANALYSER | M400WWTPANALZ | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132716 | M400AT742 | AIR QUALITY ANALYZER | EXHAUST GAS QUALITY CONTROL ANALYZER OF AC ABSORBER C |  | ANALYSER | M400WWTPANALZ | 3 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132717 | M400FE254 | METER,FLOW | FLOW METERING SYSTEM-OUTFLOW |  | FL_MTR | M400WWTPFLOW | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132718 | M400FE704 | METER,FLOW | FLOW METERING SYSTEM-FEED PUMPS CHAIN-1 |  | FL_MTR | M400WWTPFLOW | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132719 | M400FE708 | METER,FLOW | FLOW METERING SYSTEM - FEED PUMPS DAF |  | FL_MTR | M400WWTPFLOW | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132720 | M400FE724 | METER,FLOW | FLOW METERING SYSTEM-FEED PUMPS CHAIN-II |  | FL_MTR | M400WWTPFLOW | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132721 | M400FE728 | METER,FLOW | FLOW METERING SYSTEM-EVACUATION PUMPS |  | FL_MTR | M400WWTPFLOW | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132722 | M400FE738 | METER,FLOW | FLOW METERING SYSTEM - FEED PUMPS TO AIR STRIPPER |  | FL_MTR | M400WWTPFLOW | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132723 | M400FE746 | METER,FLOW | FLOW METERING SYSTEM - FEED PUMPS AC FILTERS |  | FL_MTR | M400WWTPFLOW | 2 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132724 | M400FI282 | FLOW CONTROLLER - UTILITY WATER SUPPLY | FLOW CONTROLLER - UTILITY WATER SUPPLY |  | OPENLOOP | M400WWTPFLOW | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132725 | M400FI283 | FLOW CONTROLLER- PROCESS AIR SUPPLY | FLOW CONTROLLER- PROCESS AIR SUPPLY |  | OPENLOOP | M400WWTPFLOW | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132726 | M400FI711 | FLOW CONTROLLER-COAGULANT DOSING PUMPS | FLOW CONTROLLER-COAGULANT DOSING PUMPS |  | OPENLOOP | M400WWTPFLOW | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132727 | M400FI716 | FLOW CONTROLLER - CAUSTIC SODA DOSING PUMPS | FLOW CONTROLLER - CAUSTIC SODA DOSING PUMPS |  | OPENLOOP | M400WWTPFLOW | 3 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132729 | M400FSLL711 | SWITCH,FLOW | FLOW CONTROLLER- COAGULANT DOSINGS PUMPS |  | FL_SWT | M400WWTPFLOW | 1 | FL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132737 | M400LSHH712 | SWITCH,LEVEL | LEVEL SWITCH-CAUSTIC SODA STORAGE TANK |  | LVL_SWT | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131906 | M400LEP03 | EARTHING SYSTEM | EARTHING PIT NEAR 400VSD016BTR FOR LIGHTING SYSTEM AT SUB STATION |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400LEP03-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 22/11/18 | ME-PM-004-Y1
969131907 | M400LEP08 | EARTHING SYSTEM | EARTHING PIT NEAR DG SET FOR LIGHTING SYSTEM AT SUB STATION |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400LEP08-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 24/05/19 | ME-PM-004-Y1
969131908 | M400LEP07 | EARTHING SYSTEM | EARTHING PIT NEAR 400TMM001A FOR LIGHTING SYSTEM AT SUB STATION |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400LEP07-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 17/01/19 | ME-PM-004-Y1
969131909 | M400EP02 | EARTHING SYSTEM | EARTHING PIT FOR SUBSTATION 400 |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400EP02-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 21/06/19 | ME-PM-004-Y1
969131910 | M400EP03 | EARTHING SYSTEM | EARTHING PIT FOR SUBSTATION 400 |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400EP03-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 19/07/19 | ME-PM-004-Y1
969131911 | M400LEP06 | EARTHING SYSTEM | EARTHING PIT NEAR 400TMM001B FOR LIGHTING SYSTEM AT SUB STATION |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400LEP06-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 21/12/18 | ME-PM-004-Y1
969131912 | M400LEP05 | EARTHING SYSTEM | EARTHING PIT FOR LIGHTING SYSTEM AT SUB STATION |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400LEP05-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 20/12/18 | ME-PM-004-Y1
969131913 | M400LEP04 | EARTHING SYSTEM | EARTHING PIT FOR LIGHTING SYSTEM AT SUB STATION |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400LEP04-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 23/11/18 | ME-PM-004-Y1
969131914 | M400EP04 | EARTHING SYSTEM | EARTHING PIT FOR SUBSTATION 400 |  | ERTH_NET | M400SUBSTN | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400EP04-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 16/08/18 | ME-PM-004-Y1
969131915 | M400EP09 | EARTHING SYSTEM | EARTHING PIT NEAR GATE NO.8 BATTERY LIMIT AREA |  | ERTH_NET | M400TANKS | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400EP09-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 20/09/18 | ME-PM-004-Y1
969131916 | M400EP10 | EARTHING SYSTEM | EARTHING PIT NEAR GATE NO.7 |  | ERTH_NET | M400TANKS | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400EP10-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 21/09/18 | ME-PM-004-Y1
969131917 | M400EP11 | EARTHING SYSTEM | EARTHING PIT NEAR GATE NO.6 |  | ERTH_NET | M400TANKS | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400EP11-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/10/18 | ME-PM-004-Y1
969131918 | M400EP13 | EARTHING SYSTEM | EARTHING PIT NEAR GATE NO.5 |  | ERTH_NET | M400TANKS | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400EP13-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 19/10/18 | ME-PM-004-Y1
969131919 | MMCRLEP05 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCRLEP05-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/04/19 | ME-PM-004-Y1
969131920 | MMCRLEP06 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCRLEP06-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 19/04/19 | ME-PM-004-Y1
969131921 | MMCRLEP07 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCRLEP07-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 23/05/19 | ME-PM-004-Y1
969131923 | MMCRLEP01 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCRLEP01-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 21/02/19 | ME-PM-004-Y1
969131924 | MMCRLEP02 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCRLEP02-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 22/02/19 | ME-PM-004-Y1
969131925 | MMCRLEP03 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCRLEP03-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 21/03/19 | ME-PM-004-Y1
969131926 | MMCRLEP04 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 1 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCRLEP04-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 22/03/19 | ME-PM-004-Y1
969131927 | MMCREP08 | EARTHING SYSTEM | EARTHING PIT FOR MUSAFFAH MAIN CONTROL ROOM |  | ERTH_NET | MMCR | 3 | ERTH_NET | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | MMCREP08-ME1 | ACTIVE | ELEC | PM | EDS | 1 | YEARS | 18/01/19 | ME-PM-004-Y1
969131931 | MQ600XAC002 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT HVAC ROOM(OUTSIDE) MAQTA TERMINAL |  | PB_HS-MC | MQ600FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XAC002-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131933 | MQ600XAC201 | CALL POINT, YES, BREAK GLASS MANUAL, RED | MANUAL CALL POINT AT SUMP TANK AREA MAQTA TERMINAL |  | PB_HS-MC | MQ600FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XAC201-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131938 | MQ600XSP001 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131948 | MQ600XSP011 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131950 | MQ600XSP013 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT HVAC ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131928 | MQ600FACP001 | PANEL,FIRE ALARM | FIRE ALARM CONTROL PANEL AT MAQTA TERMINAL |  | F&G_PNL | MQ600 | 1 | F&G_PNL | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600FACP001-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM01.M3
969131929 | MQ600FSP001 | PANEL,FIRE ALARM | FIRE SUPPRESSION PANEL AT MAQTA TERMINAL |  | F&G_PNL | MQ600FACP001 | 1 | F&G_PNL | 616101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600FSP001-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM10.M3
969131930 | MQ600XAC001 | CALL POINT, BREAK GLASS MANUAL, RED, YES | MANUAL CALL POINT AT SCADA ROOM MAQTA TERMINAL |  | PB_HS-MC | MQ600FACP001 | 1 | PB_HS-MC | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XAC001-UFPS | INACTIVE | ELEC | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM07.M3
969131949 | MQ600XSP012 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131953 | MQ600XSP016 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT HVAC AIR INTAKE DUCT OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132044 | PL300BATT007B | BATTERY,BANK, Ni-Cd, 1000 AH, 48 V, YES | BATTERY BANK-B =38 Nos FOR SV-7. |  | BATTERY | PL300BAT007 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969132053 | MQ600XGC202 | GAS FLAMMABLE GAS DETECTOR | FLAMMABLE GAS DETECTOR SUMP TANK |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XGC202-MFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM02.M3
969132054 | MQ600XGC203 | GAS FLAMMABLE GAS DETECTOR | FLAMMABLE GAS DETECTOR SUMP TANK |  | FG_DET | MQ600 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | MQ600XGC203-MFPS | INACTIVE | CONT | PM | FIC | 3 | MONTHS | 05/07/18 | MFPS-PM02.M3
969131939 | MQ600XSP002 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131940 | MQ600XSP003 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131941 | MQ600XSP004 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131943 | MQ600XSP006 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131945 | MQ600XSP008 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131946 | MQ600XSP009 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT SCADA ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131951 | MQ600XSP014 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT HVAC ROOM OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131954 | MQ600XSP017 | DETECTOR,FIRE PROTECTION, OPTICAL SMOKE, YES | SMOKE DETECTOR AT HVAC AIR INTAKE DUCT OF MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 1 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969131993 | MQ600PDB001 | PANEL,ELEC POWER, DISTRIBUTION, 240V/24V, 200VA, 50HZ, YES | SMALL POWER PANEL FOR FIRE AND GAS SYSTEM |  | LIGHT | MQ600PC001 | 1 | LIGHT | 616101-310600 | IRPMAQTA | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 6 | d | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477028 | PL318HCU100101 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-10 |  | PACKAGE | PLPL318SVS10 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477029 | PL318HCU100102 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-10 |  | PACKAGE | PLPL318SVS10 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477030 | PL318HCU110101 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-11 |  | PACKAGE | PLPL318SVS11 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477031 | PL318HCU110102 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-11 |  | PACKAGE | PLPL318SVS11 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477032 | PL318HCU120101 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-12 |  | PACKAGE | PLPL318SVS12 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477033 | PL318HCU120102 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-12 |  | PACKAGE | PLPL318SVS12 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477034 | PL318HCU80101 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-8 |  | PACKAGE | PLPL318SVS8 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969477035 | PL318HCU80102 | HYDRAULIC POWER UNIT | HYDRAULIC POWER UNIT, SV STATION-8 |  | PACKAGE | PLPL318SVS8 | 2 | PACKAGE | 0 | MUSS.–AL AIN PL | OPERATING | 10 | 100 | 10 | 5 | 100 | 5 | 7.3979 | High | Medium | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271750 | M410STR904 | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969271751 | M410STR904B | STRAINER | STRAINER |  | TRST | M410FILTER | 3 | TRST | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37146 | UTOYOTA52692 | 12 / 52692 - TOYOTA HILUX PICK-UP | TOYOTA HILUX PICK-UP 12 / 52692 |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA52692UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 09/08/18 | MM-PM-029-M1
969147421 | M410T010 | GAS OIL STORAGE TANK | GAS OIL STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147422 | M410T011 | JET A1 STORAGE TANK | JET A1 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147423 | M410T012 | JET A1 STORAGE TANK | JET A1 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147424 | M410T013 | JET A1 STORAGE TANK | JET A1 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147425 | M410T014 | JET A1 STORAGE TANK | JET A1 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969147426 | M410T015 | JET A1 STORAGE TANK | JET A1 STORAGE TANK |  | VESSEL | M410VESSEL | 1 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205272 | M410INS2308001 | FCM -1 MODULE | INERGEN GAS SYSTEM | 969175977 |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205283 | M410INS2308001 | KDM-R2 DISPLAY ,ODULE | INERGEN GAS SYSTEM | 969175977 |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205288 | M410FACP001 | COMMUNICATION CARD - SIMPLEX | FIRE ALARM CONTROL PANEL IN THE SIS BUILDING. | 969195600 |  | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205433 | M410MP032B | FIRE WATER PUMP- MOTOR | FIRE WATER PUMP- MOTOR |  | MOTOR | M410P032B | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MP032B-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 25/11/18 | MC-PM-02-M6
969278684 | PL312CCTV112 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278685 | PL312CCTV113 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278686 | PL312CCTV114 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278687 | PL312CCTV115 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278688 | PL312CCTV116 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL312TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278772 | PL315CCTV011 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278773 | PL315CCTV012 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278774 | PL315CCTV013 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278775 | PL315CCTV014 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278776 | PL315CCTV015 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278777 | PL315CCTV016 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278778 | PL315CCTV017 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278779 | PL315CCTV018 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278780 | PL315CCTV019 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278781 | PL315CCTV020 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278782 | PL315CCTV021 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278783 | PL315CCTV022 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278784 | PL315CCTV023 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278785 | PL315CCTV024 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278786 | PL315CCTV025 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278787 | PL315CCTV026 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278788 | PL315CCTV027 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278789 | PL315CCTV028 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278790 | PL315CCTV029 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278791 | PL315CCTV030 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278792 | PL315CCTV031 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL315TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278794 | PL315TEL001 | SDH/ACS SHARED CABINET | SDH/ACS SHARED CABINET |  | BLDGS | PL315MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278795 | PL318CCTV002 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278796 | PL318CCTV003 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278797 | PL318CCTV006 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278798 | PL318CCTV007 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278799 | PL318CCTV008 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278800 | PL318CCTV009 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278801 | PL318CCTV010 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278802 | PL318CCTV011 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278803 | PL318CCTV012 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278804 | PL318CCTV013 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278805 | PL318CCTV014 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278806 | PL318CCTV015 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278807 | PL318CCTV016 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278808 | PL318CCTV017 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278809 | PL318CCTV018 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278810 | PL318CCTV019 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278811 | PL318CCTV020 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278812 | PL318CCTV021 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278813 | PL318CCTV022 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278814 | PL318CCTV023 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278815 | PL318CCTV024 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278816 | PL318CCTV025 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278817 | PL318CCTV026 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278818 | PL318CCTV027 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278819 | PL318CCTV028 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278820 | PL318CCTV029 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278821 | PL318CCTV030 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278822 | PL318CCTV031 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278823 | PL318CCTV032 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278824 | PL318CCTV033 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278825 | PL318CCTV034 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278826 | PL318CCTV035 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278827 | PL318CCTV036 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278828 | PL318CCTV037 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278829 | PL318CCTV038 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278830 | PL318CCTV039 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278831 | PL318CCTV040 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278832 | PL318CCTV041 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278833 | PL318CCTV042 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278834 | PL318CCTV043 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278835 | PL318CCTV044 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278836 | PL318CCTV045 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278837 | PL318CCTV046 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278838 | PL318CCTV047 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278839 | PL318CCTV048 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278840 | PL318CCTV049 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278841 | PL318CCTV050 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278842 | PL318CCTV051 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278843 | PL318CCTV052 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278844 | PL318CCTV053 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278845 | PL318CCTV054 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278846 | PL318CCTV055 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278847 | PL318CCTV056 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278848 | PL318CCTV057 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278849 | PL318CCTV058 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278850 | PL318CCTV059 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353319 | PL318EOV31810 | HYDRAULIC CONTROL UNIT FOR 318-EOV-318-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | 969275362 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353320 | PL318EOV31910 | HYDRAULIC CONTROL UNIT FOR 318-EOV-319-10 | ELECTRO HYDRAULIC VALVE, SV STATION-10 | 969275367 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353321 | PL318EOV31811 | HYDRAULIC CONTROL UNIT FOR 318-EOV-318-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | 969275363 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353322 | PL318EOV31911 | HYDRAULIC CONTROL UNIT FOR 318-EOV-319-11 | ELECTRO HYDRAULIC VALVE, SV STATION-11 | 969275368 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353323 | PL318EOV31812 | HYDRAULIC CONTROL UNIT FOR 318-EOV-318-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | 969275364 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353324 | PL318EOV31912 | HYDRAULIC CONTROL UNIT FOR 318-EOV-319-12 | ELECTRO HYDRAULIC VALVE, SV STATION-12 | 969275369 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353325 | PL318EOV31808 | HYDRAULIC CONTROL UNIT FOR 318-EOV-318-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | 969275360 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353326 | PL318EOV31908 | HYDRAULIC CONTROL UNIT FOR 318-EOV-319-08 | ELECTRO HYDRAULIC VALVE, SV STATION-08 | 969275365 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353327 | PL318EOV31809 | HYDRAULIC CONTROL UNIT FOR 318-EOV-318-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | 969275361 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353328 | PL318EOV31909 | HYDRAULIC CONTROL UNIT FOR 318-EOV-319-09 | ELECTRO HYDRAULIC VALVE, SV STATION-09 | 969275366 | PACKAGE | PL318VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278851 | PL318CCTV060 | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / Ex-Proof PTZ Color Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278852 | PL318CCTV061 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278853 | PL318CCTV062 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278854 | PL318CCTV063 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278855 | PL318CCTV064 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278856 | PL318CCTV065 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278857 | PL318CCTV066 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278858 | PL318CCTV067 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278859 | PL318CCTV068 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 25mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278860 | PL318CCTV069 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278861 | PL318CCTV070 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 100mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969278862 | PL318CCTV071 | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera | CAMERA FOR CLOSE CIRCUIT TELEVISION / 50mm Fixed Thermal Camera |  | CCTVSEC | PL318TELM | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216031 | M410DCSEWS001 | ENGINEERING WORK STATION (DCS) | ENGINEERING WORK STATION (DCS) |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216032 | M410ESDEWS001 | ENGINEERING WORK STATION (ESD) | ENGINEERING WORK STATION (ESD) |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216033 | M400HWC001 | DCS CONSOLE | DCS CONSOLE |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216034 | M400HWC002 | ESD CONSOLE | ESD CONSOLE |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216035 | M410PDB002 | POWER DISTRIBUTION BOARD SIS - 001 | POWER DISTRIBUTION BOARD SIS - 001 |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216036 | M410DCSPRN001 | DCS PRINTER | DCS PRINTER |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216037 | M410ESDPRT001 | ESD PRINTER | ESD PRINTER |  | BLDGS | M410MISC | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216038 | M410LANCB07 | LAN CABINET SUBSTATION | LAN CABINET SUBSTATION |  | BLDGS | M410TELSS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216039 | M410LANCB011 | LAN CABINET SIS | LAN CABINET SIS |  | BLDGS | M410TELSIS | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969216040 | M410LANCB021 | LAN CABINET PLCR | LAN CABINET PLCR |  | BLDGS | M410TELPLCR | 3 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205432 | M410MP032A | FIRE WATER PUMP- MOTOR | FIRE WATER PUMP- MOTOR |  | MOTOR | M410P032A | 1 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MP032A-MC1 | ACTIVE | CONT | PM | FIC | 26 | WEEKS | 25/11/18 | MC-PM-02-M6
969205054 | M410MOV0109 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175558 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0109-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
969205055 | M410MOV0110 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175559 | MOV | M410T001 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0110-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/09/18 | ME-PM-002-M6
969205056 | M410MOV0111 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175560 | MOV | M410T001 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0111-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/09/18 | ME-PM-002-M6
969205057 | M410MOV0112 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-001 | 969175561 | MOV | M410T001 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0112-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969205058 | M410MOV0201 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175562 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0201-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/09/18 | ME-PM-002-M6
969205059 | M410MOV0202 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175563 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0202-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
969205060 | M410MOV0203 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175564 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0203-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/09/18 | ME-PM-002-M6
969205061 | M410MOV0204 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175565 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0204-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/09/18 | ME-PM-002-M6
969205062 | M410MOV0205 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175566 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0205-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969205063 | M410MOV0206 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175567 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0206-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/09/18 | ME-PM-002-M6
969205064 | M410MOV0207 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175568 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0207-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
969205286 | M410FACP001 | XPS POWER | FIRE ALARM CONTROL PANEL IN THE SIS BUILDING. | 969195600 |  | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205287 | M410FACP001 | IDNET LOOP MODULE | FIRE ALARM CONTROL PANEL IN THE SIS BUILDING. | 969195600 |  | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205065 | M410MOV0208 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175569 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0208-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/09/18 | ME-PM-002-M6
969205066 | M410MOV0209 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175570 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0209-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/10/18 | ME-PM-002-M6
969205067 | M410MOV0210 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175571 | MOV | M410T002 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0210-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969205068 | M410MOV0211 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175572 | MOV | M410T002 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0211-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969205069 | M410MOV0212 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-002 | 969175573 | MOV | M410T002 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0212-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 02/10/18 | ME-PM-002-M6
969205070 | M410MOV0301 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175574 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0301-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/10/18 | ME-PM-002-M6
969205071 | M410MOV0302 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175575 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0302-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 07/10/18 | ME-PM-002-M6
969205072 | M410MOV0303 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175576 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0303-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/10/18 | ME-PM-002-M6
969205073 | M410MOV0304 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175577 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0304-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969205074 | M410MOV0305 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-003 | 969175578 | MOV | M410T003 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV0305-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/10/18 | ME-PM-002-M6
969257162 | M410P009 | SEAL FLUSH SYSTEM FOR ULG/GAS OIL SUMP PUMP | ULG/GAS OIL SUMP PUMP ON 410V003. | 969147453 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P009-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-7-Y1
969257163 | M410P007A | SEAL FLUSH SYSTEM FOR ULG 91/95 INTER-TANK TRANSFER PUMP | ULG 91/95 INTER-TANK TRANSFER PUMP | 969147446 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P007A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-7-Y1
969269257 | M410BAV21243004 | 0.75" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 0.75" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269258 | M410BAV21243059 | 0.75" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 0.75" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269259 | M410BAV21243033 | 0.75" Ball Valve Reduced Bore, ASME B16.34, Class 1500, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/Devlon V, Fire Safe | 0.75" Ball Valve Reduced Bore, ASME B16.34, Class 1500, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/Devlon V, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269260 | M410BAV21243012 | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-160 Nipple Plain End L=100mm, Fire Safe | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-160 Nipple Plain End L=100mm, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269261 | M410BAV21243001 | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe | 0.75" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269262 | M410BAV21243006 | 1" Ball Valve Full Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe | 1" Ball Valve Full Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269263 | M410BAV21243005 | 1" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 1" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275070 | M410BAV21273001 | 1" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Flat Face, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, ASME B16.5, Fire Safe | 1" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Flat Face, Split Body Floating Ball, Lever Operator, ASTM B148 Class C95500, Trim Al-Bronze w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269264 | M410BAV21243062 | 1" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved | 1" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269265 | M410BAV21243002 | 1" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe | 1" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A105, Trim 316SS w/RTFE Seats, w/S-80 Nipple Plain End L=100mm, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269266 | M410BAV21243058 | 1" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A182 Grade F316L, Trim 316LSS w/RTFE Seats, w/S-40S Nipple Plain End L=100mm, Fire Safe | 1" Ball Valve Reduced Bore, ISO 17292, Class 800, Socket Weld End, Split Body Floating Ball, Lever Operator, ASTM A182 Grade F316L, Trim 316LSS w/RTFE Seats, w/S-40S Nipple Plain End L=100mm, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269267 | M410BAV21243019 | 1.5" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 1.5" Ball Valve Long Pattern Full Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269268 | M410BAV21243063 | 1.5" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved | 1.5" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Floating Ball, Lever Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe, UL/FM Approved |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269305 | M410PT752A | 2ND DISCH PRESSURE TRANSMITTER | 2ND DISCH PRESSURE TRANSMITTER |  | PRES_TX | M410K001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT752A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269340 | M410BAV21243015 | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 6" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Floating Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969185918 | M410PSV003 | VALVE,SAFETY RELIEF | Jet A1 Inter-Tank Transfer Filter Coalescers |  | PSV | M410L004C | 1 | PSV | 617101-310600 | IRPMTERMINAL | NOT READY | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195486 | M410FU331 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195487 | M410FU332 | HYDRANT | HYDRANT |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281573 | M410P002A | MECHANICAL SEAL (DE) | AL AIN ULG MAIN LINE PUMP | 969269213 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281574 | M410P002A | MECHANICAL SEAL (NDE) | AL AIN ULG MAIN LINE PUMP | 969269213 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281575 | M410P002B | MECHANICAL SEAL (DE) | AL AIN ULG MAIN LINE PUMP | 969269214 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281576 | M410P002B | MECHANICAL SEAL (NDE) | AL AIN ULG MAIN LINE PUMP | 969269214 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281577 | M410P004A | MECHANICAL SEAL (DE) | AL AIN GAS OIL MAIN LINE PUMP | 969269215 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281578 | M410P004A | MECHANICAL SEAL (NDE) | AL AIN GAS OIL MAIN LINE PUMP | 969269215 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281579 | M410P004B | MECHANICAL SEAL (DE) | AL AIN GAS OIL MAIN LINE PUMP | 969269216 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281580 | M410P004B | MECHANICAL SEAL (NDE) | AL AIN GAS OIL MAIN LINE PUMP | 969269216 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281581 | M410P005A | MECHANICAL SEAL (DE) | ADIA NORTH JET A1 BOOSTER PUMP. | 969269217 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281582 | M410P005A | MECHANICAL SEAL (NDE) | ADIA NORTH JET A1 BOOSTER PUMP. | 969269217 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281583 | M410P005B | MECHANICAL SEAL (DE) | ADIA NORTH JET A1 BOOSTER PUMP. | 969269218 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281584 | M410P005B | MECHANICAL SEAL (NDE) | ADIA NORTH JET A1 BOOSTER PUMP. | 969269218 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281585 | M410P005C | MECHANICAL SEAL (DE) | ADIA NORTH JET A1 BOOSTER PUMP. | 969269219 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281586 | M410P005C | MECHANICAL SEAL (NDE) | ADIA NORTH JET A1 BOOSTER PUMP. | 969269219 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281587 | M410P006A | MECHANICAL SEAL (DE) | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269220 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281588 | M410P006A | MECHANICAL SEAL (NDE) | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269220 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281589 | M410P006B | MECHANICAL SEAL (DE) | ADIA NORTH JET A1 MAIN LINE PUMP | 969269221 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281590 | M410P006B | MECHANICAL SEAL (NDE) | ADIA NORTH JET A1 MAIN LINE PUMP | 969269221 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281591 | M410P006C | MECHANICAL SEAL (DE) | ADIA NORTH JET A1 MAIN LINE PUMP. | 969269222 | MECHSEAL | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281605 | M410TELSVR001 | ACS SYSTEM CABINET | ACS SYSTEM CABINET |  | BLDGS | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281606 | M410PT109 | PRESSURE Transmitter FOR DELUGE VALVE SKID | PRESSURE Transmitter FOR DELUGE VALVE SKID |  | PRES_TX | M410MISC | 3 | PRES_TX | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT109-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281607 | M410PT054 | PRESSURE TRANSMITTERS | PRESSURE TRANSMITTERS |  | PRES_TX | M410MISC | 3 | PRES_TX | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PT054-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969281608 | M410PG007 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281609 | M410PG376 | PRESSURE GAUGE | PRESSURE GAUGE |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281621 | M410PG633 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281622 | M410PG634 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281623 | M410PG635 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281624 | M410PG636 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281625 | M410PG637 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969281626 | M410PG638 | PRESSURE GAUGES | PRESSURE GAUGES |  | INDICATR | M410MISC | 3 | BLDGS | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VHC37132 | UTOYOTA27987 | 8 / 27987 - TOYOTA HILUX PICK-UP (MECH. SUPVR., P & T DEPT) | TOYOTA HILUX PICK-UP 8 / 27987 (MECH. SUPVR., P & T DEPT) |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA27987-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 07/08/18 | MM-PM-029-M1
VHC37124 | UTOYOTA49076 | 11 / 49076 - TOYOTA FORTUNER (FIRE & SAFETY, P & T DEPT.) | TOYOTA FORTUNER 11 / 49076 (FIRE & SAFETY, P & T DEPT.) |  |  | MVEHICLES | 4 | 0 | 648701-610920 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | a | 0 | N | N |  | 0 | Y | UTOYOTA49076-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 13/08/18 | MM-PM-029-M1
969168220 | M400CP005 | CAR PARKING FOR MUSSAFAH TERMINAL. | CAR PARKING FOR MUSSAFAH TERMINAL. |  |  | MBLDG | 4 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969265908 | PL100MOV400AB | MOTOR OPERATED VALVE (100-FT-400 METERING SKID) | MOV (RUWAIS) SHEWIHAT RECIVING STATION. (100-FT-400 METERING SKID) |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400AB-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969265909 | PL100MOV400BA | MOTOR OPERATED VALVE (100-FT-400 METERING SKID) | MOV (RUWAIS) SHEWIHAT RECIVING STATION. (100-FT-400 METERING SKID) |  | MOV | PL100MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL100MOV400BA-MP1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969168242 | M410L014A | PRE-FILTER | PRE-FILTER A 22PCs. |  | VESSEL | M410FILTER | 2 | 0 | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969168243 | M410L014B | FILTER, PRE | PRE-FILTER B, ELEMENTS = 22PCs. |  | VESSEL | M410FILTER | 3 | 0 | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969168244 | M410L014C | FILTER, PRE | PRE-FILTER C |  | VESSEL | M410FILTER | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365134 | M410XHD601B | LINEAR HEAT DETECTOR FOR TANK-012 | LINEAR HEAT DETECTOR FOR TANK-012 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365135 | M410XHD602A | LINEAR HEAT DETECTOR FOR TANK-013 | LINEAR HEAT DETECTOR FOR TANK-013 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365136 | M410XHD602B | LINEAR HEAT DETECTOR FOR TANK-013 | LINEAR HEAT DETECTOR FOR TANK-013 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365137 | M410XHD603A | LINEAR HEAT DETECTOR FOR TANK-014 | LINEAR HEAT DETECTOR FOR TANK-014 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365138 | M410XHD603B | LINEAR HEAT DETECTOR FOR TANK-014 | LINEAR HEAT DETECTOR FOR TANK-014 |  | PB_HS-MC | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365139 | M410XHD604B | LINEAR HEAT DETECTOR FOR TANK-015 | LINEAR HEAT DETECTOR FOR TANK-015 |  | FGBHFD | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365140 | M410XHD605B | LINEAR HEAT DETECTOR FOR TANK-016 | LINEAR HEAT DETECTOR FOR TANK-016 |  | FGBHFD | M410FGSC001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365141 | M410XHD667A | LINEAR HEAT DETECTOR FOR FW PUMP-031A | LINEAR HEAT DETECTOR FOR FW PUMP-031A |  | PB_HS-MC | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969195261 | M410MVP002 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP002-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 06/09/18 | ME-PNL1-PM-M6
969195262 | M410MVP003 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP003-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 02/11/18 | ME-PNL1-PM-M6
969195263 | M410MVP004 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP004-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 08/09/18 | ME-PNL1-PM-M6
969195264 | M410MVP005 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP005-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 09/09/18 | ME-PNL1-PM-M6
969195265 | M410MVP006 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP006-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 10/09/18 | ME-PNL1-PM-M6
969195266 | M410MVP007 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP007-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 11/09/18 | ME-PNL1-PM-M6
969195267 | M410MVP008 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP008-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 12/09/18 | ME-PNL1-PM-M6
969195268 | M410MVP009 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP009-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 13/09/18 | ME-PNL1-PM-M6
969195269 | M410MVP010 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP010-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 14/09/18 | ME-PNL1-PM-M6
969195270 | M410MVP011 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP011-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 15/09/18 | ME-PNL1-PM-M6
969195271 | M410MVP012 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP012-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 16/09/18 | ME-PNL1-PM-M6
969195272 | M410MVP013 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP013-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 17/09/18 | ME-PNL1-PM-M6
969195273 | M410MVP014 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP014-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 18/09/18 | ME-PNL1-PM-M6
969195274 | M410MVP015 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP015-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 19/09/18 | ME-PNL1-PM-M6
969195275 | M410MVP016 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP016-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 20/09/18 | ME-PNL1-PM-M6
969195276 | M410MVP017 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP017-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 21/09/18 | ME-PNL1-PM-M6
969195277 | M410MVP018 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP018-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 22/09/18 | ME-PNL1-PM-M6
969195278 | M410MVP019 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP019-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 23/09/18 | ME-PNL1-PM-M6
969195279 | M410MVP020 | MOV POWER DISTRIBUTION PANEL | MOV POWER DISTRIBUTION PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410MVP020-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 24/09/18 | ME-PNL1-PM-M6
969195280 | M410ELP011 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP011-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 04/12/18 | ME-PNL1-PM-M6
969195281 | M410ELP012 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP012-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/12/18 | ME-PNL1-PM-M6
969195282 | M410ELP013 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP013-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 06/12/18 | ME-PNL1-PM-M6
969195283 | M410ELP021 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP021-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 07/12/18 | ME-PNL1-PM-M6
969195284 | M410ELP022 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP022-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 08/12/18 | ME-PNL1-PM-M6
969195285 | M410ELP031 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP031-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 09/12/18 | ME-PNL1-PM-M6
969195286 | M410ELP032 | EMERGENCY LIGHTING PANEL | EMERGENCY LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | M410ELP032-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 10/12/18 | ME-PNL1-PM-M6
969195287 | M410LP011 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP011-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 25/12/18 | ME-PNL1-PM-M6
969195288 | M410LP012 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP012-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 26/12/18 | ME-PNL1-PM-M6
969195289 | M410LP013 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP013-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 27/12/18 | ME-PNL1-PM-M6
969195290 | M410LP021 | NORMAL LIGHTING PANEL | NORMAL LIGHTING PANEL |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | M410LP021-ME1 | ACTIVE | ELEC | PM | FIC | 6 | MONTHS | 28/12/18 | ME-PNL1-PM-M6
969169063 | M410P008A | MECHANICAL SEAL (NDE) FOR GAS OIL INTER-TANK TRANSFER PUMP | GAS OIL INTER-TANK TRANSFER PUMP | 969147449 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-4-Y1
969169064 | M410P008B | MECHANICAL SEAL(NDE) FOR GAS OIL INTER-TANK TRANSFER PUMP | GAS OIL INTER-TANK TRANSFER PUMP | 969147450 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P008B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 11/11/18 | MM-PM-4-Y1
969169065 | M410P014A | MECHANICAL SEAL(NDE) FOR JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP | 969147451 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 12/01/19 | MM-PM-4-Y1
969205217 | M410MOV1505 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175721 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1505-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 28/10/18 | ME-PM-002-M6
969205218 | M410MOV1506 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175722 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1506-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 29/10/18 | ME-PM-002-M6
969205219 | M410MOV1507 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175723 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1507-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969205220 | M410MOV1508 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175724 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1508-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 30/10/18 | ME-PM-002-M6
969205221 | M410MOV1509 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175725 | MOV | M410T015 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1509-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 01/11/18 | ME-PM-002-M6
969205222 | M410MOV1510 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-015 | 969175726 | MOV | M410T015 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1510-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/11/18 | ME-PM-002-M6
969205223 | M410MOV1601 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175727 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1601-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 05/11/18 | ME-PM-002-M6
969205224 | M410MOV1602 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175728 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1602-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969205225 | M410MOV1603 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175729 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1603-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/11/18 | ME-PM-002-M6
969205226 | M410MOV1604 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175730 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1604-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 08/11/18 | ME-PM-002-M6
969205227 | M410MOV1605 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175731 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1605-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/11/18 | ME-PM-002-M6
969205228 | M410MOV1606 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175732 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1606-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 12/11/18 | ME-PM-002-M6
969205229 | M410MOV1607 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175733 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1607-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969205230 | M410MOV1608 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175734 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1608-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/11/18 | ME-PM-002-M6
969205231 | M410MOV1609 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175735 | MOV | M410T016 | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1609-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 15/11/18 | ME-PM-002-M6
969205232 | M410MOV1610 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) OF 410-T-016 | 969175736 | MOV | M410T016 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV1610-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/11/18 | ME-PM-002-M6
969205233 | M410MOV450A | Motor Operated Valve(Ball)- ACTUATOR | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004A | 969175737 | MOV | M410L004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV450A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 03/12/18 | ME-PM-002-M6
969205234 | M410MOV450B | Motor Operated Valve(Ball)- ACTUATOR | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004B | 969175738 | MOV | M410L004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV450B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969205235 | M410MOV450C | Motor Operated Valve(Ball)- ACTUATOR | OUTLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004C | 969175739 | MOV | M410L004C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV450C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969205236 | M410MOV451A | Motor Operated Valve(Ball)- ACTUATOR | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004A | 969175740 | MOV | M410L004A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV451A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969205237 | M410MOV451B | Motor Operated Valve(Ball)- ACTUATOR | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004B | 969175741 | MOV | M410L004B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 3 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV451B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969205238 | M410MOV451C | Motor Operated Valve(Ball)- ACTUATOR | INLET Motor Operated Valve(Ball) OF FILTER COALESCER 410-L-004C | 969175742 | MOV | M410L004C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV451C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/12/18 | ME-PM-002-M6
969205239 | M410MOV751A | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-007A | 969175743 | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV751A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205240 | M410MOV752A | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-007A | 969175744 | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV752A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205241 | M410MOV753A | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007A | 969175745 | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV753A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205242 | M410MOV754A | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007A | 969175746 | MOV | M410P007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV754A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205243 | M410MOV755B | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-007B | 969175747 | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV755B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205244 | M410MOV756B | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-007B | 969175748 | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV756B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205245 | M410MOV757B | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007B | 969175749 | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV757B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205246 | M410MOV758B | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007B | 969175750 | MOV | M410P007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV758B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205247 | M410MOV759C | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-007C | 969175751 | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV759C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205248 | M410MOV760C | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) OF 410-P-007C | 969175752 | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV760C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205249 | M410MOV761C | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007C | 969175753 | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV761C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205250 | M410MOV762C | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) OF 410-P-007C | 969175754 | MOV | M410P007C | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV762C-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/05/19 | ME-PM-002-M6
969205251 | M410MOV763 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM | 969175755 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV763-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 04/12/18 | ME-PM-002-M6
969205252 | M410MOV764 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM | 969175756 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV764-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 06/12/18 | ME-PM-002-M6
969205253 | M410MOV765 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM | 969175757 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV765-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 09/12/18 | ME-PM-002-M6
969205254 | M410MOV766 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM | 969175758 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV766-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 10/12/18 | ME-PM-002-M6
969205255 | M410MOV767 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) ON G-95 ITT SYSTEM | 969175759 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV767-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969205256 | M410MOV768 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) ON G-91 ITT SYSTEM | 969175760 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV768-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 11/12/18 | ME-PM-002-M6
969205257 | M410MOV769A | Motor Operated Valve(Ball)- ACTUATOR | INLET Motor Operated Valve(Ball) TO FILTER | 969175761 | MOV | M410L007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV769A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 13/12/18 | ME-PM-002-M6
969205258 | M410MOV769B | Motor Operated Valve(Ball)- ACTUATOR | INLET Motor Operated Valve(Ball) TO FILTER | 969175762 | MOV | M410L007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV769B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 16/12/18 | ME-PM-002-M6
969205259 | M410MOV770A | Motor Operated Valve(Ball)- ACTUATOR | OUTLET Motor Operated Valve(Ball) TO FILTER | 969175763 | MOV | M410L007A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV770A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 17/12/18 | ME-PM-002-M6
969205260 | M410MOV770B | Motor Operated Valve(Ball)- ACTUATOR | OUTLET Motor Operated Valve(Ball) TO FILTER | 969175764 | MOV | M410L007B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV770B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969205261 | M410MOV851A | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) | 969175765 | MOV | M410P008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV851A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 18/12/18 | ME-PM-002-M6
969205262 | M410MOV852A | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) | 969175766 | MOV | M410P008A | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV852A-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 20/12/18 | ME-PM-002-M6
969205263 | M410MOV853B | Motor Operated Valve(Ball)- ACTUATOR | SUCTION Motor Operated Valve(Ball) | 969175767 | MOV | M410P008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV853B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 23/12/18 | ME-PM-002-M6
969205264 | M410MOV854B | Motor Operated Valve(Ball)- ACTUATOR | DISCHARGE Motor Operated Valve(Ball) | 969175768 | MOV | M410P008B | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV854B-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 24/12/18 | ME-PM-002-M6
969205265 | M410MOV855 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM | 969175769 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV855-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969205266 | M410MOV856 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM | 969175770 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV856-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 25/12/18 | ME-PM-002-M6
969205267 | M410MOV857 | Motor Operated Valve(Ball)- ACTUATOR | Motor Operated Valve(Ball) GAS OIL ITT SYSTEM | 969175771 | MOV | M410MOV | 2 | MOV | 0 | 0 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MOV857-ME1 | ACTIVE | ELEC | PM | EDS | 12 | MONTHS | 27/12/18 | ME-PM-002-M6
969205270 | M410INS2308001 | IQ636X-2 CPU CARD | INERGEN GAS SYSTEM | 969175977 |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205271 | M410INS2308001 | ACM - 8R-RELAY CARD | INERGEN GAS SYSTEM | 969175977 |  | M410SYS | 1 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205276 | M410GAP001 | CM32/2 CPU CARD VERSION 2 | GAS ALARM PANEL SIS BUILDING | 969195603 |  | M410SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205277 | M410GAP001 | CM32/2 VERSION 2 DISPLAY MODULE | GAS ALARM PANEL SIS BUILDING | 969195603 |  | M410SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205278 | M410GAP001 | GAS CARD | GAS ALARM PANEL SIS BUILDING | 969195603 |  | M410SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205279 | M410GAP001 | GAS TERMINATION CARD | GAS ALARM PANEL SIS BUILDING | 969195603 |  | M410SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205280 | M410GAP001 | POWER SUPPLY | GAS ALARM PANEL SIS BUILDING | 969195603 |  | M410SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205281 | M410GAP001 | IO-32T ( RELAY CARD) | GAS ALARM PANEL SIS BUILDING | 969195603 |  | M410SYS | 1 | BLDGS | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205284 | M410FACP001 | CPU CARD | FIRE ALARM CONTROL PANEL IN THE SIS BUILDING. | 969195600 |  | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205285 | M410FACP001 | SPS POWER SUPPLY | FIRE ALARM CONTROL PANEL IN THE SIS BUILDING. | 969195600 |  | M410MISC | 1 | F&G_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205443 | M410PT031A | PRESSURE TRANSDUCER | PRESSURE TRANSDUCER |  |  | M410FWCP031A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205444 | M410PS33A | Pressure Switch | Pressure Switch |  | PRES_SWT | M410P033A | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969205445 | M410LG203 | Level gauge | Level gauge |  | INDICATR | M410P031A | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969169665 | MFBAY1EGD | FIRE BUILDING BAY#1 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. | FIRE BUILDING BAY#1 EAST GARAGE DOOR AT MUSSAFAH TERMINAL. |  |  | MFBAY1 | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969169066 | M410P014B | MECHANICAL SEAL (NDE) FOR JET A1 INTER-TANK TRANSFER PUMP | JET A1 INTER-TANK TRANSFER PUMP | 969147452 | MECHSEAL | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P014B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-4-Y1
969269436 | M410SDV400A | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L005A | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269437 | M410SDV400B | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L005B | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269438 | M410SDV400C | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L005C | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269439 | M410SDV400D | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L005D | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269440 | M410SDV400E | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L005E | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269441 | M410SDV401A | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L001A | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269442 | M410SDV401B | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L001B | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269443 | M410SDV401C | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L001C | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269444 | M410SDV401D | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L001D | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269445 | M410SDV403 | Valve, Ball, 28 X 24, 300#, A105 | Valve, Ball, 28 X 24, 300#, A105 |  | CNTR_VLV | M410PLR007 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269446 | M410SDV403A | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L011A | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269447 | M410SDV403B | Valve, Ball, 2 x 1.5, 300#, A216 WCB | Valve, Ball, 2 x 1.5, 300#, A216 WCB |  | CNTR_VLV | M410L011B | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269448 | M410SDV415 | Valve, Ball, 28 X 24, 600#, A105 | Valve, Ball, 28 X 24, 600#, A105 |  | CNTR_VLV | M410PT412 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269449 | M410SDV427 | Valve, Ball, 12 X 10, 900#, A216 WCB | Valve, Ball, 12 X 10, 900#, A216 WCB |  | CNTR_VLV | M410PLR005 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269450 | M410SDV435 | Valve, Ball, 12 X 10, 900#, A216 WCB | Valve, Ball, 12 X 10, 900#, A216 WCB |  | CNTR_VLV | M410PLR006 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269451 | M410SDV448 | Valve, Ball, 20 X 16, 300#, A216 WCB | Valve, Ball, 20 X 16, 300#, A216 WCB |  | CNTR_VLV | M410PLR007 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269452 | M410SDV463 | Valve, Ball, 10 X 8, 300#, A216 WCB | Valve, Ball, 10 X 8, 300#, A216 WCB |  | CNTR_VLV | M410PLR007 | 1 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269529 | M410ME105 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE4 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE4 |  | PACKAGE |  | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269530 | M410ME107 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE4 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE4 |  | PACKAGE | M410MISC | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269455 | M410FA091A | BREATHER FOR COMPRESSOR | BREATHER FOR COMPRESSOR |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269456 | M410FA091B | BREATHER FOR COMPRESSOR | BREATHER FOR COMPRESSOR |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269457 | M410VH093A | BYPASS SILENCER | BYPASS SILENCER |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269458 | M410VH093B | BYPASS SILENCER | BYPASS SILENCER |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269206 | M410P023A | DHAFRA JP-8 BOOSTER CENTRIFUGAL PUMP | AL DHAFRA JP-8 BOOSTER PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269207 | M410P023B | DHAFRA JP-8 BOOSTER CENTRIFUGAL PUMP | AL DHAFRA JP-8 BOOSTER PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269208 | M410P023C | DHAFRA JP-8 BOOSTER CENTRIFUGAL PUMP | AL DHAFRA JP-8 BOOSTER PUMP. |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 1 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269209 | M410P040A | JP-8 ANTI FREEZE OFFLOADING CENTRIFUGAL PUMP | ANTI FREEZE CHEMICAL OFFLOADING PUMP-A |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P040A-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269210 | M410P040B | JP-8 ANTI FREEZE OFFLOADING CENTRIFUGAL PUMP | ANTI FREEZE CHEMICAL OFFLOADING PUMP-B |  | PUCE | M410PUMP | 3 | PUCE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M410P040B-MM1 | INACTIVE | MECH | PM | EDS | 6 | MONTHS | 05/07/18 | MM-PM-36-Y1
969269459 | M410ME001 | CHEMICAL INJECTION PACKAGE | BLUE DYE CHEMICAL INJECTION PACKAGE |  | PACKAGE | M410PKG | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269460 | M410ME002 | CHEMICAL INJECTION PACKAGE | ANTI-STATIC CHEMICAL INJECTION PACKAGE |  | PACKAGE | M410PKG | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269461 | M410ME010 | CHEMICAL INJECTION PACKAGE | CORROSION INHIBITOR INJECTION PACKAGE |  | PACKAGE | M410PKG | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269462 | M410ME011 | CHEMICAL INJECTION PACKAGE | ANTI FREEZE CHEMICAL INJECTION PACKAGE |  | PACKAGE | M410PKG | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 10 | 10 | 1 | 5 | 1 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269463 | M410JBEI761 | CHEMICAL INJECTION SYSTEM FOR ANTI-STATIC | CHEMICAL INJECTION SYSTEM FOR ANTI-STATIC |  | CCTV_SYS | M410TELM | 3 | CCTV_SYS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269464 | M410LAN001 | LAN SYSTEM | LAN SYSTEM |  | SWBOARD | M410SCB | 3 | SWBOARD | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269531 | M410ME108 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE4 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE4 |  | PACKAGE | M410MISC | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269532 | M410ME103 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE6 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE 6 |  | PACKAGE |  | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269533 | M410ME104 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE6 | Deluge Valve Skid-Diaphragm-DIAPHRAM,SIZE6 |  | PACKAGE |  | 1 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 100 | 1 | 100 | 10 | 100 | 5 | 7.699 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269542 | M410PDG701 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M400ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269543 | M410PDG702 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M400ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269544 | M410PDG711 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M400ME003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269545 | M410PDG712 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M400ME003 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269546 | M410PDG721 | DIFF. PRESSURE GAUGES | BLUE DYE DIFF. PRESSURE GAUGE |  | INDICATR | M410ME001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269547 | M410PDG722 | DIFF. PRESSURE GAUGES | BLUE DYE DIFF. PRESSURE GAUGE |  | INDICATR | M410ME001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269548 | M410PDG723 | DIFF. PRESSURE GAUGES | BLUE DYE DIFF. PRESSURE GAUGE |  | INDICATR | M410ME001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269549 | M410PDG724 | DIFF. PRESSURE GAUGES | BLUE DYE DIFF. PRESSURE GAUGE |  | INDICATR | M410ME001 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269550 | M410PDG731 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269551 | M410PDG732 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269552 | M410PDG733 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269553 | M410PDG734 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269554 | M410PDG735 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269555 | M410PDG736 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269556 | M410PDG737 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269557 | M410PDG738 | DIFF. PRESSURE GAUGES | ANTI-STATIC DIFF. PRESSURE GAUGES |  | INDICATR | M410ME002 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269558 | M410PDG741 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME010 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269559 | M410PDG742 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME010 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269560 | M410PDG743 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME010 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269561 | M410PDG744 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME010 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269562 | M410PDG751 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME011 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269563 | M410PDG752 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME011 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269564 | M410PDG753 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME011 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269565 | M410PDG754 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME011 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269566 | M410PDG761 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME201 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269567 | M410PDG762 | DIFF. PRESSURE GAUGES | DIFF. PRESSURE GAUGES |  | INDICATR | M410ME201 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269568 | M410FT403A | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS |  | PRES_TX | M410L005A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269569 | M410FT403B | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS |  | PRES_TX | M410L005B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269570 | M410FT403C | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS |  | PRES_TX | M410L005C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269571 | M410FT403D | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS |  | PRES_TX | M410L005D | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269572 | M410FT403E | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS | DIFFERENTIAL PRESSURE FLOW TRANSMITTERS |  | PRES_TX | M410L005E | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269573 | M410PDG400A | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269574 | M410PDG400B | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269575 | M410PDG400C | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269576 | M410PDG401A | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269577 | M410PDG401B | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269578 | M410PDG401C | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269579 | M410PDG203A | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269580 | M410PDG203B | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269581 | M410PDG206A | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269582 | M410PDG206B | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269583 | M410PDG209A | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269584 | M410PDG209B | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269585 | M410PDG211A | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269586 | M410PDG211B | DIFFERENTIAL PRESSURE GAUGE | DIFFERENTIAL PRESSURE GAUGE |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269587 | M410PDT203A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT203 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT203A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269588 | M410PDT203B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT203 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT203B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269589 | M410PDT206A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT206 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT206A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269590 | M410PDT206B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT206 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT206B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269591 | M410PDT209A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT209 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT209A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269592 | M410PDT209B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT209 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT209B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269593 | M410PDT211A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT211 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT211A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269594 | M410PDT211B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT211 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT211B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269595 | M410PDT400A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT400 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT400A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269596 | M410PDT400B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT400 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT400B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269597 | M410PDT400C | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT400 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT400C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269598 | M410PDT401A | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT401 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT401A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269599 | M410PDT401B | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT401 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT401B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269600 | M410PDT401C | Differential Pressure Transmitter | Differential Pressure Transmitter |  | PRES_TX | M410FT401 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT401C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269601 | M410FT402A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269602 | M410FT402B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269603 | M410FT402C | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269604 | M410FT402D | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L001D | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269605 | M410LT452 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410T030 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269606 | M410LT454 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410T031 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269607 | M410PDT265 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P001A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT265-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269608 | M410PDT266 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P001B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT266-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269609 | M410PDT278 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P002A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT278-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269610 | M410PDT279 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P002B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT279-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269611 | M410PDT288 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P003A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT288-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269612 | M410PDT289 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P003B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT289-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269613 | M410PDT301 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P004A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT301-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269614 | M410PDT302 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P004B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT302-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269615 | M410PDT311 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P005A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT311-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269616 | M410PDT312 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P005B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT312-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269617 | M410PDT323 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P006A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT323-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269618 | M410PDT324 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P006B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT324-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269619 | M410PDT334 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P023A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT334-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269620 | M410PDT335 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P023B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT335-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269621 | M410PDT336 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P023C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT336-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269622 | M410PDT345A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L008A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT345A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269623 | M410PDT345B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L008B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT345B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269624 | M410PDT346A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L009A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT346A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269625 | M410PDT346B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L009B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT346B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269626 | M410PDT390 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P024A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT390-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269627 | M410PDT391 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P024B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT391-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269628 | M410PDT392 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P024C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT392-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269629 | M410PDT393 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P006C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT393-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269630 | M410PDT396 | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410P005C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT396-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269631 | M410PDT411A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT411A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269632 | M410PDT411B | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005B | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT411B-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269633 | M410PDT411C | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005C | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT411C-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269634 | M410PDT411D | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005D | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT411D-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269635 | M410PDT411E | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005E | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT411E-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969269636 | M410PDT412A | DIFFERENTIAL PRESSURE TRANSMITTERS | DIFFERENTIAL PRESSURE TRANSMITTERS |  | PRES_TX | M410L005A | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M410PDT412A-MC1 | INACTIVE | CONT | PM | FIC | 6 | MONTHS | 05/07/18 | MC-PM-PT1-M6
969270549 | M410TSV210 | 3/4X1" THERMAL RELIEF VALVE, CLASS 300(IN),150(OUT), ULG | 3/4X1" THERMAL RELIEF VALVE, CLASS 300(IN),150(OUT), ULG |  | CONTHNDV | M410P002A | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270550 | M410TE451 | TEMPERATURE ELEMENT W/WELL (RTD) | TEMPERATURE ELEMENT W/WELL (RTD) |  | TEMP_ELE | M410T030 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270551 | M410TE453 | TEMPERATURE ELEMENT W/WELL (RTD) | TEMPERATURE ELEMENT W/WELL (RTD) |  | TEMP_ELE | M410T031 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270552 | M410TG203A | Temperature gauge | Temperature gauge |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270553 | M410TG203B | Temperature gauge | Temperature gauge |  | INDICATR | M410FT203 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270554 | M410TG206A | Temperature gauge | Temperature gauge |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270555 | M410TG206B | Temperature gauge | Temperature gauge |  | INDICATR | M410FT206 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270556 | M410TG209A | Temperature gauge | Temperature gauge |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270557 | M410TG209B | Temperature gauge | Temperature gauge |  | INDICATR | M410FT209 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270558 | M410TG211A | Temperature gauge | Temperature gauge |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270559 | M410TG211B | Temperature gauge | Temperature gauge |  | INDICATR | M410FT211 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270560 | M410TG400A | Temperature gauge | Temperature gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270561 | M410TG400B | Temperature gauge | Temperature gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270562 | M410TG400C | Temperature gauge | Temperature gauge |  | INDICATR | M410FT400 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270563 | M410TG401A | Temperature gauge | Temperature gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270564 | M410TG401B | Temperature gauge | Temperature gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270565 | M410TG401C | Temperature gauge | Temperature gauge |  | INDICATR | M410FT401 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270566 | M410TG001 | TEMPERATURE GAUGE | TEMPERATURE GAUGE |  | INDICATR | M410MISC | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270567 | M410TG451 | TEMPERATURE GAUGE | TEMPERATURE GAUGE |  | INDICATR | M410T030 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270568 | M410TG452 | TEMPERATURE GAUGE | TEMPERATURE GAUGE |  | INDICATR | M410T031 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270569 | M410TT203A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT203 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270570 | M410TT203B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT203 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270571 | M410TT206A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT206 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270572 | M410TT206B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT206 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270573 | M410TT209A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT209 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270574 | M410TT209B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT209 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270575 | M410TT211A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT211 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270576 | M410TT211B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT211 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270577 | M410TT400A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT400 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270578 | M410TT400B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT400 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270579 | M410TT400C | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT400 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270580 | M410TT401A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT401 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270581 | M410TT401B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT401 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270582 | M410TT401C | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410FT401 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270583 | M410TT400 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410PLR001 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270584 | M410TT402 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410PT412 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270585 | M410TT404 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410PLR005 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270586 | M410TT407 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410PLR006 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270587 | M410TT409 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410PLR003 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270588 | M410TT413 | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410PLR007 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270589 | M410TT751A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270590 | M410TT751B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270591 | M410TT752A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270592 | M410TT752B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270593 | M410TT753A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270594 | M410TT753B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270595 | M410TT754A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270596 | M410TT754B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270597 | M410TT756A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270598 | M410TT756B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270599 | M410TT757A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270600 | M410TT757B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270601 | M410TT758A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270602 | M410TT758B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270603 | M410TT759A | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001A | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270604 | M410TT759B | TEMPERATURE TRANSMITTER | TEMPERATURE TRANSMITTER |  | TEMP_TX | M410K001B | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270605 | M410TT451 | TEMPERATURE TRANSMITTER & Remote indicator | TEMPERATURE TRANSMITTER & Remote indicator |  | TEMP_TX | M410T030 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270606 | M410TT453 | TEMPERATURE TRANSMITTER & Remote indicator | TEMPERATURE TRANSMITTER & Remote indicator |  | TEMP_TX | M410T031 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270607 | M410TT001 | TEMPERATURE TRANSMITTER WITH T-WELL | TEMPERATURE TRANSMITTER WITH T-WELL |  | TEMP_TX | M410TEMP | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270695 | M410TCP053B | TRANSFOMER / RECTIFIER FOR TANK AND PIPING UNIT 410 | TRANSFOMER / RECTIFIER FOR TANK AND PIPING UNIT 410 |  | TRANSFMR | M410SCB | 3 | TRANSFMR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | M410TCP053B-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-009-M6
969269213 | M410P002A | AL AIN ULG MAIN LINE PUMP A IN PUMP HOUSE #4 | AL AIN ULG MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269214 | M410P002B | AL AIN ULG MAIN LINE CENTRIFUGAL PUMP. | AL AIN ULG MAIN LINE PUMP |  | PUMPS | M410PUMP | 3 | PUMPS | 617101-310600 | MTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 10 | 10 | 5.3979 | Low | Low | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270696 | M410VE901AA | VIBRATION SENSOR | VIBRATION SENSOR |  | VIBRMON | M410VIBR | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270697 | M410VE901BA | VIBRATION SENSOR | VIBRATION SENSOR |  | VIBRMON | M410VIBR | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270698 | M410VE902AA | VIBRATION SENSOR | VIBRATION SENSOR |  | VIBRMON | M410VIBR | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270699 | M410VE902AB | VIBRATION SENSOR | VIBRATION SENSOR |  | VIBRMON | M410VIBR | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270700 | M410VE902BA | VIBRATION SENSOR | VIBRATION SENSOR |  | VIBRMON | M410VIBR | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270701 | M410VE902BB | VIBRATION SENSOR | VIBRATION SENSOR |  | VIBRMON | M410VIBR | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270702 | M410DCSOPCA0106 | WP001 LED LARGE SCREEN MONITOR INTERFACE STATION | WP001 LED LARGE SCREEN MONITOR INTERFACE STATION |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270703 | M410DCSOPCA0108 | WP002 OPERATOR WORK STATION | WP002 OPERATOR WORK STATION |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270704 | M410DCSOPCA0111 | WP003 OPERATOR WORK STATION | WP003 OPERATOR WORK STATION |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270705 | M410LCSMG001 | Ex Local Control Station(TYPE-A) | Ex Local Control Station(TYPE-A) |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270706 | M410LCSMG002 | Ex Local Control Station(TYPE-B) | Ex Local Control Station(TYPE-B) |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270707 | M410LCSMG003 | Ex Local Control Station(TYPE-C) | Ex Local Control Station(TYPE-C) |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270708 | M410LCSMG004 | Ex Local Control Station(TYPE-E) | Ex Local Control Station(TYPE-E) |  | BLDGS | M410SYS | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270709 | M410FT203 | CORIOLIS CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, ULG | ULG CUSTODY TRANSFER METERING SKID (FLOWMETER). |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270710 | M410FT206 | CORIOLIS CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, GAS OIL | GAS OIL CUSTODY TRANSFER METERING SKID (FLOWMETER). |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270711 | M410FT209 | CORIOLIS CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, JET A1 | JET A1 CUSTODY TRANSFER METERING SKID (FLOWMETER). |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270712 | M410FT211 | CORIOLIS CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, JP-8 | JP-8 CUSTODY TRANSFER METERING SKID (FLOWMETER). |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270713 | M410FT400 | CORIOLIS CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, JET A1 | JET A1 CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, JET A1 |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270714 | M410FT401 | CORIOLIS CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, GAS OIL | CUSTODY TRANSFER METERING SYSTEM (FLOWMETER), MUSSAFAH TERMINAL, GAS OIL |  | FL_MTR | M410FLOW | 3 | FL_MTR | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270715 | M410FV402A | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, 410-L-001A OUTLET | 969269226 | CNTR_VLV | M410L001A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270716 | M410FV402B | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, 410-L-001B OUTLET | 969269227 | CNTR_VLV | M410L001B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270717 | M410FV402C | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, 410-L-001C OUTLET | 969269228 | CNTR_VLV | M410L001C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270718 | M410FV402D | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, 410-L-001D OUTLET | 969269229 | CNTR_VLV | M410L001D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270719 | M410FV403A | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 969269230 | CNTR_VLV | M410L005A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270720 | M410FV403B | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 969269231 | CNTR_VLV | M410L005B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270721 | M410FV403C | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 969269232 | CNTR_VLV | M410L005C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270722 | M410FV403D | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 969269233 | CNTR_VLV | M410L005D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270723 | M410FV403E | ACTUATOR FOR 8" GLOBE VALVE, CLASS 300 | 8" GLOBE VALVE, CLASS 300, JET A1 TO TANKS 410-T-011 TO 016 | 969269234 | CNTR_VLV | M410L005E | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270724 | M410LV401A | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-005A DRAIN | 969269235 | CNTR_VLV | M410L005A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270725 | M410LV401B | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-005B DRAIN | 969269236 | CNTR_VLV | M410L005B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270726 | M410LV401C | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-005C DRAIN | 969269237 | CNTR_VLV | M410L005C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270727 | M410LV401D | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-005D DRAIN | 969269238 | CNTR_VLV | M410L005D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270728 | M410LV401E | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-005E DRAIN | 969269239 | CNTR_VLV | M410L005E | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270729 | M410LV403A | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-001A DRAIN | 969269240 | CNTR_VLV | M410L001A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270730 | M410LV403B | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-001B DRAIN | 969269241 | CNTR_VLV | M410L001B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270731 | M410LV403C | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-001C DRAIN | 969269242 | CNTR_VLV | M410L001C | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270732 | M410LV403D | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-001D DRAIN | 969269243 | CNTR_VLV | M410L001D | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270733 | M410LV407A | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-011A DRAIN | 969269244 | CNTR_VLV | M410L011A | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969270734 | M410LV407B | ACTUATOR FOR 1" GLOBE VALVE, CLASS 300 | 1" GLOBE VALVE, CLASS 300, 410-L-011B DRAIN | 969269245 | CNTR_VLV | M410L011B | 3 | CNTR_VLV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9557288 | M410GSKT | GASKETS - DUMMY EQUIPMENT | GASKET (1ST & 2ND) |  |  | M410MISC | 3 | 0 | 617101-310600 | IRPMTERMINAL | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269279 | M410FFE2101311 | 125 lbs BC DCP Fire Extinguisher (Trolley) | 125 lbs BC DCP Fire Extinguisher (Trolley) |  | FG_DET | M410MISC | 3 | FG_DET | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | o | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269280 | M410BAV21243008 | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269281 | M410BAV21243060 | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 14" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 600, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269282 | M410BAV21243009 | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269283 | M410BAV21243011 | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 16" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 300, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269284 | M410BAV21243010 | 18" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe | 18" Ball Valve Long Pattern Reduced Bore, ISO 17292, Class 150, Raised Face, Split Body Trunnion Mounted Ball, Gear Operator, ASTM A216 Grade WCB, Trim 316SS w/RTFE Seats, ASME B16.5, Fire Safe |  | CONTHNDV | M410VALVE | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269285 | M410VH091A | 1st DISCHARGE FOR COMPRESSOR(VENTURIELBOW) | 1st DISCHARGE FOR COMPRESSOR(VENTURIELBOW) |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269286 | M410VH091B | 1st DISCHARGE, 2nd SILENCER (VENTURIELBOW) | 1st DISCHARGE, 2nd SILENCER (VENTURIELBOW) |  | VESSEL | M410K001B | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269287 | M410D091A | 1st DRAIN SEPARATOR FOR COMPRESSOR | 1st DRAIN SEPARATOR FOR COMPRESSOR |  | VESSEL | M410K001A | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275986 | M400VS920 | VALVE,CHECK | VALVE @ DRAIN LINE OF JET A1 SORAGE TANK 120 | 939613 | VALCH | M400T120 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969275987 | M400VS921 | VALVE,CHECK | VALVE @ DRAIN LINE OF COALIZER FILTER | 932609 | VALCH | M400L004A | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512585 | A-MSFH-ICCSP3 | HP Prodesk 600 G1 | YOURAJ |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512665 | SDELECTCONT | Fujitsu Siemense | SEMCO Comany |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512586 | A-MSFH-ICCPLANN | HP Prodesk 600 G1 | ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512587 | A-MSFH-ICCSADN | HP Prodesk 600 G1 | ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512588 | SD-MSFH-ICCCOM | HP Prodesk 600 G1 | ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512589 | A-MSFH-ICCOPER | HP Prodesk 600 G1 | ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512590 | A-MSFH-ICCLOGIS | HP Prpdesk 600 G1 | ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512591 | SUPERVISOR_PC | HP - ML310 | Supervisior - ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512592 | SD-MSFH-ICCSP1 | HP Prodesk 600 G1 | ICC Room Secretary |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512735 | A-MSFH-PLCRSUP | HP Prodesk 600 G1 | SILVANO LUPPI |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512672 | SD-PT-HHA10943 | HP Prodesk 600 G1 | Haleema Al Yamahee |  |  | P&T_NEW_ADMIN | [12 empty] | Non Critical |  | Non Critical | N | Non Critical | N |  |  | d
969512675 | A-PI-R43 | Lenovo - M2999-A34 | IBM Lenovo M92P |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512693 | A-MSFH-CONF2 | HP Prodesk 600 G1 | Conference Room - 2nd Floor |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512717 | A-MSFH-MEL | Lenovo - M2999-A34 | YOURAJ NANDAYAL DHANAPAL |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512719 | A-MSFH-MCRSUP | Fujitsu Siemans | Mohammed shukri |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512733 | SCDHEXA | Dell - Optiplex 760 | Mohammed Sanad |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512734 | A-MSFH-ABUBAKER | Dell Optiplex 9020 | Abu Baker Alamoodi |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512702 | A-MSFH-MINHALI | Dell Optiplex 9020 | ABDULLAH METAWAH |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512703 | SD-MSFH-TRAIN | HP Prodesk 600 G1 | BADR ABDUL RAHMAN ALI AL HADHARMI |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512705 | A-MSFH-CPTECH | Dell Optiplex 7010 | BABY CHAKKUNGAL MATHAI |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512706 | A-MSFH-NDT | Dell Opteplex 7010 | ASHFAN |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512732 | SCDSHOKATH | Lenovo - M7491 | Sunu Sivaraj Sivarajan |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512652 | A-MSFH-ICCFADMN | HP Prodesk 600 G1 | ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512653 | A-MSFH-ICCSEC | HP Prodesk 600 G1 | New Admin Building - ICC Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512654 | A-PI-ROMAITHI | Fujitsu Siemense | Planning |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512655 | A-MSFH-DCS | Dell Optiplex 9020 | Dhasleem Mohammed Mahroof |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0