969512656 | A-MSFH-NASSER7 | Dell Optiplex 9020 | NASSER MOHAMED AL MANSOORI |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512725 | SDHAZZA | Lenovo - M5498-PS4 | HAZZA IBRAHIM AL BALOOSHI |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512731 | A-MSFH-SPOOL | Fujitsu Siemans | Security Room |  |  | P&T_SECURITY | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512666 | A-MSFH-CONF1 | HP Prodesk 600 G1 | Meeting Room - first floor |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512669 | A-MSFH-RELENG | Dell Optiplex 9020 | Debal Choudhary |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512671 | A-MSFH-KAREN2 | Lenovo - M2999-A34 | Karen Ramos |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512722 | A-MSFH-HSESEC | Lenovo - M7491 | P&T HSE CONFERENCE-MUSAFFAH |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512704 | A-MSFH-PIPLINE | Dell Optiplex 9020 | GANDA HIMAWAN BIN MOHAMAD JURI |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512713 | A-MSFH-INSP1 | Dell - optiplex9020 | MOHAMMED SUHEL MOHAMMED RAFIQUE |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512727 | SDBHAKEET | HP Prodesk 600 G1 | SCURITY SUPERVISOR |  |  | P&T_SECURITY | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512737 | SCDPERMIT | HP Prodesk 600 G1 | WORK PERMIT |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512739 | SDPLCRTV | Dell Optiplex 490 | SHIFT CONTROL ROOM |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512740 | A-MSFH-PERMIT | Dell Optiplex 760 | WORK PERMIT OFFICE |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512723 | SDFIRESUP | Dell Optiplex 9020 | Fire Supervisor |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512736 | A-MSFH-PLCR | Lenovo - M7491 | Control Room - Mussafah Terminal |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513312 | A-MSFH-ABDULLA | Dell OptiPlex 9020. | Security Gate - Conf Room |  |  | P&T_SECURITY | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969417160 | MV49878 | FORD F-150 PICKUP 10-49878 TERMINAL FIRE DEPT FIRST RESPONCE VEHCL.(RED) | FORD F-150 PICKUP 10-49878 TERMINAL FIRE DEPT FIRST RESPONCE VEHCL.(RED) |  | VEHICLE | MVEHICLES | 1 | VEHICLE | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | a | 0 | Y | Y | 0 | 0 | 0 | MV49878-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 23/08/18 | MM-PM-029-M1
969417161 | MV90727 | NISSAN PATROL 11-90727 PIPELINE MAINTENANCE.(WHITE) | NISSAN PATROL 11-90727 PIPELINE MAINTENANCE.(WHITE) |  | VEHICLE | MVEHICLES | 4 | VEHICLE | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | a | 0 | N | N |  | 0 | Y | MV90727-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 08/08/18 | MM-PM-029-M1
969417162 | MV91475 | NISSAN PATROL 11-91475 PIPELINE OPERATION.(WHITE) | NISSAN PATROL 11-91475 PIPELINE OPERATION.(WHITE) |  | VEHICLE | MVEHICLES | 3 | VEHICLE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | a | 0 | N | N | 0 | 0 | 0 | MV91475-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 07/08/18 | MM-PM-029-M1
969417163 | MV93767 | NISSAN PATROL 11-93767 PIPELINE OPERATION.(WHITE) | NISSAN PATROL 11-93767 PIPELINE OPERATION.(WHITE) |  | VEHICLE | MVEHICLES | 3 | VEHICLE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | a | 0 | N | N | 0 | 0 | 0 | MV93767-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 06/08/18 | MM-PM-029-M1
969365343 | M400ACCUACR | CONTROL ROOM ISOLATOR PANEL "A" INSTALLED OUTSIDE. | CONTROL ROOM ISOLATOR PANEL "A" INSTALLED OUTSIDE. |  | MCC_SWBD | M400SUBSTN | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ACCUACR-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 31/01/19 | ME-PNL1-PM-M6
969365344 | M400ACCUBCR | CONTROL ROOM ISOLATOR PANEL "B" INSTALLED OUTSIDE. | CONTROL ROOM ISOLATOR PANEL "B" INSTALLED OUTSIDE AT MCR. |  | MCC_SWBD | M400SUBSTN | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | M400ACCUBCR-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 21/10/18 | ME-PNL1-PM-M6
969365345 | M400ACCUAS/S | SUB STATION ISOLATOR PANEL "A" OUTSIDE S/S-400. | SUB STATION ISOLATOR PANEL A INSTALLED OUTSIDE AT MUSAFFAH S/S-400 |  | MCC_SWBD | M400SUBSTN | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365346 | M400ACCUBS/S | SUB STATION ISOLATOR PANEL "B" OUTSIDE S/S-400. | SUB STATION ISOLATOR PANEL "B" INSTALLED OUTSIDE AT MUSAFFAH S/S-400. |  | MCC_SWBD | M400SUBSTN | 3 | MOTOR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969362106 | M410MP034 | MOTOR OF PUMP,CENTRIFUGAL | MOTOR FOR FIRE WATER MAKE UP PUMP 410-P-034. |  | EMACFF | M410P034 | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | M410MP034-ME1 | INACTIVE | ELEC | PM | FIC | 6 | MONTHS | 05/07/18 | ME-PM-LT1-6M
969532799 | M400RVRV16D | RIM VENT RELIEF VALVE FOR TANK T-116 | RIM VENT RELIEF VALVE FOR TANK T-116 |  | PSV | M400T116 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532810 | M400RVRV20A | RIM VENT RELIEF VALVE FOR TANK T-120 | RIM VENT RELIEF VALVE FOR TANK T-120 |  | PSV | M400T120 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532775 | M400RVRV11E | RIM VENT RELIEF VALVE FOR TANK T-111 | RIM VENT RELIEF VALVE FOR TANK T-111 |  | PSV | M400T111 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532776 | M400RVRV12A | RIM VENT RELIEF VALVE FOR TANK T-112 | RIM VENT RELIEF VALVE FOR TANK T-112 |  | PSV | M400T112 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532777 | M400RVRV12B | RIM VENT RELIEF VALVE FOR TANK T-112 | RIM VENT RELIEF VALVE FOR TANK T-112 |  | PSV | M400T112 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532778 | M400RVRV12C | RIM VENT RELIEF VALVE FOR TANK T-112 | RIM VENT RELIEF VALVE FOR TANK T-112 |  | PSV | M400T112 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532779 | M400RVRV12D | RIM VENT RELIEF VALVE FOR TANK T-112 | RIM VENT RELIEF VALVE FOR TANK T-112 |  | PSV | M400T112 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532780 | M400RVRV12E | RIM VENT RELIEF VALVE FOR TANK T-112 | RIM VENT RELIEF VALVE FOR TANK T-112 |  | PSV | M400T112 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532781 | M400RVRV13A | RIM VENT RELIEF VALVE FOR TANK T-113 | RIM VENT RELIEF VALVE FOR TANK T-113 |  | PSV | M400T113 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532782 | M400RVRV13B | RIM VENT RELIEF VALVE FOR TANK T-113 | RIM VENT RELIEF VALVE FOR TANK T-113 |  | PSV | M400T113 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532784 | M400RVRV13D | RIM VENT RELIEF VALVE FOR TANK T-113 | RIM VENT RELIEF VALVE FOR TANK T-113 |  | PSV | M400T113 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532785 | M400RVRV13E | RIM VENT RELIEF VALVE FOR TANK T-113 | RIM VENT RELIEF VALVE FOR TANK T-113 |  | PSV | M400T113 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532800 | M400RVRV16E | RIM VENT RELIEF VALVE FOR TANK T-116 | RIM VENT RELIEF VALVE FOR TANK T-116 |  | PSV | M400T116 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532801 | M400RVRV17A | RIM VENT RELIEF VALVE FOR TANK T-117 | RIM VENT RELIEF VALVE FOR TANK T-117 |  | PSV | M400T117 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532802 | M400RVRV17B | RIM VENT RELIEF VALVE FOR TANK T-117 | RIM VENT RELIEF VALVE FOR TANK T-117 |  | PSV | M400T117 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532803 | M400RVRV17C | RIM VENT RELIEF VALVE FOR TANK T-117 | RIM VENT RELIEF VALVE FOR TANK T-117 |  | PSV | M400T117 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532804 | M400RVRV18A | RIM VENT RELIEF VALVE FOR TANK T-118 | RIM VENT RELIEF VALVE FOR TANK T-118 |  | PSV | M400T118 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532805 | M400RVRV18B | RIM VENT RELIEF VALVE FOR TANK T-118 | RIM VENT RELIEF VALVE FOR TANK T-118 |  | PSV | M400T118 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532806 | M400RVRV18C | RIM VENT RELIEF VALVE FOR TANK T-118 | RIM VENT RELIEF VALVE FOR TANK T-118 |  | PSV | M400T118 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532807 | M400RVRV19A | RIM VENT RELIEF VALVE FOR TANK T-119 | RIM VENT RELIEF VALVE FOR TANK T-119 |  | PSV | M400T119 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532808 | M400RVRV19B | RIM VENT RELIEF VALVE FOR TANK T-119 | RIM VENT RELIEF VALVE FOR TANK T-119 |  | PSV | M400T119 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532809 | M400RVRV19C | RIM VENT RELIEF VALVE FOR TANK T-119 | RIM VENT RELIEF VALVE FOR TANK T-119 |  | PSV | M400T119 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532811 | M400RVRV20B | RIM VENT RELIEF VALVE FOR TANK T-120 | RIM VENT RELIEF VALVE FOR TANK T-120 |  | PSV | M400T120 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532812 | M400RVRV20C | RIM VENT RELIEF VALVE FOR TANK T-120 | RIM VENT RELIEF VALVE FOR TANK T-120 |  | PSV | M400T120 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532813 | M410RVRV001 | RIM VENT RELIEF VALVE FOR TANK T-001 | RIM VENT RELIEF VALVE FOR TANK T-001 |  | PSV | M410T001 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532814 | M410RVRV002 | RIM VENT RELIEF VALVE FOR TANK T-002 | RIM VENT RELIEF VALVE FOR TANK T-002 |  | PSV | M410T002 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532815 | M410RVRV003 | RIM VENT RELIEF VALVE FOR TANK T-003 | RIM VENT RELIEF VALVE FOR TANK T-003 |  | PSV | M410T003 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532816 | M410RVRV004 | RIM VENT RELIEF VALVE FOR TANK T-004 | RIM VENT RELIEF VALVE FOR TANK T-004 |  | PSV | M410T004 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532817 | M410RVRV005 | RIM VENT RELIEF VALVE FOR TANK T-005 | RIM VENT RELIEF VALVE FOR TANK T-005 |  | PSV | M410T005 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532818 | M410RVRV006 | RIM VENT RELIEF VALVE FOR TANK T-006 | RIM VENT RELIEF VALVE FOR TANK T-006 |  | PSV | M410T006 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532819 | M410RVRV007 | RIM VENT RELIEF VALVE FOR TANK T-007 | RIM VENT RELIEF VALVE FOR TANK T-007 |  | PSV | M410T007 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532820 | M410RVRV008 | RIM VENT RELIEF VALVE FOR TANK T-008 | RIM VENT RELIEF VALVE FOR TANK T-008 |  | PSV | M410T008 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532821 | M410RVRV009 | RIM VENT RELIEF VALVE FOR TANK T-009 | RIM VENT RELIEF VALVE FOR TANK T-009 |  | PSV | M410T009 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532822 | M410RVRV010 | RIM VENT RELIEF VALVE FOR TANK T-010 | RIM VENT RELIEF VALVE FOR TANK T-010 |  | PSV | M410T010 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351156 | PL100EOV403 | HPU for ELECTRO HYDRAULIC VALVE | ELECTRO HYDRAULIC VALVE, GAS OIL TO BASKET FILTERS & METERING | 969265858 | PACKAGE | PL100VALVE | 3 | CONTHNDV | 615101-310600 | SHWEIHAT TERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353285 | M410JBE752B | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001B | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001B |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969353286 | M410JBE753B | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001B | JUNCTION BOX FOR AIR COMPRESSOR PACKAGE 410-K-001B |  | BLDGS | M410MISC | 3 | BLDGS | 0 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969532798 | M400RVRV16C | RIM VENT RELIEF VALVE FOR TANK T-116 | RIM VENT RELIEF VALVE FOR TANK T-116 |  | PSV | M400T116 | 1 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363362 | M410XHD675A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363363 | M410XHD675B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363364 | M410XHD676A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363365 | M410XHD676B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363366 | M410XHD677A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363367 | M410XHD677B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P005C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363368 | M410XHD678A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363369 | M410XHD678B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363370 | M410XHD679A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363371 | M410XHD679B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P001B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363372 | M410XHD680A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363373 | M410XHD680B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363374 | M410XHD681A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363375 | M410XHD681B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P003B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363376 | M410XHD682A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363377 | M410XHD682B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363378 | M410XHD683A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363379 | M410XHD683B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363380 | M410XHD684A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363381 | M410XHD684B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363382 | M410XHD685A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363383 | M410XHD685B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363384 | M410XHD686A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363385 | M410XHD686B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P006C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363386 | M410XHD687A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363387 | M410XHD687B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363388 | M410XHD688A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363389 | M410XHD688B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P002B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363390 | M410XHD689A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363391 | M410XHD689B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363392 | M410XHD690A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363393 | M410XHD690B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P004B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363394 | M410XHD691A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363395 | M410XHD691B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024A |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363396 | M410XHD692A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363397 | M410XHD692B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024B |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363398 | M410XHD693A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363399 | M410XHD693B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P024C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363400 | M410XHD694A | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363401 | M410XHD694B | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023C | LINEAR HEAT DETECTOR AT MAIN PUMP HOUSE AND SCRAPPER AREA-M410P023C |  | FG_DET | M410FGSC001 | 1 | TEMP_ELE | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363402 | M410XAC621 | MANUAL CALL POINT AT ZONE-32-NORTH SIDE OF SCRAPPER AREA ON ROAD | MANUAL CALL POINT AT ZONE-32-NORTH SIDE OF SCRAPPER AREA ON ROAD |  | FG_DET | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363403 | M410XAC622 | MANUAL CALL POINT AT ZONE-32-NORTH SIDE OF SCRAPPER AREA NEAR FILTER AREA | MANUAL CALL POINT AT ZONE-32-NORTH SIDE OF SCRAPPER AREA NEAR FILTER AREA |  | FG_DET | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363404 | M410XAC623 | MANUAL CALL POINT AT ZONE-32-NORTH SIDE OF SCRAPPER AREA NEAR PIG AREA | MANUAL CALL POINT AT ZONE-32-NORTH SIDE OF SCRAPPER AREA NEAR PIG AREA |  | FG_DET | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363405 | M410XAC630 | MANUAL CALL POINT AT ZONE-32-SOUTH SIDE OF SCRAPPER AREA ON ROAD | MANUAL CALL POINT AT ZONE-32-SOUTH SIDE OF SCRAPPER AREA ON ROAD |  | FG_DET | M410FGSC001 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363406 | M410FD627 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-005C SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-005C SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363407 | M410FD628 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-005C NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-005C NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363408 | M410FD629 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-005A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-005A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363409 | M410FD630 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001B NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001B NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363410 | M410FD631 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001A SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001A SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363411 | M410FD632 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-003B NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-003B NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363412 | M410FD633 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001B SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-001B SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363413 | M410FD634 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023C NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-023C NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363414 | M410FD635 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-003B SOUTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-003B SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363415 | M410FD636 | FLAME DETECTOR (IR TYPE) FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006A NORTH SIDE | FLAME DETECTOR FOR MAIN PUMP HOUSE & SCRAPPER AREA NEAR 410-P-006A NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363492 | M410XGC614 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-023B | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-023B |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363493 | M410XGC615 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-006A | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-006A |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363494 | M410XGC616 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-006B | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-006B |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363495 | M410XGC617 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-006C | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-006C |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363496 | M410XGC618 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-002A | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-002A |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363497 | M410XGC619 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-002B | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-002B |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363498 | M410XGC622 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-024A | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-024A |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363499 | M410XGC623 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-024B | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-024B |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363500 | M410XGC624 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-040A | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-040A |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363501 | M410XGC625 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-023C | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-023C |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363502 | M410XGC626 | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-024C | FLAMMABLE GAS DETECTORS-BOOSTER PUMP AREA-ZONE 32 NEAR 410-P-024C |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363503 | M410XGC627 | FLAMMABLE GAS DETECTORS-CHEMICAL INJECTION PACKAGE AREA ZONE 33, NEAR 410-ME001 | FLAMMABLE GAS DETECTORS-CHEMICAL INJECTION PACKAGE AREA ZONE 33, NEAR 410-ME001 |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363504 | M410XGC628 | FLAMMABLE GAS DETECTORS-CHEMICAL INJECTION PACKAGE AREA ZONE 33, NEAR 410-ME003 | FLAMMABLE GAS DETECTORS-CHEMICAL INJECTION PACKAGE AREA ZONE 33, NEAR 410-ME003 |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363505 | M410XGC691A | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001B NORTH SIDE LEFT | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001B NORTH SIDE LEFT |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363506 | M410XGC691B | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001B NORTH SIDE CENTRE | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001B NORTH SIDE CENTRE |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363507 | M410XGC691C | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001B NORTH SIDE RIGHT | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001B NORTH SIDE RIGHT |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363508 | M410XGC692A | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001A SOUTH SIDE LEFT | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001A SOUTH SIDE LEFT |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363509 | M410XGC692B | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001A SOUTH SIDE CENTRE | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001A SOUTH SIDE CENTRE |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969363510 | M410XGC692C | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001A SOUTH SIDE RIGHT | FLAMMABLE GAS DETECTORS-NEW SUMP VESSEL AREA(ZONE-28) NEAR 410-K-001A SOUTH SIDE RIGHT |  | FG_DET | M410GAP001 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269534 | M410DV101 | DELUGE VALVES-3inch | DELUGE VALVES-3inch |  | CONTHNDV | M410FIRE | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969486037 | M400TCP011I | CATHODIC PROTECTION, C.P.RECTIFIER FOR TANK T-201, 240 VOLT, 50 HZ, 1, 50 VOLT, 25 AMPERES, AIR, BS 148, 190 LITERS | IN-SIDE C.P.RECTIFIER/TRANSFORMER UNIT FOR TANK T-201 |  | CATHPRO | M400T201 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95152635 | M410K091A | ROTOR ASSEMBLY FOR 1ST STAGE OF COMPRESSOR | 1ST STAGE OF COMPRESSOR FOR 410-K-001A AIR COMPRESSOR UNIT | 969269289 |  | M410K001A | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95152636 | M410K091B | ROTOR ASSEMBLY FOR 1ST STAGE OF COMPRESSOR | 1ST STAGE OF COMPRESSOR FOR 410-K-001B AIR COMPRESSOR UNIT | 969269290 |  | M410K001B | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95152637 | M410K092A | ROTOR ASSEMBLY FOR 2ND STAGE OF COMPRESSOR | 2ND STAGE OF COMPRESSOR FOR 410-K-001A AIR COMPRESSOR UNIT | 969269311 |  | M410K001A | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95152638 | M410K092B | ROTOR ASSEMBLY FOR 2ND STAGE OF COMPRESSOR | 2ND STAGE OF COMPRESSOR FOR 410-K-001B AIR COMPRESSOR UNIT | 969269312 |  | M410K001B | 3 | COMPRS | 0 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269535 | M410DV102 | DELUGE VALVES-3inch | DELUGE VALVES-3inch |  | CONTHNDV | M410FIRE | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269536 | M410DV106 | DELUGE VALVES-3inch | DELUGE VALVES-3inch |  | CONTHNDV | M410ME106 | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969485973 | MBFFFS | SHELTER FOR THE BIG FLOW FIRE FIGHTING SYSTEM. | SHELTER FOR THE BIG FLOW FIRE FIGHTING SYSTEM. |  | PACKAGE | M410 | 2 | BFS | 617101-310600 | IRPMTERMINAL | NOT READY | 10 | 1 | 5 | 1 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269537 | M410DV105 | DELUGE VALVES-4inch | DELUGE VALVES-4inch |  | CONTHNDV | M410FIRE | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269538 | M410DV107 | DELUGE VALVES-4inch | DELUGE VALVES-4inch |  | CONTHNDV | M410ME107 | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269539 | M410DV108 | DELUGE VALVES-4inch | DELUGE VALVES-4inch |  | CONTHNDV | M410ME108 | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269540 | M410DV103 | DELUGE VALVES-6inch | DELUGE VALVES-6inch |  | CONTHNDV | M410FIRE | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969269541 | M410DV104 | DELUGE VALVES-6inch | DELUGE VALVES-6inch |  | CONTHNDV | M410FIRE | 1 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95154160 | PL100EOV403 | HYDRAULIC POWER | ELECTRO HYDRAULIC VALVE, GAS OIL TO BASKET FILTERS & METERING | 969265858 |  | PL100VALVE | 3 | CONTHNDV | 615101-310600 | SHWEIHAT TERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374391 | M410LS060 | OUTDOOR LOUD SPEAKER NEAR TANK-116 SW SIDE ON POLE-ZONE-B1 | Loud Speaker with J/B-Outdoor-HVAC ROOM-SIS BUILDING EAST SIDE | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969399941 | M410L015A | JP-8 FILTER COALESCERS (MUSSAFAH) | JP-8 FILTER COALESCERS (MUSSAFAH) |  | VESSEL | M410FILTER | 2 | 0 | 0 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969399942 | M410L015B | JP-8 FILTER COALESCERS (MUSSAFAH) | JP-8 FILTER COALESCERS (MUSSAFAH) |  | VESSEL | M410FILTER | 2 | 0 | 0 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513058 | PANASONIC PROJECTOR | Panasonic Projector - New Conf Security Gate | Panasonic Projector - security Gate |  |  | P&T_SECURITY | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513060 | ISE | Cisco Secure Network Server - New Admin server Room | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513066 | ITTEAM-LAPTOP | Dell Laptop - IT Team | Dell Laptop -New Admin - IT Team |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513067 | HAMAD-PC | Dell Laptop - Mr. Hamad Al Yafeei | Dell Laptop - Mr. Hamad Al Yafeei |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513068 | THAUPEEK-LAPTOP | Dell Laptop - Mr. Mohammed Thaupeek | Dell Laptop - Mr. Mohammed Thaupeek |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513150 | PIMS SERVER | HP DL380 BIMS Server - New Admin in Server Room | PIMS Server - Server Room. |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365253 | M410XAC675 | MANUAL CALL POINT INSIDE HVAC ROOM-NEW S/S | MANUAL CALL POINT INSIDE HVAC ROOM-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365254 | M410XAC676 | MANUAL CALL POINT INSIDE DOCUMENT ROOM-NEW S/S | MANUAL CALL POINT INSIDE DOCUMENT ROOM-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365255 | M410XAC677 | MANUAL CALL POINT INSIDE BATTERY ROOM GATE-NEW S/S | MANUAL CALL POINT INSIDE BATTERY ROOM GATE-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365256 | M410XAC678 | MANUAL CALL POINT AT OUTSIDE BATTERY ROOM GATE-NEW S/S | MANUAL CALL POINT AT OUTSIDE BATTERY ROOM GATE-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365257 | M410XAC679 | MANUAL CALL POINT AT INSIDE CORRIDOR'S GATE-NEW S/S | MANUAL CALL POINT AT INSIDE CORRIDOR'S GATE-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365258 | M410XAC680 | MANUAL CALL POINT INSIDE S/S GATE-NEW S/S | MANUAL CALL POINT INSIDE S/S GATE-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365259 | M410XAC681 | MANUAL CALL POINT AT OUTSIDE SWGR ROOM ENTERANCE CORRIDOR DOOR-NEW S/S | MANUAL CALL POINT AT OUTSIDE SWGR ROOM ENTERANCE CORRIDOR DOOR-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365260 | M410XAC682 | MANUAL CALL POINT AT INSIDE SWGR ROOM ENTERANCE MAIN DOOR-NEW S/S | MANUAL CALL POINT AT INSIDE SWGR ROOM ENTERANCE MAIN DOOR-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365261 | M410XAC683 | MANUAL CALL POINT OUTSIDE SWGR ROOM GATE EAST-NEW S/S | MANUAL CALL POINT OUTSIDE SWGR ROOM GATE EAST-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365262 | M410XAC684 | MANUAL CALL POINT INSIDE SWGR ROOM NEAR EAST GATE-NEW S/S | MANUAL CALL POINT INSIDE SWGR ROOM NEAR EAST GATE-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365263 | M410XAC685 | MANUAL CALL POINT OUTSIDE SWGR ROOM AIR LOCK DOOR NORTH SIDE-NEW S/S | MANUAL CALL POINT OUTSIDE SWGR ROOM AIR LOCK DOOR NORTH SIDE-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365264 | M410XAC686 | MANUAL CALL POINT INSIDE SWGR ROOM WEST SIDE WALL-NEW S/S | MANUAL CALL POINT INSIDE SWGR ROOM WEST SIDE WALL-NEW S/S |  | PB_HS-MC | M410FACP002 | 1 | PA_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365265 | M410FD726 | FLAME DETECTOR FOR FW PUMP-031A-NORTH SIDE | FLAME DETECTOR FOR FW PUMP-031A-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365266 | M410FD727 | FLAME DETECTOR FOR FW PUMP-031A-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031A-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365267 | M410FD728 | FLAME DETECTOR FOR FW PUMP-031B-NORTH SIDE | FLAME DETECTOR FOR FW PUMP-031B-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365268 | M410FD729 | FLAME DETECTOR FOR FW PUMP-031B-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031B-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365269 | M410FD730 | FLAME DETECTOR FOR FW PUMP-031C-NORTH SIDE | FLAME DETECTOR FOR FW PUMP-031C-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365270 | M410FD731 | FLAME DETECTOR FOR FW PUMP-031C-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031C-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365271 | M410FD732 | FLAME DETECTOR FOR FW PUMP-031D-NORTH SIDE | FLAME DETECTOR FOR FW PUMP-031D-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365272 | M410FD733 | FLAME DETECTOR FOR FW PUMP-031D-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031D-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365273 | M410FD734 | FLAME DETECTOR FOR FW PUMP-031E-NORTH SIDE | FLAME DETECTOR FOR FW PUMP-031E-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365274 | M410FD735 | FLAME DETECTOR FOR FW PUMP-031E-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031E-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365275 | M410FD736 | FLAME DETECTOR FOR FW PUMP-031F-NORTH SIDE | FLAME DETECTOR FOR FW PUMP-031F-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365276 | M410FD737 | FLAME DETECTOR FOR FW PUMP-031F-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031F-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365277 | M410FD738 | FLAME DETECTOR FOR FW PUMP-031G-NORTH SIDE | FLAME DETECTOR FOR FW PUMP-031G-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365278 | M410FD739 | FLAME DETECTOR FOR FW PUMP-031G-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031G-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365279 | M410FD740 | FLAME DETECTOR FOR FW PUMP-031G-SOUTH SIDE | FLAME DETECTOR FOR FW PUMP-031G-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365280 | M410FD696 | FLAME DETECTOR FOR PUMP-014A-NORTH SIDE | FLAME DETECTOR FOR PUMP-014A-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365281 | M410FD697 | FLAME DETECTOR FOR PUMP-014B-SOUTH SIDE | FLAME DETECTOR FOR PUMP-014B-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365282 | M410FD698 | FLAME DETECTOR FOR PUMP-014B-NORTH SIDE | FLAME DETECTOR FOR PUMP-014B-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365283 | M410FD699 | FLAME DETECTOR FOR PUMP-014B-SOUTH SIDE | FLAME DETECTOR FOR PUMP-014B-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365284 | M410FD700 | FLAME DETECTOR FOR PUMP-008A-NORTH SIDE | FLAME DETECTOR FOR PUMP-008A-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365285 | M410FD701 | FLAME DETECTOR FOR PUMP-008A-SOUTH SIDE | FLAME DETECTOR FOR PUMP-008A-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365286 | M410FD702 | FLAME DETECTOR FOR PUMP-008B-NORTH SIDE | FLAME DETECTOR FOR PUMP-008B-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365287 | M410FD703 | FLAME DETECTOR FOR PUMP-008B-SOUTH SIDE | FLAME DETECTOR FOR PUMP-008B-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365288 | M410FD704 | FLAME DETECTOR FOR PUMP-007A-NORTH SIDE | FLAME DETECTOR FOR PUMP-007A-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365289 | M410FD705 | FLAME DETECTOR FOR PUMP-007A-SOUTH SIDE | FLAME DETECTOR FOR PUMP-007A-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365290 | M410FD706 | FLAME DETECTOR FOR PUMP-007B-NORTH SIDE | FLAME DETECTOR FOR PUMP-007B-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365291 | M410FD707 | FLAME DETECTOR FOR PUMP-007B-SOUTH SIDE | FLAME DETECTOR FOR PUMP-007B-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365292 | M410FD708 | FLAME DETECTOR FOR PUMP-007C-NORTH SIDE | FLAME DETECTOR FOR PUMP-007C-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365293 | M410FD709 | FLAME DETECTOR FOR PUMP-007C-SOUTH SIDE | FLAME DETECTOR FOR PUMP-007C-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365294 | M410FD710 | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365295 | M410FD711 | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-SOUTH SIDE | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365296 | M410FD712 | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365297 | M410FD713 | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-SOUTH SIDE | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365298 | M410FD714 | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365299 | M410FD715 | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-SOUTH SIDE | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365300 | M410FD716 | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE | FLAME DETECTOR FOR GAS OIL FILTER NEAR ITTP AREA-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365301 | M410FD720 | FLAME DETECTOR FOR NEW SUMP VESSEL-ZONE-28-SOUTH SIDE | FLAME DETECTOR FOR NEW SUMP VESSEL-ZONE-28-SOUTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969365302 | M410FD721 | FLAME DETECTOR FOR NEW SUMP VESSEL-ZONE-28-NORTH SIDE | FLAME DETECTOR FOR NEW SUMP VESSEL-ZONE-28-NORTH SIDE |  | FGBFFD | M410FGSC001 | 1 | FGBFFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512741 | LASERJET-2420N | LASERJET-2420N - Control Room | CONTROLE ROOM |  |  |  | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512743 | LASERJET-400 | HP LASERJET-400 B&W - Control Room | Control Room - Incharge Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512744 | LASERJET-400 | HP LASERJET-400 B&W - Control Room | Control Room - Incharge Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512774 | SDVM01 | Dell Server - New Admin- SDAV ,SDDC01,SDDHCP | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512775 | SDVM02 | Dell Server - New Admin- SDDC02,SDLMSRV | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512776 | SDBACKUP | Dell Server - New Admin Building - BACKUP | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512742 | LASERJET-2420N | HP LASERJET-2420N B&W Control Room | CONTROLE ROOM |  |  |  | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512752 | LASERJET-400_B&W | HP LASERJET-400 - New Admin Room 212 | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512754 | COLO LASERJET-CP5225 | HP COLO LASERJET-CP5225 - New Adim Room 110 | New Admin Building - Room 110 |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512755 | COLOR LASERJET-M476 | HP COLOR LASERJET-M476 - New admin Room 207 | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512756 | LASERJET-400_B&W | HP LASERJET-400 - New Admin Room 210 | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512757 | COLOR LASERJET-M476 | HP COLOR LASERJET-M476 - New admin Room 211 | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512758 | LASERJET-600 | LASERJET-600- New Admin Room 205 | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512763 | HP COLOR LJ -CP5225 | HP HP COLOR LJ -CP5225 - New Admin Room 118 | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512765 | HP COLOR LJ -CP5225 | HP COLOR LJ -CP5225 - New Admin First Floor | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512766 | COLOR LASERJET-M476 | HP COLOR LASERJET-M476 - VP Office | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512772 | AHMED OBEID OFF | Scanner Fujitsu - Mr. Ahmed Obeid | New Admin Buiding |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969361520 | M400P025A | MULTI STAGE RECIPROCATING PUMP. | SLOP INJECTION PUMPS |  | PURE | M400PUMP | 4 | PUMPS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P025A-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 03/11/18 | MM-PM-08-Y1
969361521 | M400P025B | MULTI STAGE RECIPROCATING PUMP. | SLOP INJECTION PUMPS |  | PURE | M400PUMP | 4 | PUMPS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 5 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | M400P025B-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 01/12/18 | MM-PM-08-Y1
969351362 | PL312EOV002 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-002 | ELECTRO HYDRAULIC VALVE, ULG FROM TARRIFTAPOFF AT SV STATION-4 | 969275343 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351363 | PL312EOV003 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-003 | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"GAS OIL PIPELINE | 969275344 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351364 | PL312EOV004 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-004 | ELECTRO HYDRAULIC VALVE, GAS OIL FROM TARRIFTAPOFF AT SV STATION-4 | 969275345 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351365 | PL312EOV31201 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-01 | ELECTRO HYDRAULIC VALVE, SV STATION-1 | 969275346 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351366 | PL312EOV31202 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-312-02 | ELECTRO HYDRAULIC VALVE, SV STATION-2 | 969275347 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969351361 | PL312EOV001 | HPU FOR ELECTRO HYDRAULIC VALVE 312-EOV-001- | ELECTRO HYDRAULIC VALVE, TO SV STATION-13 10"ULG PIPELINE | 969275342 | PACKAGE | PL312VALVE | 2 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374392 | M410LS061 | OUTDOOR LOUD SPEAKER NEAR TANK-111 EAST SIDE ON POLE-ZONE-B1 | Loud Speaker with J/B-Outdoor-MAIN CONTROL BUILDING ON ROOF SOUTH SIDE SIDE ON WALL | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374393 | M410LS062 | OUTDOOR LOUD SPEAKER NEAR TANK-115 EAST SIDE ON POLE-ZONE-B1 | Loud Speaker with J/B-Outdoor-AT BATTERY ROOM ECR | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374394 | M410LS063 | OUTDOOR LOUD SPEAKER NEAR TANK-113 WEST SIDE ON POLE-ZONE-B1 | Loud Speaker with J/B-Outdoor-AT UPS ROOM ECR | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374395 | M410LS064 | OUTDOOR LOUD SPEAKER NEAR TANK-120 WEST SIDE ON POLE-ZONE-B1 | Loud Speaker with J/B-Outdoor-SIS BUILDING ON ROOF-EAST SIDE WALL | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374396 | M410LS178 | OUTDOOR LOUD SPEAKER NEAR TANK-103 SOUTH SIDE ON POLE-ZONE-B5 | Loud Speaker with J/B-Outdoor-NEAR TANK-103 SOUTH SIDE ON POLE | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374397 | M410LS179 | OUTDOOR LOUD SPEAKER NEAR TANK-111 EAST SIDE ON POLE-ZONE-B1 | Loud Speaker with J/B-Outdoor-NEAR TANK-111 EAST SIDE ON POLE | 969195785 | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374398 | M410HSSD001 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HIGH SENSITIVE SMOKE DETECTOR SYSTEM AT SWGR ROOM IRP II S/S |  | FGBFFD | M410FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374399 | M410HSSD002 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HIGH SENSITIVE SMOKE DETECTOR SYSTEM AT BATTERY ROOM IRP II S/S |  | FGBFFD | M410FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374400 | M410HSD301 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT NEW ADMIN BUILDING |  | FGBFFD | M400FAGP006 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374401 | M410HSD001 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT SWGR ROOM IRP II S/S | 969195601 | FGBFFD | M410FACP002 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374402 | M410HSD002 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT BATTERY & MCM ROOMS IRPII S/S | 969195601 | FGBFFD | M410FACP002 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374403 | M410HSD010 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT SWGR ROOM EXT.PANL IRP II S/S | 969195601 | FGBFFD | M410FACP002 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374404 | M410HSD004 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT BATTERY ROOM SIS | 969195600 | FGBFFD | M410FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374405 | M410HSD005 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT RACK ROOM SIS | 969195600 | FGBFFD | M410FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374406 | M410HSD006 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT UPS ROOM PLCR EXTENTION BLDG. |  | FGBFFD | M400FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374407 | M410HSD007 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT BATTERY ROOM PLCR EXTENTION. |  | FGBFFD | M400FACP001 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374408 | M410HSD003 | PROTECTION, VESDA, 18-30VDC, IN-DOOR, YES | HI SENSITIVE SMOKE DETECTION SYSTEM AT THE UPS ROOM IN THE SIS BUILDING. | 969195601 | FGBFFD | M410FACP002 | 1 | FG_DET | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374409 | M410LSZA1 | LOUD SPEAKER AT ZONE A-MCR INDOOR (M410LS036,M410LS037,M410LS038,M410LS054 ,M410LS111,M410LS113,M410LS114,M410LS115,M410LS133,M410LS134) | LOUD SPEAKER AT ZONE A-MCR INDOOR = 10 LS |  | PA_SYS | M410LSZA | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374410 | M410LSZA2 | LOUD SPEAKER AT ZONE A -MCR OUTDOOR & ECR (M410LS062,M410LS063,M410LS034 ,M410LS035 ,M410LS131,M410LS132,M410LS135,M410LS061) | LOUD SPEAKER AT ZONE A -MCR OUTDOOR & ECR = 8 LS. |  | PA_SYS | M410LSZA | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374412 | M410LSZB1 | LOUD SPEAKER AT ZONE B-TANK FARM AREA (M410LS055,M410LS160,M410LS161 ,M410LS162,M410LS163 ,M410LS164 ,M410LS165 ,M410LS176,M410LS177,M410LS179) | LOUD SPEAKER AT ZONE B-TANK FARM AREA = 10 LS. |  | PA_SYS | M410LSZB | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374413 | M410LSZB2 | LOUD SPEAKER AT ZONE B-IRP-II TANKS 001-007 (M410LS001,M410LS002,M410LS003 ,M410LS004,M410LS005,M410LS006,M410LS057) | LOUD SPEAKER AT ZONE B-IRP-II TANKS 001-007 = 7 LS. |  | PA_SYS | M410LSZB | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374414 | M410LSZB3 | LOUD SPEAKER AT ZONE B-IRP-II TANKS 008-011 (M410LS007,M410LS008 ,M410LS009 ,M410LS010,M410LS017,M410LS056) | LOUD SPEAKER AT ZONE B-IRP-II TANKS 008-011 = 6 LS. |  | PA_SYS | M410LSZB | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374415 | M410LSZB4 | LOUD SPEAKER AT ZONE B-IRP-II TANKS 012-016 (M410LS013,M410LS014 ,M410LS015 ,M410LS016,M410LS018,M410LS019,M410LS166) | LOUD SPEAKER AT ZONE B-IRP-II TANKS 012-016 = 7 LS. |  | PA_SYS | M410LSZB | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374416 | M410LSZB5 | LOUD SPEAKER AT ZONE B-ADNOC TANK FARM AREA (M410LS167,M410LS168,M410LS169 ,M410LS170,M410LS171,M410LS172,M410LS173,M410LS174,M410LS175,M410LS178) | LOUD SPEAKER AT ZONE B-ADNOC TANK FARM AREA = 10 LS. |  | PA_SYS | M410LSZB | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374417 | M410LSZC1 | LOUD SPEAKER AT ZONE C-ADMIN BLDG OUTDOOR (M410LS146,M410LS147,M410LS153 ,M410LS154,M410LS044,M410LS046,M410LS047) | LOUD SPEAKER AT ZONE C-ADMIN BLDG OUTDOOR = 7 LS. |  | PA_SYS | M410LSZC | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374418 | M410LSZC2 | LOUD SPEAKER AT ZONE C-ADMIN BLDG INDOOR (M410LS148,M410LS149,M410LS150 ,M410LS151,M410LS152,M410LS155,M410LS156,M410LS157,M410LS158,M410LS159) | LOUD SPEAKER AT ZONE C-ADMIN BLDG INDOOR = 10 LS. |  | PA_SYS | M410LSZC | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969374419 | M410LSZC3 | LOUD SPEAKER AT ZONE C-FIRE STATION (M410LS049,M410LS050,M410LS051 ,M410LS052 ,M410LS053,M410LS126,M410LS127,M410LS128,M410LS129,M410LS130) | LOUD SPEAKER AT ZONE C-FIRE STATION = 10 LS. |  | PA_SYS | M410LSZC | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969487354 | M400T216 | STORAGE TANK COAGULANT OFF WWTP. | COAGULANT STORAGE TANK WWTP. |  | TANK | M400WWTPLEVEL | 1 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512790 | SDFSRV | Dell Server - New Admin Building - FILE SERVER | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512794 | Q-RADAR | IBM Server - Q-RADAR | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512795 | ISE | Cisco - SECURE NETWORK SERVER | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512797 | NEW ADMIN(OFFICE009) | Fujitsu Scanner - Office 009 | New Admin Buliding |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512825 | SD-CORE-SW02 | Cisco Switch - WS-C6509-E | Control Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512828 | TAKREER_SW_MAIN_2 | Cisco Voice switch - WS-C3560G-24PS-S | Control Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512829 | TAKREER_SW_MAIN_3 | Cisco Voice Switch - WS-C3560G-24PS-S | Control Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512830 | TAKREER_CME | Cisco Voice Switch - CISCO3845 | Control Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512833 | MUSSAFAH_FIRE_VOICE1 | Cisco Voice Switch - WS-C3560G-24PS-S | Fire Station Building |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512834 | MUSSAFAH_ADMIN_VOICE | Cisco Voice Switch - WS-C3560G-24PS-S | Old Admin Building |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512835 | MUSSSAFAH_WARE_VOICE | Cisco Voice Switch - WS-C3560G-24PS-S | Warehouse Building |  |  | P&T_WAREHOUSE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512836 | MUSSAFA_GUARD_VOICE | Cisco Voice Switch - WS-C3560G-24PS-S | Security Building |  |  | P&T_SECURITY | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512837 | SIS_SW_1 | Cisco Voice Switch - WS-C3560G-24PS | Satellite Instrument Shelter |  |  | P&T_SIS | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512791 | BACKUP | Dell Tape Library - Server Room | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512800 | EPSON PRO - AUDIT | Epson Projector - Auditorium | New Admin Building - Auditorium |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512824 | TAKREER-MUS-MPLS | Cisco Switch - C3900-SPE100/K9 | Control Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512838 | SUBSTATIONSW1 | Cisco Voice Switch - WS-C3560G-24PS |  |  |  | P&T_410_SS | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512840 | NEWADMIN_VOICE_SW1 | Cisco Voice Switch - WS-C3650-48PD | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512841 | NEWADMIN_VOICE_SW2 | Cisco Voice Switch - WS-C3650-48PD | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512842 | NEWADMIN_VOICE_SW3 | Cisco Voice Switch - WS-C3650-48PD | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512843 | WS-C3560G-24PS-S | Unused Swith in IT store | IT Store - Unused Switches |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512845 | WS-C3560G-24PS-S | Unsed Switch in IT Store. | IT Store - Unused Switches |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512848 | WS-C3560G-24PS-S | Unsed Switch in IT Store. | IT Store - Unused Switches |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512851 | WS-C3650-48PD | Unused Switch in IT Store. | IT Store - Unused Switch. |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512853 | WS-C2960S-48P1 | Unused Switch in New Admin | New Admin - Unused Switch |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512854 | WS-3560X-48P | Unused Switch in New Admin | New Admin Building - Unused Switch |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512792 | KVM SWITCH | Dell- KVM Switch - Rack 21 Rear Side | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512793 | TFT MONITOR | Dell - TFT Monitor - Rack 21 Front side | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512798 | NEW ADMIN(OFFICE102) | Fujitsu Scanner - New Admin - with Mr. Arum Gopal | New Admin Building |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512801 | EPSON PRO-1ST FLOOR | Epson Projector - 1st Floor. | New Admin Building - First Floor - Conf Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512803 | EPSON PRO-2ND FLOOR | Epson Projector - 2nd Floor - Conf Room | New Admin Building - 2nd Floor |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512804 | SHARP PRO-HSE BLD | Sharp Projector - Fire Station Bld - Conf Room | Fire Station Building - 1st Floor |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512809 | SD-DNADM-SW01 | Cisco Switch - WS-C3650-48PD | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512810 | SD-DNADM-SW02 | Cisco Switch - WS-C3650-48PD | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512811 | SD-DNADM-SW03 | Cisco Switch - WS-C3650-48PD | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512812 | SD-DNADM-SVRSW01 | Cisco Switch - WS-C3750X-24P | New Admin Building - Server Room |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512817 | SD-DWARH-SW01 | Cisco Switch - WS-C3650-24PD | Warehouse Building |  |  | P&T_WAREHOUSE | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512818 | SD-DOADM-SW01 | Cisco Switch - WS-C3650-48PD | Old Building Building. |  |  | P&T_OLD_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512820 | SD-DFIRE-SW01 | Cisco - WS-C3650-48PD | Fire Station Building. |  |  | P&T_FIRE_STN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512821 | SD-DSUB400-SW01 | Cisco - WS-C3650-48PD | IRP-I Substation |  |  | P&T_400_SS | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512822 | SD-DPLCR-SW01 | Cisco - WS-C3650-48PD | Control Room |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512844 | WS-C3560G-24PS-S | Unused Switch in IT Store. | IT Store - Unused Switches |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512849 | WS-C3560G-24PS-S | Unused Switch in IT Store. | IT Store - Unused Switches |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512884 | CISCO 3900 | Unused Switch in Control Room | Control Room - Unused switch |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512886 | CISCO 3900 | Unused Switch in Control Room | Control Room - Unused switch |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512887 | CISCO ASA 5520 | Unused Switch in Control Room | Unused Switch in Control Room. |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512846 | WS-C3560G-24PS-S | Unserd Switch in IT store | IT Store - Unused Switches |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512850 | WS-C2924M | Unused Swith in IT Store. | IT Strore - Unused Switch |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512888 | CISCO ASA 5521 | Unused Switch in Control Room. | Control Room - Unused Switch |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512847 | WS-C3560G-24PS-S | Unused Switch In IT Store | IT Store - Unused Switches |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512852 | WS-C2960S-48P | Unused Switch in IT Store. | IT Store - Unused Switch. |  |  | P&T_ITSTORE | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969513059 | BENQ PROJECTOR | Benq projector - ICC Room New Admin | Benq projector - ICC Room New Admin |  |  | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969512855 | WS-3560X-48P1 | Unused Switch in Control Room. | Control Room - Unsed Switch |  |  | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969372115 | M400DMP651 | MOTOR,ELECTRIC | DENSITY METER PUMP MOTOR FOR RUWAIS MUSSAFAH MP/L RECEIVNG-DENSITY SKID 900LB |  | ANALYSER | M400DT651 | 2 | ANALYSER | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | M400DMP651-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 21/01/19 | ME-PM-LT1-6M
969372172 | MADMINFWP | MOTOR OF FOUNTAIN WATER PUMP AT OLD ADMIN BUILDING. | FOUNTAIN WATER PUMP AT OLD ADMIN BUILDING- P&TD. |  | PUCE | MADMIN | 4 | PUCEWI | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | 0 | MADMINFWP-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 24/11/18 | ME-PM-LT1-6M
969372181 | MOADMINWPA | POTABLE WATER PUMP A, AT OLD ADMIN BUILDING | POTABLE WATER PUMP A, AT OLD ADMIN BUILDING ROOF. |  | PUCEWI | MADMIN | 3 | PUCEWI | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | MOADMINWPA-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/10/18 | ME-PM-LT1-6M
969372182 | MOADMINWPB | POTABLE WATER PUMP B, AT OLD ADMIN BUILDING | POTABLE WATER PUMP B, AT OLD ADMIN BUILDING ROOF. |  | PUCE | MADMIN | 3 | PUCEWI | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | MOADMINWPB-ME1 | ACTIVE | ELEC | PM | EDS | 6 | MONTHS | 25/10/18 | ME-PM-LT1-6M
| A213TSV149 |  | TO BE DELETED |  | 0 | 0 | 0 | 0 | 0 | 0 | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A213TSV150 |  | TO BE DELETED |  | 0 | 0 | 0 | 0 | 0 | 0 | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13 |  | IRP, 13 AL AIN RECEIVING TERMINAL |  | TANK | SALAINPIPE | 3 | TANK | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13FILTER |  | All Filters, Strainers, AA13 |  | CLN_FLTR | AA13 | 3 | CLN_FLTR | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13FLOW |  | Control, Flow, AA13 |  | CLN_FLTR | AA13 | 3 | CLN_FLTR | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 5 | 1 | 1 | 10 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13LEVEL |  | Control Level, AA13 |  | 0 | AA13 | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13MISC |  | Miscellaneous (All Others), AA13 |  | 0 | AA13 | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13MOTOR |  | Elec, Motors, Generators, Heaters, AA13 |  | 0 | AA13 | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13SYS |  | Control, DCS, PLC, Others, AA13 |  | 0 | AA13 | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA13VALVE |  | All Valves, AA13 |  | 0 | AA13 | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA213TSV149 |  | AL AIN RECEIVING STATION GAS OIL, THERMAL RLF VALVE |  | PSV | AA13VALVE | 3 | PSV | 617101-310600 | IRPALAIN | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AA213TSV150 |  | AL AIN RECEIVING STATION GAS OIL, THERMAL RLF VALVE |  | PSV | AA13VALVE | 3 | PSV | 617101-310600 | IRPALAIN | OPERATING | 10 | 50 | 10 | 50 | 1 | 1 | 5.3979 | Low | Low | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ADMIN |  | Admin- Ibrahim omer Redwan |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ADMIN1 |  | ICC Room |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A-MSFH-ABU |  | Abu Bakr Alammodi |  | 0 | 0 | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A-R32-HALEEMA |  | HALEEMAH HASSAN SAEED AL YAMMAHI |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800 |  | AIRPORT TRANSFER PIPE LINE, ADIA, SOUTH |  | PIPING | MTERMINAL | 3 | PIPING | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800BATT |  | Electrical, Battery Banks, AT800 |  | BATTERY | AT800 | 3 | BATTERY | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800FLOW |  | Control, Flow, AT800 |  | 0 | AT800 | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800MISC |  | Miscellaneous (All Others), AT800 |  | 0 | AT800 | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800MOTOR |  | Elec, Motors, Generators, Heaters, AT800 |  | 0 | AT800 | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800PRESS |  | Control, Pressure, AT800 |  | 0 | AT800 | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800SYS |  | Control, DCS, PLC, Others, AT800 |  | DCS_PNL | AT800 | 3 | DCS_PNL | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800TEMP |  | Control, Temperature, AT800 |  | TEMP_ELE | AT800 | 3 | TEMP_ELE | 617101-310600 | IRPADIA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AT800VALVE |  | All Valves, AT800 |  | 0 | AT800 | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BIMS SERVER |  | PIMS Server - Server Room |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CCTV COMPUTER |  | CCTV PC - Security Gate |  | 0 | P&T_SECURITY | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CCTVPC_NEW ADMIN |  | CCTV Computer - New Admin |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CCTVPC_PLCR |  | CCTV Computer - Control Room |  | 0 | P&T_PLCR | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLOR LASERJET -CP52 |  | New Admin Building |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLOR LASERJET-CP522 |  | New Admin Building |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E&SD MANAGER |  | New Admin building |  | 0 | 0 | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E&SD MANAGER (NEW AD |  | New Admin Building |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E&SD MANAGER(NEW ADM |  | New Admin Building |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EPSON PROJECTOR - AU |  | New Admin Building - Auditorium |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HQITD_ITSTORE |  | Permanent IT Storage Room |  | 0 | SDITASSETS | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HQITD_ITSTORE_WROFF |  | Write-off Store |  | 0 | SDITASSETS | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10CIVIL |  | COMMON CIVIL AUXILLARIES OF PRODUCT TANKS AREA |  | 0 | M10COMMON | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10COMMON |  | COMMON LOCNS/EQPTS FOR PRODUCT STORAGE TANKS AREA |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10FH01 |  | FIRE HYDRANT ON WEST SIDE OF 10T101 MUSSAFAH TERMINAL. |  | VALVE_MALF | MFIRE | 1 | VALVE_MALF | 617101-310510 | MTERMINAL | OPERATING | 100 | 1 | 1 | 10 | 1 | 1 | 3 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10FH02 |  | FIRE HYDRANT ON WEST SIDE OF 10T102 MUSSAFAH TERMINAL. |  | VALVE_MALF | MFIRE | 1 | VALVE_MALF | 617101-310510 | MTERMINAL | OPERATING | 100 | 1 | 1 | 10 | 1 | 1 | 3 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10FH03 |  | FIRE HYDRANT ON WEST SIDE OF 10T103 CULVERT #12 MUSSAFAH TERMINAL. |  | VALVE_MALF | MFIRE | 1 | VALVE_MALF | 617101-310510 | MTERMINAL | OPERATING | 100 | 1 | 1 | 10 | 1 | 1 | 3 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10FH04 |  | FIRE HYDRANT BETWEEN T104 & T104 WEST SIDE MUSSAFAH TERMINAL. |  | VALVE_MALF | MFIRE | 1 | VALVE_MALF | 617101-310510 | MTERMINAL | OPERATING | 100 | 1 | 1 | 10 | 1 | 1 | 3 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10FH32 |  | FIRE HYDRANT AT CULVERT #11 WEST SIDE OF 10T103 MUSSAFAH TERMINAL. |  | VALVE_MALF | MFIRE | 1 | VALVE_MALF | 617101-310510 | MTERMINAL | OPERATING | 100 | 1 | 1 | 10 | 1 | 1 | 3 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10INLETMAN |  | INLET MANIFOLD FOR MULTIPRODUCT |  | PIPES | M10TANKS | 3 | PIPES | 617101-310600 | MTERMINAL | OPERATING | 1 | 1 | 1 | 1 | 1 | 5 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10INLETMET |  | INLET METERING FOR MULTI PRODUCT |  | FL_MTR | M10TANKS | 3 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10LAHH063 |  | LEVEL ALARM HIGH HIGH OF TANK 106 ON DCS. |  | OPENLOOP | M10T106 | 2 | OPENLOOP | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10MISC |  | COMMON MISC. ITEMS FOR PRODUCT STORAGE TANKS |  | 0 | M10COMMON | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10PI221F |  | FIRE FIGHTING PRESSURE INDICATOR FOR TANK T-105 |  | INDICATR | M10T105 | 3 | INDICATR | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL01 |  | T110 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA. |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL02 |  | T108 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA. |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL03 |  | T107 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA. |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL04 |  | T106 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA. |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL05 |  | T104 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA. |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL06 |  | T103 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL07 |  | T103 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA. |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10POL08 |  | T103 LIGHT POLES FOR OLD PRODUCT STORAGE TANKS AREA. |  | 0 | M10TANKS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10PSV015 |  | PRESSURE RELIEF SAFETY VALVE FOR OUTLET TANK T-101 |  | PSV | M10T101 | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10PUBLICAD |  | COMMON PUBLIC ADD. SYSTEM PROD. STORAGE TANKSAREA |  | 0 | M10COMMON | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10TANKS |  | M10 SERIES (OLD) PRODUCT STORAGE TANKS |  | TK | MTERMINAL | 3 | TK | 617101-310600 | MTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | Low | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10TELEPHONE |  | COMMON TEL. SYSTEM FOR PRODUCT STORAGE TANKS AREA |  | 0 | M10COMMON | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10V301 |  | GAS OIL RECIVING VESEL FROM ADRD ON 10FT301 AT TANK 10T101 AREA. |  | VESSEL | M10FT301 | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M10V302 |  | GAS OIL RECIVING VESEL ON 10FT302 AT TANK 10T101 AREA. |  | VESSEL | M10FT302 | 1 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 10 | 1 | 1 | 5 | 50 | 1 | 3.3979 | Low | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M15PI163 |  | PRESS. INDICATING/TRANSMITTER AT MULTIPRODUCT PIG RECEIVER. |  | 0 | M15R04 | 3 | 0 | 617101-310600 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 5 | 2.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M15XPI125 |  | PIG SIGNALLER AT MULTIPRODUCT PIG RECEIVER. |  | 0 | M15R04 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 50 | 3.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20 |  | JET A1 LOADING PUMPS (ADNOC DISTRIBUTION) |  | 0 | MTERMINAL | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20MOTOR |  | Elec, Motors, Generators, Heaters, M20 |  | 0 | M20 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20PRESS |  | Control, Pressure, M20 |  | PSV | M20 | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | N | Medium | N | 0 | 12 | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20PSV111 |  | 16" GAS OIL LOWERING, DOWN STREAM OF 41ESD562. |  | PSV | M20VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20PSV131 |  | 16" ULG95 LOWERING, DOWN STREAM OF 41ESD572. |  | PSV | M20VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20PSV141 |  | 12" ULG91 LOWERING, DOWN STREAM OF 41ESD582. |  | PSV | M20VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20PSV151 |  | 8" KEROSENE LOWERING, DOWN STREAM OF 41ESD592. |  | PSV | M20VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20PUMP |  | All Pumps, M20 |  | 0 | M20 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20SYS |  | Control, DCS, PLC, Others, M20 |  | 0 | M20 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20TEMP |  | Control, Temperature, M20 |  | 0 | M20 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20TSV261 |  | SR#323625, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20TSV262 |  | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20TSV263 |  | SR# 323627 JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20TSV264 |  | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20TSV265 |  | JET A1, THERMAL RELIEF VALVE. |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20TSV516 |  | TRUCK LOADING, THERMAL RELIEF VALVE. |  | PSV | M20VALVE | 1 | PSV | 617101-310600 | MTERMINAL | NOT READY | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M20VALVE |  | All Valves, M20 |  | 0 | M20 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30 |  | JET A1 LOADING BASE (ADNOC DISTRIBUTION) |  | 0 | MTERMINAL | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M300FH301 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M300FH302 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M300FH303 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M300FH306 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M300FH307 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M300FH308 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M300FH309 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30FILTER |  | All Filters, Strainers, M30 |  | 0 | M30 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30FT261H |  | Flow TRANSMITTER at JET A1 Loading Bay H |  | 0 | M30SYS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30FT261J |  | Flow TRANSMITTER at JET A1 Loading Bay J |  | 0 | M30SYS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30LEVEL |  | Control Level, M30 |  | 0 | M30 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30MISC |  | Miscellaneous (All Others), M30 |  | 0 | M30 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30PRESS |  | Control, Pressure, M30 |  | 0 | M30 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30PSV101 |  | SR # 31067 RELIEF VALVE. 13.50 COLD SET PRESSURE, |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30PSV102 |  | SR # 31068 RELIEF VALVE. 13.50 COLD SET PRESSURE, |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30PSV271 |  | SR# 490294 PRESSURE RELIEF VALVE. |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30PSV272 |  | SR# 490293 PRESSURE RELIEF VALVE. |  | PSV | M400VALVE | 3 | PSV | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30SYS |  | Control, DCS, PLC, Others, M30 |  | 0 | M30 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30TSV261 |  | SR # 323628 RELIEF VALVE. 18.40 COLD SET PRESSURE, |  | 0 | M400VALVE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30TSV264 |  | SR# 323673 THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30TSV272 |  | SR # 420091 RELIEF VALVE. 13.99 COLD SET PRESSURE, |  | 0 | M400VALVE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30TSV274 |  | SR # 420093 RELIEF VALVE. 13.99 COLD SET PRESSURE, |  | 0 | M400VALVE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30TSV275 |  | SR # 420089 THERMAL RELIEF VALVE. 18.00 COLD SET PRESSURE, |  | 0 | M400VALVE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30TT261H |  | Temp. at Loading Bay H |  | 0 | M30MISC | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30TT261J |  | Temp. at Loading Bay J |  | 0 | M30MISC | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M30VALVE |  | All Valves, M30 |  | 0 | M30 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400 |  | MUSSAFAH TERMINAL STORAGE & DESPATCH. |  | 0 | MTERMINAL | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400BATT |  | Electrical, Battery Banks, M400 |  | 0 | M400ELEC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400BOILER |  | Boiler, Heater, Dryer, Furnace, M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400CCTV |  | TERMINAL IRP1 CCTV SYSTEMS |  | SEQPLC | M400 | 2 | SEQPLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 1 | 6 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400CINJ |  | CHEMICAL INJECTION SYSTEMS. |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400CP |  | CATHODIC PROTECTION SYSTEMS OF IRP-1 AT MUSAFFAH TERMINAL. |  | MOV | M400ELEC | 3 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400ELEC |  | Electrical, M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400F3 |  | FIRE Vehicle RD69435, Heavy equipment, M400 |  | 0 | M400FIRE | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FAN |  | Fan, Blower, Mixer, Soot Blower, M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FE006 |  | ORIFICE PLATE ASSEMBLY |  | ORIFICE | M400MISC | 3 | ORIFICE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH265 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | VALVE | M400FIRE | 3 | VALVE | 617101-310510 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH266 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | VALVE | M400FIRE | 3 | VALVE | 617101-310510 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH267 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | VALVE | M400FIRE | 3 | VALVE | 617101-310510 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH268 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | VALVE | M400FIRE | 3 | VALVE | 617101-310510 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low+T11064:U11074 | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH269 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | VALVE | M400FIRE | 3 | VALVE | 617101-310510 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH270 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | VALVE | M400FIRE | 3 | VALVE | 617101-310510 | IRPMTERMINAL | OPERATING | 1 | 1 | 5 | 5 | 50 | 50 | 4.7959 | Low | Low | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH271 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH272 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH273 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH274 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH275 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH276 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH277 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH278 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH279 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH280 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH281 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH282 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH283 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH284 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH285 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH286 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH287 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH288 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH289 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH290 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH291 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH292 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH296 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH297 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH298 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH300 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET #6. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH301 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH302 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH303 |  | FIRE HYDRANT FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH306 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | ALARMANC | M400FIRE | 3 | ALARMANC | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | f | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH307 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH308 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH309 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH310 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH311 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH312 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH313 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH314 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH315 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH316 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET XXX. |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH317 |  | FIRE HYDRANT FIRE WATER VALVE 4" ON STREET #11(WEST OF S/S). |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FH318 |  | FIRE HYDRANT BEHINED CONTROL ROOM, FIRE WATER VALVE 4" ON STREET "J". |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FI018 |  | PPM FLOW INDICATOR/ TRANSMITTER FOR PPD INJECTION PUMP 400P303A. |  | OPENLOOP | M400P303A | 2 | OPENLOOP | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FILTER |  | All Filters, Strainers, M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FIRE |  | All Fire equipment, M400 |  | 0 | M400 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | f | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FLOW |  | Control, Flow, M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FM279 |  | FIRE MONITOR FIRE WATER VALVE ON STREET XXX. |  | 0 | M400FIRE | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400FT017 |  | FLOW TX FOR PPD INJECTION PKG. |  | FL_TX | M400CINJ | 2 | FL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400HSSD301 |  | TO BE DELETED |  | 0 | 0 | 0 | 0 | 0 | 0 | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LCP001 |  | WWTP LOCAL CONTROL PANEL BOX |  | ESD_PNL | M400WWTP | 3 | ESD_PNL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LEVEL |  | Control Level, M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LI557 |  | LEVEL INDICATOR OF LUBRICITY IMPROVER TANK 302. |  | OPENLOOP | UREDUNDANT | 2 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LI558 |  | LEVEL INDICATOR FOR M400T302. |  | OPENLOOP | UREDUNDANT | 2 | OPENLOOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LP001B201 |  | STREET LIGHT POLE AT SUB STATION SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LP006Y301 |  | STREET LIGHT POLE AT CONTROL ROOM SIDE ROAD |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LP008B201 |  | STREET LIGHT POLE NEAR TANKTK-116 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LP011Y402 |  | STREET LIGHT POLE NEAR TANKTK-111 |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 2 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LPLP006B401 |  | STREET LIGHT POLE AT SOUTH BOUNDARY WALL SIDE |  | LIGHT | M400STLIGHT | 3 | LIGHT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LSHH223 |  | LEVEL SWITCH HH SLOP OIL TANK, WWTP. |  | LVL_SWT | M400WWTP | 3 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LSHH301 |  | Level for ULG 95 Tank 400-T-111 |  | LVL_SWT | M400SYS | 2 | LVL_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400LT566 |  | LEVEL TRANSMITTER FOR M400T302 |  | LVL_TX | UREDUNDANT | 2 | LVL_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | M400LT566-MC1 | ACTIVE | CONT | PM | FIC | 1 | YEARS | 23/05/19 | MC-PM-004-Y1
| M400ME004 |  | F-14 FIRE TRUCK 79046, MUSSAFAH TERMINAL. |  | 0 | M400F14 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400ME004-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 28/08/18 | MM-PM-029-M1
| M400ME005 |  | F-23 FIRE TRUCK 25759, MUSSAFAH TERMINAL. |  | 0 | M400F23 | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | M400ME005-UHE | ACTIVE | MECH | PM | EDS | 1 | MONTHS | 28/08/18 | MM-PM-029-M1
| M400ME005A |  | F/FIGHT. VEHICLE-CONTROL PANEL |  | 0 | M400F23 | 3 | 0 | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | f | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400MISC |  | Miscellaneous (All Others), M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400MON002 |  | CCTV MONITOR SYSTEM AT PLCR CONSOLE ROOM |  | WS_SYS | M400CCTV | 1 | WS_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400MON003 |  | CCTV MONITOR SYSTEM AT PLCR AT NEW ADMIN BUILDING |  | WS_SYS | M400CCTV | 1 | WS_SYS | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400MOTOR |  | Elec, Motors, Generators, Heaters, M400 |  | 0 | M400ELEC | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400MOV |  | MOTOR OPERATED VALVES OF IRP-1 AT MUSAFFAH TERMINAL |  | MOV | M400ELEC | 3 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400MP025A |  | MOTOR, SLOP INJECTION PUMPS |  | PUMPS | M400PUMP | 2 | PUMPS | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 5 | 10 | 5 | 5 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400P851 |  | PUMP FOR COLORIMETER ANALYZER MSFH-AAIN MLTI PROD TIE-IN. |  | ANALYSER | M400AT851 | 2 | ANALYSER | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCP017 |  | CP SYSTEM TRANSFORMER M400-PCP-017OBS AT MTERMINAL IRP-1 SUBSTATION. |  | BATTERY | M400CP | 1 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS01 |  | Test post of line no 3"-400-BD-136-11051-MV located near Tk-116. |  | 0 | M400T116 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS02 |  | Test post of line no 3"-400-BD-035-11051-M-V located Near Tk-112 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS03 |  | Test post of line no 4"-400-BD-013-11051-M-V located Near Tk-111 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS04 |  | Test post of line no 4"-400-BD-013-11051-MV located near Tk-111. |  | 0 | M400T111 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS05 |  | Test post of line no 4"-400-BD-113-11051-M-V located Near Tk-115 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS06 |  | Test post of line no 4"-400-BD-113-11051-M-V located Near Tk-115 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS07 |  | Test post of line no 4"-400-BD-088-11051-M-V located Near Tk-114 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS08 |  | Test post of line no 3"-400-BD-060-11051-MV located near Tk-113. |  | 0 | M400T113 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS09 |  | Test post of line no 4"-400-BD-394-11051-M-V located Near Tk-120 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS10 |  | Test post of line no 4"-400-BD-374-11051-M-V located Near Tk-119 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS11 |  | Test post of line no 4"-400-BD-264-11051-M-V located Near Tk-117 |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS12 |  | Test post of line no 1"-400-BD-959-11051-M-V located Near SLOP pump |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS13 |  | Test post of line no 1"-400-BD-961-11051-M-V located Near SLOP pump |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS14 |  | Test post of line no 2"-400-BD-449-11051-M-V located Near SLOP pump |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS15 |  | Test post of line no 1" fire water sprinkler header AT IRP-I booster pump house. |  | 0 | MPH2 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS16 |  | Test post of line no 1"-400-BD-656-11051-M-V located Near PLR sump |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS17 |  | Test post of IRP-I 16" MP RR-Muss blow down. |  | 0 | M400PLR012 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PCPS18 |  | Test post of line no 1"-400-BD-656-11051-M-V located Near PLR sump |  | MOTOR | M400MOTOR | 3 | MOTOR | 0 | 0 | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PDI023 |  | PRESSURE TRANSMITTER FOR PPD INJECTION PUMP 400P303A. |  | OPENLOOP | M400P303A | 2 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PG988 |  | PRESSURE GAUGE OF COOLING SYSTEM ON TANK 118. |  | INDICATR | M400PRESS | 3 | INDICATR | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PI654 |  | PR. RUWAIS MUSSAFAH MP P/L SCRAPER RECEIVER ISO |  | OPENLOOP | M400PRESS | 2 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PI754 |  | PR. JET A1 STORAGE TANK-BOOSTER PUMP 400P017A |  | OPENLOOP | M400P017A | 2 | OPENLOOP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PKG |  | AIR CONDITIONING Package units, M400 |  | 0 | M400MISC | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400POV717 |  | PNEUMATIC DRIVEN BV-RECIRCULATION FLOW |  | SD_VLV | M400WWTP | 1 | SD_VLV | 616101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PP014 |  | POWER PANEL AT WWTP (HVAC AND MISC LOADS) |  | LIGHT | M400MCC001 | 3 | LIGHT | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PRESS |  | Control, Pressure, M400 |  | 0 | M400 | 2 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV418 |  | SAFETY RELIEF VALVE FOR AUXILIARY LUB UNIT OF 400P16B. |  | 0 | M400P016B | 1 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV531 |  | SR # 31061 NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV532 |  | NAPHTHA/REFORMATE, THERMAL RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV533 |  | POUR POINT DEPRESS PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV534 |  | POUR POINT DEPRESS PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV535 |  | POUR POINT DEPRESS PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV536 |  | POUR POINT DEPRESS PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV537 |  | LUBRICITY IMPROVER PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV538 |  | LUBRICITY IMPROVER PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV539 |  | LUBRICITY IMPROVER PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV540 |  | LUBRICITY IMPROVER PUMP DISCHG, PRESS RELIEF VALVE |  | PSV | M400VALVE | 3 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV751 |  | SR # 31065 PRESURE RELIEF VALVE FOR DISCHRGE LINE |  | PSV | 0 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 1 | 1 | 1 | 100 | 5.3979 | Low | Low | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV926 |  | CORROSION INHIBITOR SKID PRESSURE RELIEF VALVE ON 400P80A. |  | PSV | M400VALVE | 2 | PSV | 616101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSV927 |  | CORROSION INHIBITOR SKID PRESSURE RELIEF VALVE ON 400P80B. |  | PSV | M400VALVE | 2 | PSV | 616101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSVX02 |  | PRESSURE SAFTETY VALVE |  | PSV | M400VALVE | 4 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 5 | 5 | 2.0969 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PSVX03 |  | PRESSURE SAFTETY VALVE |  | PSV | M400VALVE | 4 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 5 | 5 | 2.0969 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400PUMP |  | All Pumps, M400 |  | 0 | M400 | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400SCB |  | Electrical, Feeder,Transformer, Substn, M400 |  | 0 | M400SUBSTN | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400SSP |  | PUMP SEAL SYSTEM. |  | 0 | M400PUMP | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400SUBSTN |  | MUSAFFAH TERMINAL INTER REFINERY PIPELINES-1 SUB STATION 400 |  | 0 | MS/S | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400SYS |  | Control, DCS, PLC, Others, M400 |  | SEQPLC | M400 | 2 | SEQPLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T111 |  | ULG-95 TANK IRP MUSSAFFAH TERMINAL. |  | TK | M400TANKS | 3 | TK | 616101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 50 | 100 | 100 | 5 | 10.3979 | High | High | High | N | High | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T112 |  | ULG-95 TANK IRP MUSSAFFAH TERMINAL. |  | 0 | M400TANKS | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T113 |  | ULG-95 TANK IRP MUSSAFFAH TERMINAL. |  | 0 | M400TANKS | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T212 |  | OIL SEPARATOR FOR WWTP (CHAIN 1) |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T217 |  | DISOLVED AIR FLOTATION OF WWTP. |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T219 |  | OIL SEPARATOR FOR WWTP.(CHAIN 2) |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T221 |  | PRE FILTER WATER TANK AT WWTP. |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T222 |  | FINAL TREATED WATER TANK AT WWTP. |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T223 |  | SLOP OIL TANK AT WWTP. |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400T224 |  | FINAL SLOP OIL TANK AT WWTP. |  | VESSEL | M400WWTP | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 10 | 5 | 10 | 5 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TAH403C |  | Lube Oil Heater Tripped for 400-P-016A |  | ALARMANC | M400P016A | 3 | ALARMANC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TANKS |  | OIL STORAGE TANKS AT MUSSAFAH TERMINAL. |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TE474C |  | Lube Oil Header Temp. For Pump 400-P-019 |  | TEMP_ELE | M400TI474C | 3 | TEMP_ELE | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TEL |  | TELECOM SYSTEM OF STORAGE TERMINAL. |  | TELEPHON | M400 | 2 | TELEPHON | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TEL003 |  | ETISALAT TELECOM CABINET, MCR PANEL ROOM. |  | TELECOM | M400TEL | 2 | TELECOM | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TEMP |  | Control, Temperature, M400 |  | 0 | M400 | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV510 |  | SR # 323598, COLD SET 18.40, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV511 |  | ULG95 TRANSFERRING, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV512 |  | ULG95 TRANSFERRING, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV513 |  | ULG91 TRANSFERRING, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV515 |  | ULG95 TRANSFERRING, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV519 |  | TRANSFER PUMP 400P24A/B THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV521 |  | SR # 323664 COLD SET 18.00, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV522 |  | SR # 323665 COLD SET 18.40, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV523 |  | SR # 323504 COLD SET 47.00, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV541A |  | TSV OF NEPTHA/REFORM P/L, JET A1,CUSTODY METERING |  | 0 | M400FT541A | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV541B |  | SR # PB30535-39 TSV OF NEPTHA/REFORM P/L, JET A1, CUSTODY METERING |  | 0 | M400SYS | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV620A |  | THERMAL SAFETY VALVE, RUW-MUS CUSTODY METERING SKID |  | PSV | M400SYS | 2 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 5 | 50 | 10 | 50 | 50 | 8.4949 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV620B |  | THERMAL SAFETY VALVE, RUW-MUS, CUSTODY METERING SKID |  | PSV | M400SYS | 2 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 5 | 50 | 10 | 50 | 50 | 8.4949 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV620C |  | THERMAL SAFETY VALVE, RUW-MUS, CUSTODY METERING SKID |  | PSV | M400SYS | 2 | PSV | 616101-310600 | IRPMTERMINAL | OPERATING | 50 | 5 | 50 | 10 | 50 | 50 | 8.4949 | High | Medium | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV771A |  | JET A1 FLOW METRING TO ADIA, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV771B |  | JET A1 FLOW METRING TO ADIA, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV772A |  | JET A1 OFF SPEC FLOW METRING, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSV881 |  | 10'' SUCTION OF 400P016A/B, THERMAL RELIEF VALVE. |  | 0 | M400VALVE | 3 | 0 | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TSVX02 |  | TEMPERATURE SAFETY VALVE |  | PSV | M400VALVE | 4 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 5 | 5 | 2.0969 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400TT555 |  | TEMPRATURE TRANSMITTER FOR M400T301. |  | LVL_TX | M400T301 | 2 | LVL_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400V183 |  | SATURATION VESSEL ON DESCHARGE OF RECIRCULATION PUMPS. |  | PUCE | M400WWTPPUMP | 3 | PUCE | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400V185A |  | VESSEL A FOR ABSORBANT CARBON. |  | CLN_FLTR | M400WWTP | 4 | CLN_FLTR | 617101-310600 | IRPMTERMINAL | NOT READY | 1 | 1 | 5 | 1 | 1 | 5 | 1.3979 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400V185B |  | VESSEL B FOR ABSORBANT CARBON. |  | CLN_FLTR | M400WWTP | 4 | CLN_FLTR | 617101-310600 | IRPMTERMINAL | NOT READY | 1 | 1 | 5 | 1 | 1 | 5 | 1.3979 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400V185C |  | VESSEL C FOR ABSORBANT CARBON. |  | CLN_FLTR | M400WWTP | 4 | CLN_FLTR | 617101-310600 | IRPMTERMINAL | NOT READY | 1 | 1 | 5 | 1 | 1 | 5 | 1.3979 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400V186A |  | VESSEL A FOR GRANULATED ACTIVATED CARBON |  | CLN_FLTR | M400WWTP | 4 | CLN_FLTR | 617101-310600 | IRPMTERMINAL | NOT READY | 1 | 1 | 5 | 1 | 1 | 5 | 1.3979 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400V186B |  | VESSEL B FOR GRANULATED ACTIVATED CARBON |  | CLN_FLTR | M400WWTP | 2 | CLN_FLTR | 617101-310600 | IRPMTERMINAL | NOT READY | 10 | 10 | 10 | 10 | 5 | 10 | 5.699 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400VALVE |  | All Valves, M400 |  | 0 | M400 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400VE434 |  | VIBRATION FOR MAINLINE PUMP 400-P-018A |  | VIBRE_TX | M400P018A | 2 | VIBRE_TX | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400VH002 |  | O/HEAD CRANE AT TRANSFER PUMP HOUSE. |  | CRANE | MPH2 | 3 | CRANE | 616101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 50 | 10 | 4.0969 | Non Critical | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400VI408Y |  | (M400P016B) MAIN MOTOR RADIAL BEARING D.E |  | VIBRMON | M400P016B | 2 | VIBRMON | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400VSD16A |  | DRIVE,VARIABLE SPEED |  | SWBOARD | M400P016A | 3 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400VSD16B |  | DRIVE,VARIABLE SPEED |  | SWBOARD | M400P016B | 2 | SWBOARD | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WO01TO20 |  | WELDING SOCKET POWER OUTLETS OF IRP1. |  | 0 | MFPH1 | 3 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WTP |  | WAIST WATER TREATMENT PLANT AT MSP. |  | 0 | MREDUNDANT | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WWTP |  | WASTE WATER TREATMENT PLANT AT MUSAFFAH TERMINAL IRP-1 |  | 0 | M400 | 4 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WWTPAC |  | SPLIT A/C UNIT, M400WWTP |  | HVAC | M400WWTP | 4 | HVAC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | e | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WWTPANALZ |  | Analyzers, M400WWTP |  | 0 | M400WWTP | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WWTPFLOW |  | flow Instruments, M400WWTP |  | 0 | M400WWTP | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WWTPLEVEL |  | Level Instruments, M400WWTP |  | 0 | M400WWTP | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WWTPMOV |  | TO BE DELETED |  | 0 | 0 | 0 | 0 | 0 | 0 | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400WWTPPUMP |  | PUMPS, M400WWTP |  | 0 | M400WWTP | 2 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 12 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400XAC221 |  | NON EXISTANT***MANUAL CALL POINT AT MAIN GUARD HOUSE ENTERANCE. |  | 0 | M400FACP004 | 1 | 0 | 616101-310600 | MTERMINAL | MOTHBALLED | 1 | 1 | 1 | 5 | 5 | 5 | 2.0969 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M400XSP116 |  | SMOKE DETECTOR IN P.A. OF ADMINISTRATION BUILDING |  | FG_DET | M400FACP004 | 3 | FG_DET | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M40UTILITY |  | UTILITY AREA |  | 0 | MTERMINAL | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410 |  | MUSSAFAH STORAGE TERMINAL IRP2. |  | 0 | MTERMINAL | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410AUTO |  | All Vehicles, Heavy equipment, M410 |  | CRANE | M410 | 3 | CRANE | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410BATT |  | Electrical, Battery Banks, M410 |  | BATTERY | M410 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410CCTV |  | TERMINAL IRP2 CCTV SYSTEMS |  | CCTV_SYS | M410 | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410CINJ |  | CHEMICAL INJECTION SYSTEMS. |  | 0 | M410 | 3 | 0 | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410CNTRVL |  | Control valves, Actuators, SOV, Positioner, Regulator, M410 |  | CNTR_VLV | M410 | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410COMP |  | All Compressors, M410 |  | COMPRS | M410 | 3 | COMPRS | 617101-310600 | MTERMINAL | OPERATING | 1 | 10 | 1 | 5 | 10 | 1 | 2.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410CPRX |  | Cathodic Protection System, M410 |  | CATHPRO | M410 | 1 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410EXCH |  | All Exchanger, Cooler, Evaporator, M410 |  | HEATEXHR | M410 | 3 | HEATEXHR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 1 | 1 | 2.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FEXT |  | IRP2 FIRE EXTINGUISHERS. |  | FIREEF | M410FIRE | 2 | FIREEF | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | o | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FEXT50KG |  | IRP2 FIRE EXTINGUISHER DRY POWDER 50KG (OUTDOOR) |  | FIREEF | M410FIRE | 2 | FIREEF | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | o | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FEXT5KG |  | IRP2 FIRE EXTINGUISHER CO2 5KG (INDOOR) |  | FIREEF | 0 | 2 | FIREEF | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | o | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FEXT6KG |  | IRP2 FIRE EXTINGUISHER DRY POWDER 6KG (INDOOR) |  | FIREEF | 0 | 2 | FIREEF | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | o | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FEXT9KG |  | IRP2 FIRE EXTINGUISHER DRY POWDER 9KG (OUTDOOR) |  | FIREEF | 0 | 2 | FIREEF | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | o | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FFE2196001 |  | CANCELLED TAG |  | CRMO | M410MISC | 3 | CRMO | 617101-310600 | MTERMINAL | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FFE2196002 |  | CANCELLED TAG |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | MTERMINAL | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FFE2196003 |  | CANCELLED TAG |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | MTERMINAL | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FFE2196004 |  | CANCELLED TAG |  | F&G_PNL | M410MISC | 3 | F&G_PNL | 617101-310600 | MTERMINAL | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FFE2196008 |  | #1 IRON MAN DOMINATOR / MONITOR WITH BOOSTER PUMP-10K GPM COMBO UNIT. |  | PACKAGE | M410MISC | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | Y | High Critical | Y | 0 | 12 | m | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FFE2306001 |  | CANCELLED TAG |  | PUCEFF | M410SYS | 3 | PUCEFF | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FFE739 |  | CANCELLED TAG |  | CLDCFG | M410SYS | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FHDRNT |  | IRP2 FIRE HYDRANTS. |  | 0 | 0 | 1 | 0 | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FILTER |  | All Filters, Strainers, M410 |  | VESSEL | M410 | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 5 | 10 | 1 | 10 | 4.3979 | Low | Low | Low | N | Low | Y | 0 | 12 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FIRE |  | IRP2 FIRE PROTECTION SYSTEMS. |  | 0 | MFIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 |  | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FLOW |  | Control, Flow, M410 |  | FL_MTR | M410 | 3 | FL_MTR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FMONTR |  | IRP2 FIRE HYDRANTS WITH FIRE MONITORS. |  | 0 | 0 | 1 | 0 | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | Y | High Critical | Y | 0 | 6 | f | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU201A |  | RIM SEAL PROTECTION AT TANK-001 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU201B |  | RIM SEAL PROTECTION AT TANK-001 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU201C |  | RIM SEAL PROTECTION AT TANK-001 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU201D |  | RIM SEAL PROTECTION AT TANK-001 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU201E |  | RIM SEAL PROTECTION AT TANK-001 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU202A |  | RIM SEAL PROTECTION AT TANK-002 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU202B |  | RIM SEAL PROTECTION AT TANK-002 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU202C |  | RIM SEAL PROTECTION AT TANK-002 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU202D |  | RIM SEAL PROTECTION AT TANK-002 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU202E |  | RIM SEAL PROTECTION AT TANK-002 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU203A |  | RIM SEAL PROTECTION AT TANK-003 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU203B |  | RIM SEAL PROTECTION AT TANK-003 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU203C |  | RIM SEAL PROTECTION AT TANK-003 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU203D |  | RIM SEAL PROTECTION AT TANK-003 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU203E |  | RIM SEAL PROTECTION AT TANK-003 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU204A |  | RIM SEAL PROTECTION AT TANK-004 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU204B |  | RIM SEAL PROTECTION AT TANK-004 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU204C |  | RIM SEAL PROTECTION AT TANK-004 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU204D |  | RIM SEAL PROTECTION AT TANK-004 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU204E |  | RIM SEAL PROTECTION AT TANK-004 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU205A |  | RIM SEAL PROTECTION AT TANK-005 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU205B |  | RIM SEAL PROTECTION AT TANK-005 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU205C |  | RIM SEAL PROTECTION AT TANK-005 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU205D |  | RIM SEAL PROTECTION AT TANK-005 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU205E |  | RIM SEAL PROTECTION AT TANK-005 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU206A |  | RIM SEAL PROTECTION AT TANK-006 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU206B |  | RIM SEAL PROTECTION AT TANK-006 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU206C |  | RIM SEAL PROTECTION AT TANK-006 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU206D |  | RIM SEAL PROTECTION AT TANK-006 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU206E |  | RIM SEAL PROTECTION AT TANK-006 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU207A |  | RIM SEAL PROTECTION AT TANK-007 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU207B |  | RIM SEAL PROTECTION AT TANK-007 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU207C |  | RIM SEAL PROTECTION AT TANK-007 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU207D |  | RIM SEAL PROTECTION AT TANK-007 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU207E |  | RIM SEAL PROTECTION AT TANK-007 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU208A |  | RIM SEAL PROTECTION AT TANK-008 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU208B |  | RIM SEAL PROTECTION AT TANK-008 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU208C |  | RIM SEAL PROTECTION AT TANK-008 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU208D |  | RIM SEAL PROTECTION AT TANK-008 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU208E |  | RIM SEAL PROTECTION AT TANK-008 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU209A |  | RIM SEAL PROTECTION AT TANK-009 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU209B |  | RIM SEAL PROTECTION AT TANK-009 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU209C |  | RIM SEAL PROTECTION AT TANK-009 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU209D |  | RIM SEAL PROTECTION AT TANK-009 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU209E |  | RIM SEAL PROTECTION AT TANK-009 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU210A |  | RIM SEAL PROTECTION AT TANK-010 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU210B |  | RIM SEAL PROTECTION AT TANK-010 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU210C |  | RIM SEAL PROTECTION AT TANK-010 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU210D |  | RIM SEAL PROTECTION AT TANK-010 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU210E |  | RIM SEAL PROTECTION AT TANK-010 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU211A |  | RIM SEAL PROTECTION AT TANK-011 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU211B |  | RIM SEAL PROTECTION AT TANK-011 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU211C |  | RIM SEAL PROTECTION AT TANK-011 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU211D |  | RIM SEAL PROTECTION AT TANK-011 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU211E |  | RIM SEAL PROTECTION AT TANK-011 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU212A |  | RIM SEAL PROTECTION AT TANK-012 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU212B |  | RIM SEAL PROTECTION AT TANK-012 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU212C |  | RIM SEAL PROTECTION AT TANK-012 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU212D |  | RIM SEAL PROTECTION AT TANK-012 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU212E |  | RIM SEAL PROTECTION AT TANK-012 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU213A |  | RIM SEAL PROTECTION AT TANK-013 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU213B |  | RIM SEAL PROTECTION AT TANK-013 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU213C |  | RIM SEAL PROTECTION AT TANK-013 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU213D |  | RIM SEAL PROTECTION AT TANK-013 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU213E |  | RIM SEAL PROTECTION AT TANK-013 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU214A |  | RIM SEAL PROTECTION AT TANK-014 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU214B |  | RIM SEAL PROTECTION AT TANK-014 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU214C |  | RIM SEAL PROTECTION AT TANK-014 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU214D |  | RIM SEAL PROTECTION AT TANK-014 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU214E |  | RIM SEAL PROTECTION AT TANK-014 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU215A |  | RIM SEAL PROTECTION AT TANK-015 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU215B |  | RIM SEAL PROTECTION AT TANK-015 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU215C |  | RIM SEAL PROTECTION AT TANK-015 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU215D |  | RIM SEAL PROTECTION AT TANK-015 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU215E |  | RIM SEAL PROTECTION AT TANK-015 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU216A |  | RIM SEAL PROTECTION AT TANK-016 NORTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU216B |  | RIM SEAL PROTECTION AT TANK-016 EAST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU216C |  | RIM SEAL PROTECTION AT TANK-016 SOUTH SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU216D |  | RIM SEAL PROTECTION AT TANK-016 WEST SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FU216E |  | RIM SEAL PROTECTION AT TANK-016 NW SIDE |  | FGBHFD | M410FU200 | 1 | FGBHFD | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FV450A.ACT |  | Control Valve Globe Actuator |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FV450B.ACT |  | Control Valve Globe Actuator |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FV450C.ACT |  | Control Valve Globe Actuator |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410FVALV |  | IRP2 FIRE VALVES. |  | 0 | 0 | 2 | 0 | 617101-310510 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | o | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410GD |  | Gas detectors, M410 |  | FGBFFD | M410 | 1 | FGBFFD | 617101-310600 | MTERMINAL | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410HSD009 |  | NOT EXIST, DO NOT USE. |  | FG_DET | M410FACP002 | 4 | FG_DET | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LAB |  | Laboratory equipments, M410 |  | LAB_EQP | M410 | 3 | LAB_EQP | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LEVEL |  | Control Level, M410 |  | INDICATR | M410 | 3 | INDICATR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LI031A |  | LEVEL TX FOR DIESEL FUEL TANK (FIREWATER PUMP "A") |  | VESSEL | M410T031A | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LI031B |  | LEVEL TX FOR DIESEL FUEL TANK (FIREWATER PUMP "B") |  | VESSEL | M410T031B | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LI031C |  | LEVEL TX FOR DIESEL FUEL TANK (FIREWATER PUMP "C") |  | VESSEL | M410T031C | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LI031D |  | LEVEL TX FOR DIESEL FUEL TANK (FIREWATER PUMP "D") |  | VESSEL | M410T031D | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LI031E |  | LEVEL TX FOR DIESEL FUEL TANK (FIREWATER PUMP "E") |  | VESSEL | M410T031E | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LI031F |  | LEVEL TX FOR DIESEL FUEL TANK (FIREWATER PUMP "F") |  | VESSEL | M410T031F | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LI031G |  | LEVEL TX FOR DIESEL FUEL TANK (FIREWATER PUMP "G") |  | VESSEL | M410T031G | 3 | VESSEL | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 5 | 10 | 10 | 5 | 4.0969 | Low | Low | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LSZA |  | LOUD SPEAKER AT ZONE A |  | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LSZB |  | LOUD SPEAKER AT ZONE B |  | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LSZC |  | LOUD SPEAKER AT ZONE C |  | PA_SYS | M410PACB001 | 3 | PA_SYS | 617101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LV451A.ACT |  | Control Valve Globe Actuator |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LV451B.ACT |  | Control Valve Globe Actuator |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410LV451C.ACT |  | Control Valve Globe Actuator |  | CNTR_VLV | M410CNTRVL | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MISC |  | Miscellaneous (All Others), M410 |  | VESSEL | M410 | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOTOR |  | Elec, Motors, Generators, Heaters, M410 |  | GENRATOR | M410 | 3 | GENRATOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 10 | 1 | 1 | 2.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOV |  | Electric actuators, MOVs, M410 |  | MOV | M410 | 3 | MOV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOV1111 |  | Motor Operated Valve(Ball) OF 410-T-011 |  | MOV | 0 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOV1211 |  | Motor Operated Valve(Ball) OF 410-T-012 |  | MOV | 0 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOV1311 |  | Motor Operated Valve(Ball) OF 410-T-013 |  | MOV | 0 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOV1411 |  | Motor Operated Valve(Ball) OF 410-T-014 |  | MOV | 0 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOV1511 |  | Motor Operated Valve(Ball) OF 410-T-015 |  | MOV | 0 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410MOV1611 |  | Motor Operated Valve(Ball) OF 410-T-017 |  | MOV | 0 | 3 | MOV | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410P006D |  | TEST |  | PUMPS | 0 | 3 | PUMPS | 617101-310600 | MTERMINAL | MOTHBALLED | 1 | 5 | 1 | 5 | 1 | 1 | 1.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PCH |  | PC Hardware, M410 |  | TELECOM | M410 | 3 | TELECOM | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PKG |  | Packages unit, M410 |  | PACKAGE | M410 | 3 | PACKAGE | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PL108A |  | DE SEAL OIL PRESURE TRANSMITTER ITT PUMP 410-P-008A. |  | PRES_TX | M410P008A | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PL312 |  | IRP2 PIPE LINES TO & FROM THE MUSSAFAH TERMINAL P&TD. |  | 0 | M410 | 1 | 0 | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 5 | 1 | 1 | 5 | 2.0969 | Non Critical | Non Critical | Non Critical | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PRESS |  | Control, Pressure, M410 |  | PRES_TX | M410 | 3 | PRES_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PSV32A |  | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P032A | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PSV32B |  | FIRE PUMP DISC.PRESSURE SAFETY VALVE 18KG. |  | PSV | M410P032B | 1 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 100 | 100 | 100 | 10 | 100 | 10 | 10 | Very High | High | High | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PSV501 |  | PRESURE SAFETY VALVE ON 410P018A Anti-Static Neat Chemical Injection Pump DISCHARGE. |  | MOTOR | M410P018A | 3 | MOTOR | 615101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PT099 |  | THERMAL RELIEF VALVE |  | PRES_TX | M410VALVE | 3 | PRES_TX | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PUMP |  | Main Line Pumps, M410 |  | PUMPS | M410 | 3 | PUMPS | 617101-310600 | IRPMTERMINAL | OPERATING | 1 | 5 | 1 | 5 | 5 | 1 | 2.0969 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410PV357.ACT |  | Control Valve Actuator |  | CNTR_VLV | M410FIRE | 3 | CNTR_VLV | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX001 |  | CAMERA RECEIVER, NEAR TANK 11. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX002 |  | CAMERA RECEIVER NEAR WAREHOUSE |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX003 |  | CAMERA RECEIVER, NEAR Tank 15 |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX004 |  | CAMERA RECEIVER, NEAR Tank 14. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX005 |  | CAMERA RECEIVER, NEAR Tank 6. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX006 |  | CAMERA RECEIVER, IRP2 ITTP HOUSE AREA |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX007 |  | CAMERA RECEIVER, NEAR TANK 8. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX008 |  | CAMERA RECEIVER, NEAR TANK 10. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX009 |  | CAMERA RECEIVER, At The IRP2 Water Evaporation Pond. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX010 |  | CAMERA RECEIVER, ITTP HOUSE AREA |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX011 |  | CAMERA RECEIVER, INSIDE IRP2 SUB.S. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410RX012 |  | CAMERA RECEIVER, INSIDE SIS BLDG |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410SCB |  | Electrical, Feeder,Transformer, Substn, Switch gear, Accessories, M410 |  | TRANSFMR | M410 | 3 | TRANSFMR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410SIS |  | SATELLITE INSTRUMENTATION STATION OF MUSSAFAH OIL TERMINAL. |  | BLDG | MBLDG | 3 | BLDG | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410SS |  | ELECTRICAL SUB-STATION OF IRP-2 MUSSAFAH OIL TERMINAL. |  | BLDG | MBLDG | 3 | BLDG | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 1 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410SV |  | IRP II SAFETY RELEAFE VALVES |  | 0 | M410 | 3 | 0 | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410SYS |  | Control, DCS, PLC, Others, M410 |  | CLDCFG | M410 | 3 | CLDCFG | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410T032 |  | DIESEL FUEL TANK OF EMERGENCY DIESEL GENERATOR OF IRP-II. |  | TANK | M410EPB001 | 1 | TANK | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 50 | 5 | 50 | 10 | 6.7959 | Non Critical | Medium | Medium | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TANKS |  | STORAGE TANKS AT MUSSAFAH TERMINAL. |  | VESSEL | M410 | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | NOT READY | 10 | 10 | 5 | 10 | 100 | 1 | 5.699 | Non Critical | Low | Low | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TEL |  | TELECOM SYSTEM OF STORAGE TERMINAL. |  | TELEPHON | M410 | 2 | TELEPHON | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TELM |  | Telecom, Telemetry, PA system, M410 |  | CCTV_SYS | M410 | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TELPLCR |  | 410TEL021 - INSIDE THE PLCR (PIPELINE CONTROL ROOM) |  | TELECOM | M410TEL | 3 | TELECOM | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TELSIS |  | 410TEL011 INSIDE THE SIS (Sat.Inst.Shelter) |  | TELECOM | M410TEL | 3 | TELECOM | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TELSS |  | 410TEL007 INSIDE THE IRP2 Substation. |  | TELECOM | M410TEL | 3 | TELECOM | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TEMP |  | Control, Temperature, M410 |  | TEMP_TX | M410 | 3 | TEMP_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX001 |  | FIBER TRANSMITTER TO MCR, Tank 11 AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX0010 |  | TO BE DELETED |  | 0 | M410CCTV | 0 | 0 | 0 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX002 |  | FIBER TRANSMITTER TO MCR, WAREHOUSE AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX003 |  | FIBER TRANSMITTER TO MCR, TANK 15 AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX004 |  | FIBER TRANSMITTER TO MCR, TANK 14 AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX005 |  | FIBER TRANSMITTER TO MCR, TANK 6 AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX006 |  | FIBER TRANSMITTER TO MCR, ITTP HOUSE AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX007 |  | FIBER TRANSMITTER TO MCR, TANK 8 AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX008 |  | FIBER TRANSMITTER TO MCR, TANK 10 AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX009 |  | FIBER TRANSMITTER TO MCR, WATER EVAPORATION POND AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX010 |  | FIBER TRANSMITTER TO MCR, ITTP HOUSE AREA. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX011 |  | FIBER TRANSMITTER TO MCR, IRP2 SUB.S. BLDG. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410TX012 |  | FIBER TRANSMITTER TO MCR, SIS BLDG INSIDE. |  | CCTVSEC | M410CCTV | 3 | CCTVSEC | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410UPSAC003B |  | 360 CELLS (SLM 710-1) FOR AC UPS 410UPSAC002A IN ECR BUILDING. |  | INVRT_UP | M410UPSAC002B | 3 | INVRT_UP | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | e | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410VALVE |  | All Valves, M410 |  | PSV | M410 | 3 | PSV | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410VESSEL |  | SUMP Vessel OR Tank, M410 |  | VESSEL | M410 | 3 | VESSEL | 617101-310600 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410VIBR |  | Control, Vibration, M410 |  | INDICATR | M410 | 3 | INDICATR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410XGH312 |  | NOT USED REPLACED BY M410XGH812** H2 GAS DETECTORS-IRP-II PLCR EXTENSION-BATTERY ROOM CEILING-NORTH SIDE |  | FG_DET | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M410XGH613 |  | NOT USED REPLCED BY M410XGH813** H2 GAS DETECTORS-IRP-II PLCR EXTENSION-BATTERY ROOM CEILING-SOUTH SIDE |  | FG_DET | M400GACP001B | 1 | FG_DET | 617101-310600 | MFPS | MOTHBALLED | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M41ESD561 |  | ESD VALVE FOR MULTIPRODUCT INLET METERING |  | 0 | M10INLETMET | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M41ESD571 |  | ESD VALVE FOR MULTIPRODUCT INLET METERING |  | 0 | M10INLETMET | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M41ESD581 |  | ESD VALVE FOR MULTIPRODUCT INLET METERING |  | 0 | M10INLETMET | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M41ESD591 |  | ESD VALVE FOR MULTIPRODUCT INLET METERING |  | 0 | M10INLETMET | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M41ESD602 |  | INLET ESD VALVE FOR SLOPS TANK T-110 |  | EMERSDD | M10T110 | 2 | EMERSDD | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50MOV121 |  | FIRE FIGHTING FOAM SPRAY MOV FOR TANK T-101. |  | MOV | M10T101 | 2 | MOV | 616101-310600 | MTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50MOV122 |  | FIRE FIGHTING FOAM SPRAY MOV FOR TANK T-102. |  | MOV | M10T102 | 2 | MOV | 616101-310600 | MTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50MOV123 |  | FIRE FIGHTING FOAM SPRAY MOV FOR TANK T-103. |  | MOV | M10T103 | 2 | MOV | 616101-310600 | MTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV131A |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-101 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV131B |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-101 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV132A |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-102 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV132B |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-102 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV133A |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-103 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV133B |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-103 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV134F |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-104 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV134W |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-104 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV135F |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-105 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV135W |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-105 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV136F |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-106 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV136W |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-106 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV137F |  | FOAM SOLENOID VALVE FOR TANK T-107 |  | SOL_VLV | UREDUNDANT | 2 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 50 | 5 | 10 | 6.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV137W |  | WATERSPRAY SOLENOID VALVE FOR TANK T-107 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV138W |  | WATERSPRAY SOLENOID VALVE FOR TANK T-108 |  | SOL_VLV | UREDUNDANT | 2 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 50 | 5 | 10 | 6.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV139W |  | WATERSPRAY SOLENOID VALVE FOR TANK T-109 |  | SOL_VLV | UREDUNDANT | 2 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 50 | 5 | 10 | 6.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV140W |  | WATERSPRAY SOLENOID VALVE FOR TANK T-110 |  | SOL_VLV | UREDUNDANT | 2 | SOL_VLV | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 50 | 50 | 5 | 10 | 6.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50SOV160W |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-110 |  | 0 | UREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50WOV138W |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-108 |  | 0 | M10T108 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M50WOV139W |  | FIRE FIGHTING SOLENOID VALVE FOR TANK T-109 |  | 0 | M10T109 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M51AT103 |  | LPG SCRAPER PIG RECEIVER AT MS&P/ADNOC-D. |  | 0 | M51FQRAL103 | 2 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M600ACCUA |  | WRONG TAG TO BE DELETED. |  | 0 | MQ600MOTOR | 3 | 0 | 616101-310600 | IRPMAQTA | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60EDB001 |  | EMERGENCY DISTRIBUTION BOARD |  | 0 | M60SUBSTN | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FAC01 |  | TRANSFORMER/RECTIFIER C.P FOR TANK T-104 TO T-107 |  | MCC_SWBD | M60MDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FAC04 |  | TRANSFORMER/RECTIFIER C.P FOR TANK T-108 TO T-110 |  | MCC_SWBD | M60MDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FAD04 |  | TRANSFORMER/RECTIFIER C.P FOR TANK T-101 TO T-103 |  | MCC_SWBD | M60MDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FAF01 |  | STARTER FOR SLOPS PUMP P-173 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FAG01 |  | STARTER FOR SLOPS P-172 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC01 |  | FEEDER FOR 10-MOV561,562,564,565,568,568 |  | MCC_SWBD | M60EDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC-01 |  | FEEDER FOR LIGHTING CONTROL PANEL MDB |  | MCC_SWBD | M60MDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC02 |  | FEEDER FOR 10-MOV571,572,573,574 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC03 |  | FEEDER FOR 10-MOV581,582,583,584 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC04 |  | FEEDER FOR 10-MOV591,592,601,602,603,604 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC05 |  | FEEDER FORTANK AREA LIGHTING T-101, 102, 103 |  | MCC_SWBD | M60MDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC06 |  | FEED.TANK AREA LIGHT.T-104,105,106,108,108,109,110 |  | MCC_SWBD | M60MDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBC6 |  | FEEDER FOR 10-MOV542,543,544,545,546 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBD03 |  | FEEDER FOR 10-MOV-541 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBD07 |  | FEEDER FOR 50-MOV124A/124B |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE01 |  | FEEDER FOR 50-MOV125A/125B |  | MCC_SWBD | M60EDB001 | 3 | MCC_SWBD | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE02 |  | 16A SOCKET FOR OCTANE TANKS 16-S3, S4,S5,S6 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE02MOV |  | FEEDER FOR 50-MOV126A/126B |  | MOV | M60EDB001 | 3 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE03 |  | 16ASOCK. FORGASOIL TANKS & DISPEN. 16-S8,S8,S9,S10 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE03MOV |  | FEEDER FOR 50-MOV120,121,122,123 |  | MOV | M60EDB001 | 3 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE04 |  | 16ASOCKET FOR PUMP HOUSE/LOADING BAYS 16-S11,12,13 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE04MOV |  | FEEDER FOR 50-MOV127,128,129,130 |  | MOV | M60EDB001 | 3 | MOV | 616101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE05 |  | 32A SOCKET FOR KEROSENE AND SLOPS TANKS, 32-S1 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBE6 |  | 32A SOCKET FOR OCTANE TANKS, 32-S2,S3 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF01 |  | 32A SOCKET FOR GASOIL TANKS, 32-S4,S5 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF01LCP |  | FEEDER FOR LIGHTING CONTROL PANEL |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF02 |  | 63A SOCKET FOR OCTANE TANKS, 63-S1,S2 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF02LP |  | FEEDER FOR POLE LIGHTS POLE 01,02,03,04,05 |  | 0 | M60EDB001 | 0 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF03 |  | 63A SOCKET FOR GASOILTANKS 63-S3 |  | 0 | M60MDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF03LP |  | FEEDER FOR POLE LIGHTS POLE 06,07,08 |  | 0 | M60EDB001 | 0 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF04 |  | FEEDER FOR POLE LIGHTS POLE 09,10,11 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF05 |  | FEEDER FOR POLE LIGHTS POLE 12,13,14 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60FBF06 |  | FEEDER FOR POLE LIGHTS POLE 15,16,17 |  | 0 | M60EDB001 | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| M60SUBSTN |  | SUBSTATION AREA |  | 0 | MS/S | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MADMIN |  | OLD ADMIN BLDG. OF MUSSAFAH OIL TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MADMIN1 |  | NEW ADMINISTRATION BLDG. OF MUSSAFAH OIL TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MADMIN1FP1 |  | FOUNTAIN WATER FILTER PUMP AT NEW ADMIN BUILDING- P&TD. |  | PUCEWI | MADMIN1 | 4 | PUCEWI | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MADMIN1FP2 |  | FOUNTAIN WATER FILTER PUMP AT NEW ADMIN BUILDING- P&TD. |  | PUCEWI | MADMIN1 | 4 | PUCEWI | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MADMIN1WP1 |  | POTABLE WATER PUMP 1, AT NEW ADMIN BUILDING ROOF-TOP. |  | PUCEWI | MADMIN1 | 3 | PUCEWI | 617101-310510 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MADMIN1WP2 |  | POTABLE WATER PUMP 2, AT NEW ADMIN BUILDING ROOF-TOP. |  | PUCEWI | MADMIN1 | 3 | PUCEWI | 617101-310510 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MADMIN2 |  | ******DO NOT USE****** |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MBLDG |  | ALL BUILDINGS OF MUSSAFAH OIL TERMINAL. |  | 0 | M400 | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MCOMMON |  | COMMON LOCATIONS OF NATIONAL OIL TERM. AT MUSSAFAH |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MECR |  | MAIN CONTROL ROOM EXTENSION BUILDING OF MUSSAFAH TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFBAY1 |  | FIRE BUILDING BAY#1 OF MUSSAFAH TERMINAL. |  | 0 | MFGRG | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFBAY2 |  | FIRE BUILDING BAY#2 OF MUSSAFAH TERMINAL. |  | 0 | MFGRG | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFBAY3 |  | FIRE BUILDING BAY#3 OF MUSSAFAH TERMINAL. |  | 0 | MFGRG | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFGRG |  | FIRE BUILDING GARAGE OF MUSSAFAH TERMINAL. |  | 0 | MFIRE | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFIRE |  | FIRE & SAFETY BUILDING OF MUSSAFAH TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFPH1 |  | IRP1 FIRE PUMP HOUSE FOR FIRE WATER FOR IRP1 TANKS ON STREET "D". |  | 0 | M400FIRE | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFPH2 |  | IRP2 FIRE PUMP HOUSE & PROTECTION SYSTEMS. |  | 0 | 0 | 2 | 0 | 617101-310510 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFWH |  | FIRE BUILDING WAREHOUSE AT MUSSAFAH TERMINAL. |  | 0 | MFIRE | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MFWHGD |  | FIRE BUILDING WAREHOUSE GARAGE DOOR AT MUSSAFAH TERMINAL. |  | 0 | MFWH | 3 | 0 | 617101-310510 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE1 |  | MAIN GATE #1, SINGLE, 2 CARS, ELECTRICAL SLIDING TYPE, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE10 |  | MUS.TER GATE #10, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE11 |  | MUS.TER GATE #11, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE12 |  | MUS.TER GATE #12, DOUBLE 2 CARS, PAD LOCK, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE13 |  | MUS.TER GATE #13, DOUBLE 2 CARS, PAD LOCK, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE14 |  | MUS.TER GATE #14, DOUBLE 2 CARS, PAD LOCK, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE15 |  | MUS.TER GATE #15, DOUBLE 2 CARS, PAD LOCK, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE16 |  | MUS.TER GATE #16, DOUBLE 2 CARS, PAD LOCK, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE18 |  | MUS.TER GATE #18, SINGL 1 PERSON, PUSH BAR TYPE, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE1A |  | MAIN GATE #1A, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE1E |  | MAIN GATE #1E, SINGLE, 1 CAR ENTERING, ELECTRICAL BARRIER ARM, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE1X |  | MAIN GATE #1X, SINGLE, 1 CAR EXITING, ELECTRICAL BARRIER ARM, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE2 |  | MUS.TER GATE #2, SINGLE, 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE3 |  | MUS.TER GATE #3, SINGLE, 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE4 |  | MUS.TER GATE #4, SINGLE, 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE5 |  | MUS.TER GATE #5, DOUBLE 2 CARS, PAD LOCK, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE5A |  | MUS.TER GATE #5A, SINGLE, 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE5B |  | MUS.TER GATE #5B, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE6 |  | MUS.TER GATE #6, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE7 |  | MUS.TER GATE #7, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE8 |  | MUS.TER GATE #8, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATE9 |  | MUS.TER GATE #9, SINGLE 1 PERSON, PUSH BAR, FENCE & FRAME, OF MUSSAFAH OIL TERMINAL. |  | 0 | MGATEH | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MGATEH |  | MAIN GATE HOUSE OF MUSSAFAH OIL TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MLIGHTING |  | M10 LIGHTING OF NATIONAL OIL TERMINAL AT MUSAFA |  | 0 | M10COMMON | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 12 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MMAINT |  | MAINTENANCE BUILDING OF MUSSAFAH OIL TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MMCR |  | MAIN CONTROL ROOM BUILDING OF MUSSAFAH TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MMWS |  | MAINTENANCE MAIN WORKSHOP AT MUSAFAH TERMINAL. |  | 0 | MMAINT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MOTOR |  | DEWATRING MOTORS |  | 0 | R0046 | 3 | 0 | 616101-490310 | RUCW | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MPH1 |  | MUSSAFAH TERMINAL MAIN PUMP HOUSE. |  | 0 | MPHS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MPH2 |  | MUSSAFAH TERMINAL TRANSFER PUMP HOUSE. |  | 0 | MPHS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MPH3 |  | MUSSAFAH TERMINAL FIRE PUMP HOUSE. |  | 0 | MPHS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MPH4 |  | MUSSAFAH TERMINAL IRP2 TRANSFER PUMP HOUSE. |  | 0 | MPHS | 3 | 0 | 617101-310600 | MTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MPH5 |  | MUSSAFAH TERMINAL IRP2 FIRE PUMP HOUSE. |  | 0 | MPHS | 3 | 0 | 617101-310600 | MTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MPH6 |  | MUSSAFAH TERMINAL IRP2 MAIN PUMP HOUSE. |  | 0 | MPHS | 3 | 0 | 617101-310600 | MTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MPHS |  | ALL PUMP HOUSES OF MUSSAFAH PTD. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600 |  | IRP, MAQTA INTERMEDIATE STATION. |  | 0 | MTERMINAL | 3 | 0 | 617101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600ACCUA |  | OUTSIDE ISOLATOR PANEL "A" AT MAQTAA STATION. |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600ACCUB |  | OUTSIDE ISOLATOR PANEL "B" AT MAQTAA STATION. |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600BATT |  | Electrical, Battery Banks, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600EP01 |  | MAQTAA BUILDING ERTHING PIT #1. |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600EP02 |  | MAQTAA BUILDING ERTHING PIT #2. |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600EP03 |  | MAQTAA BUILDING ERTHING PIT #3. |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600EP04 |  | MAQTAA BUILDING ERTHING PIT #4. |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600EP05 |  | MAQTAA BUILDING ERTHING PIT #5. |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600FLOW |  | Control, Flow, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600GM77 |  | SUMP PUMP Elec, Motors, MQ600 |  | 0 | MQ600MOTOR | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600HXD201B |  | LINEAR HEAT DETECTOR FOR SUMP TANK AT MAQTA TERMINAL |  | FG_DET | MQ600FACP001 | 3 | FG_DET | 616101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600LEVEL |  | Control Level, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600ME001 |  | MOTOR OF THE INERTIA SAND FILTER. |  | 0 | MQ600MOTOR | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600MISC |  | Miscellaneous (All Others), MQ600 |  | 0 | MQ600 | 3 | 0 | 617101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600MOTOR |  | Elec, Motors, Generators, Heaters, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600MOV |  | MQ600 MOVS |  | MOV | MQ600 | 3 | MOV | 617101-310600 | IRPMAQTA | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 0 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600PRESS |  | Control, Pressure, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600PUMP |  | All Pumps, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600SCB |  | Electrical, Feeder,Transformer, Substn, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600SYS |  | Control, DCS, PLC, Others, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600TEMP |  | Control, Temperature, MQ600 |  | 0 | MQ600 | 3 | 0 | 616101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600VALVE |  | All Valves, MQ600 |  | 0 | MQ600 | 3 | 0 | 617101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MQ600VESSEL |  | Vessel, Tank, Column, Tower, Reactor, MQ600 |  | 0 | MQ600 | 3 | 0 | 617101-310600 | IRPMAQTA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MS/S |  | SUB STATIONS OF MUSSAFAH OIL TERMINAL. |  | 0 | MBLDG | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MUSSAFAH_FIRE_VOICE |  | Fire Station Building |  | 0 | 0 | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MVEHICLES |  | AUTOMOBILE, CAR, TRUCK, VAN, BUS, & ALL MOBILE ASSETS ON ROADS. |  | VEHICLE | MTERMINAL | 3 | VEHICLE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | a | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MWH |  | WARE HOUSE BUILDING OF MUSAFFAH TERMINAL IRP-1 |  | 0 | MBLDG | 2 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MWSPDP1 |  | MAIN WORKSHOP PORTABLE DIAPHRAM PUMP 3". |  | 0 | MMWS | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T |  | Pipelines & Terminal - Mussafah |  | 0 | SDITASSETS | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_400_SS |  | IRP-I Substation |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_410_SS |  | IRP-II Substation |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_FIRE_STN |  | Fire Station Building |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_ITSTORE |  | Temporary IT Storage Room |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_NEW_ADMIN |  | New Admin Building |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_OLD_ADMIN |  | Old Admin Building |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_PLCR |  | Pipeline Control Room |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_SECURITY |  | Security Gate Building |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_SIS |  | Satellite Instrument Shelter |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P&T_WAREHOUSE |  | Warehouse Building |  | 0 | P&T | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100 |  | SHEWIHAT RECIVING STATION OF INTER REFINERY PIPELINES. |  | PIPING | MTERMINAL | 3 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | i | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100ALRM |  | Control, Alarm System, PL100 |  | ALARMANC | PL100 | 3 | ALARMANC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100BATT |  | Electrical, Battery Banks, PL100 |  | BATTERY | PL100 | 3 | BATTERY | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100CNTRVL |  | Control valves, Actuators, SOV, Positioner, Regulator, PL100 |  | CNTR_VLV | PL100 | 3 | CNTR_VLV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100FILTER |  | All Filters, Strainers, PL100 |  | VESSEL | PL100 | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100FLOW |  | Control, Flow, PL100 |  | FL_MTR | PL100 | 3 | FL_MTR | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100GD |  | Gas detectors, PL100 |  | FG_DET | PL100 | 3 | FG_DET | 616101-310600 | MFPS | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | g | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100HVAC |  | Compressor, Condenser, Air Conditioner, Chiller, Humidifier, PL100 |  | HVAC | PL100 | 3 | HVAC | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100LEVEL |  | Control Level, PL100 |  | LVL_TX | PL100 | 3 | LVL_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100MISC |  | Miscellaneous (All Others), PL100 |  | BLDGS | PL100 | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100MOV |  | Electric actuators, MOVs, SHEWIHAT RECIVING STATION. |  | MOV | PL100 | 3 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100PRESS |  | Control, Pressure, PL100 |  | PRES_TX | PL100 | 3 | PRES_TX | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100SCB |  | Electrical, Feeder,Transformer, Substn, Switch gear, Accessories, PL100 |  | BLDGS | PL100 | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100SYS |  | Control, DCS, PLC, Others, PL100 |  | BLDGS | PL100 | 3 | BLDGS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100TELM |  | Telecom, Telemetry, PA system, PL100 |  | PA_SYS | PL100 | 3 | PA_SYS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | t | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100TEMP |  | Control, Temperature, PL100 |  | TEMP_ELE | PL100 | 3 | TEMP_ELE | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100VALVE |  | All Valves, PL100 |  | CONTHNDV | PL100 | 3 | CONTHNDV | 617101-310600 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL100VESSEL |  | Vessel, Tank, Column, Tower, Reactor, Dryer, Mixer, Sphere, PL100 |  | VESSEL | PL100 | 3 | VESSEL | 617101-310600 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300 |  | INTER REFINERY PIPELINES. |  | PIPING | MTERMINAL | 3 | PIPING | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 | 60 | i | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300BAT001 |  | SVS 1 BATTERY BANK A, B, C, & D 152 NOs TOTAL. |  | BATTERY | PL300SVS1 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300BAT002 |  | SVS 2 BATTERY BANK A, B, C, & D 152 NOs TOTAL. |  | BATTERY | PL300SVS2 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300BAT003 |  | SVS 3 BATTERY BANK A, B, C, & D 152 NOs TOTAL. |  | BATTERY | PL300SVS3 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300BAT004 |  | SVS 4 BATTERY BANK A, B, C, & D 152 NOs TOTAL. |  | BATTERY | PL300SVS4 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300BAT005 |  | SVS 5 BATTERY BANK A, B, C, & D 152 NOs TOTAL. |  | BATTERY | PL300SVS5 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300BAT006 |  | SVS 6 BATTERY BANK A, B, C, & D 152 NOs TOTAL. |  | BATTERY | PL300SVS6 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300BAT007 |  | SVS 7 BATTERY BANK A, & B 76 NOs TOTAL. |  | BATTERY | PL300SVS7 | 3 | BATTERY | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300CCTV |  | PIPELINE CCTV SYSTEMS |  | CCTV_SYS | PL300 | 3 | CCTV_SYS | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300CP |  | CATHODIC PROTECTION SYSTEM & TEST POINTS. |  | CATHPRO | PL300 | 3 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300CP14 |  | CATHODIC PROTECTION TEST POINT 14/191 KM RUWAIS / MUSAFAH.. |  | CATHPRO | PL300CP | 3 | CATHPRO | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300CPPSM004 |  | C.P. STATION FOR SVS4. |  | CATHPRO | PL300TCP004 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300EOV30321 |  | PL300EOV30301 MULTI PRODUCT-HPU OP. BALL VALVE,16"X900LB |  | VABAOP | PL300EOV30301 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30321-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 09/08/18 | MM-PM-014-M6
| PL300EOV30326 |  | PL300EOV30306 MULTI PRODUCT-HPU OP. BALL VALVE,16"X900LB |  | VABAOP | PL300EOV30306 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300EOV30326-MM1 | ACTIVE | MECH | PM | EDS | 6 | MONTHS | 25/10/18 | MM-PM-014-M6
| PL300EP1 |  | BUILDING EARTHING PITS FOR SVS1 (2 NOs). |  | ECBL_RLC | PL300SVS1 | 3 | ECBL_RLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300EP2 |  | BUILDING EARTHING PITS FOR SVS2 (2 NOs). |  | ECBL_RLC | PL300SVS2 | 3 | ECBL_RLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300EP3 |  | BUILDING EARTHING PITS FOR SVS3 (2 NOs). |  | ECBL_RLC | PL300SVS3 | 3 | ECBL_RLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300EP4 |  | BUILDING EARTHING PITS FOR SVS4 (2 NOs). |  | ECBL_RLC | PL300SVS4 | 3 | ECBL_RLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300EP5 |  | BUILDING EARTHING PITS FOR SVS5 (2 NOs). |  | ECBL_RLC | PL300SVS5 | 3 | ECBL_RLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300EP6 |  | BUILDING EARTHING PITS FOR SVS6 (2 NOs). |  | ECBL_RLC | PL300SVS6 | 3 | ECBL_RLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300EP7 |  | BUILDING EARTHING PITS FOR SVS7 (2 NOs). |  | ECBL_RLC | PL300SVS7 | 3 | ECBL_RLC | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300INV001 |  | INVERTER PANEL UNIT FOR SVS1. |  | INVRT_UP | PL300SVS1 | 3 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300INV002 |  | INVERTER PANEL UNIT FOR SVS2. |  | INVRT_UP | PL300SVS2 | 3 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300INV003 |  | INVERTER PANEL UNIT FOR SVS3. |  | INVRT_UP | PL300SVS3 | 3 | INVRT_UP | 616101-310600 | IRPMTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300INV004 |  | INVERTER PANEL UNIT FOR SVS4. |  | INVRT_UP | PL300SVS4 | 3 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300INV005 |  | INVERTER PANEL UNIT FOR SVS5. |  | INVRT_UP | PL300SVS5 | 3 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300INV006 |  | INVERTER PANEL UNIT FOR SVS6. |  | INVRT_UP | PL300SVS6 | 3 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300INV007 |  | INVERTER PANEL UNIT FOR SVS7. |  | INVRT_UP | PL300SVS7 | 3 | INVRT_UP | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB1CB |  | HPU JUNCTION BOX CONTROL BOARD 22 BOLTS IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU1 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB1M |  | HPU JUNCTION BOX MAIN 28 BOLTS IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU1 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB2CB |  | HPU JUNCTION BOX CONTROL BOARD 22 BOLTS IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU2 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB2M |  | HPU JUNCTION BOX MAIN 28 BOLTS IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU2 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB3CB |  | HPU JUNCTION BOX CONTROL BOARD 22 BOLTS IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU3 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB3M |  | HPU JUNCTION BOX MAIN 28 BOLTS IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU3 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB4CB |  | HPU JUNCTION BOX CONTROL BOARD 22 BOLTS IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU4 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB4M |  | HPU JUNCTION BOX MAIN 28 BOLTS IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU4 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB5CB |  | HPU JUNCTION BOX CONTROL BOARD 22 BOLTS IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU5 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB5M |  | HPU JUNCTION BOX MAIN 28 BOLTS IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU5 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB6CB |  | HPU JUNCTION BOX CONTROL BOARD 22 BOLTS IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU6 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB6M |  | HPU JUNCTION BOX MAIN 28 BOLTS IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | ELOCLSW | PL300HPU6 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB7CB |  | HPU JUNCTION BOX CONTROL BOARD 22 BOLTS IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | ELOCLSW | PL300HPU7 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300JB7M |  | HPU JUNCTION BOX MAIN 28 BOLTS IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | ELOCLSW | PL300HPU7 | 3 | ELOCLSW | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP001A |  | HPU PUMP MOTOR "A" IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU1 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP001B |  | HPU PUMP MOTOR "B" IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU1 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP002A |  | HPU PUMP MOTOR "A" IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU2 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP002B |  | HPU PUMP MOTOR "B" IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU2 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP003A |  | HPU PUMP MOTOR "A" IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU3 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP003B |  | HPU PUMP MOTOR "B" IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU3 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP004A |  | HPU PUMP MOTOR "A" IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU4 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP004B |  | HPU PUMP MOTOR "B" IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU4 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP005A |  | HPU PUMP MOTOR "A" IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU5 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP005B |  | HPU PUMP MOTOR "B" IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU5 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP006A |  | HPU PUMP MOTOR "A" IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU6 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP006B |  | HPU PUMP MOTOR "B" IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | MOTOR | PL300HPU6 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP007A |  | HPU PUMP MOTOR "A" IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | MOTOR | PL300HPU7 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300MP007B |  | HPU PUMP MOTOR "B" IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | MOTOR | PL300HPU7 | 3 | MOTOR | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P001A |  | HPU PUMP "A" IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU1 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P001B |  | HPU PUMP "B" IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU1 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P002A |  | HPU PUMP "A" IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU2 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P002B |  | HPU PUMP "B" IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU2 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P003A |  | HPU PUMP "A" IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU3 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P003B |  | HPU PUMP "B" IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU3 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P004A |  | HPU PUMP "A" IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU4 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P004B |  | HPU PUMP "B" IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU4 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P005A |  | HPU PUMP "A" IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU5 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P005B |  | HPU PUMP "B" IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU5 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P006A |  | HPU PUMP "A" IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU6 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P006B |  | HPU PUMP "B" IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | PUREOH | PL300HPU6 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P007A |  | HPU PUMP "A" IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | PUREOH | PL300HPU7 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300P007B |  | HPU PUMP "B" IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | PUREOH | PL300HPU7 | 3 | PUREOH | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PRESS |  | Control, Pressure, PL300 |  | PRES_SWT | PL300 | 3 | PRES_SWT | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV11 |  | HPU PRESSURE SAFETY VALVE ON MAIN HEADDER FOR SOLINOIDS IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV12 |  | HPU PRESSURE SAFETY VALVE ON MAIN HEADDER FOR SOLINOIDS IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV13 |  | HPU PRESSURE SAFETY VALVE ON MAIN HEADDER FOR SOLINOIDS IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV14 |  | HPU PRESSURE SAFETY VALVE ON MAIN HEADDER FOR SOLINOIDS IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV15 |  | HPU PRESSURE SAFETY VALVE ON MAIN HEADDER FOR SOLINOIDS IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV16 |  | HPU PRESSURE SAFETY VALVE ON MAIN HEADDER FOR SOLINOIDS IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV17 |  | HPU PRESSURE SAFETY VALVE ON MAIN HEADDER FOR SOLINOIDS IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | VABAOP | PL300HPU7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV1S |  | SPARE HPU PRESSURE SAFETY VALVE IN IRP1 SV STATIONS FROM 1 TO 7 USED TO OPERATE @220BARS. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV21 |  | HPU PRESSURE SAFETY VALVE ON PUMP A, IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV22 |  | HPU PRESSURE SAFETY VALVE ON PUMP A, IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV23 |  | HPU PRESSURE SAFETY VALVE ON PUMP A, IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV24 |  | HPU PRESSURE SAFETY VALVE ON PUMP A, IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV25 |  | HPU PRESSURE SAFETY VALVE ON PUMP A, IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV26 |  | HPU PRESSURE SAFETY VALVE ON PUMP A, IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV27 |  | HPU PRESSURE SAFETY VALVE ON PUMP A, IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | VABAOP | PL300HPU7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV2S |  | SPAIR HPU PRESSURE SAFETY VALVE IN IRP1 SV STATIONS FROM 1 TO 7 USED TO OPERATE @220BARS. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV31 |  | HPU PRESSURE SAFETY VALVE ON PUMP B, IN SVS1 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV32 |  | HPU PRESSURE SAFETY VALVE ON PUMP B, IN SVS2 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV33 |  | HPU PRESSURE SAFETY VALVE ON PUMP B, IN SVS3 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV34 |  | HPU PRESSURE SAFETY VALVE ON PUMP B, IN SVS4 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV35 |  | HPU PRESSURE SAFETY VALVE ON PUMP B, IN SVS5 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV36 |  | HPU PRESSURE SAFETY VALVE ON PUMP B, IN SVS6 USED TO OPERATE 3 BALL VALVES. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV37 |  | HPU PRESSURE SAFETY VALVE ON PUMP B, IN SVS7 USED TO OPERATE 2 BALL VALVES. |  | VABAOP | PL300HPU7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV3S |  | SPARE HPU PRESSURE SAFETY VALVE IN IRP1 SV STATIONS FROM 1 TO 7 USED TO OPERATE @220BARS. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV41 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE CLOSE SOLENOID, IN SVS1. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV42 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE CLOSE SOLENOID, IN SVS2. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV43 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE CLOSE SOLENOID, IN SVS3. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV44 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE CLOSE SOLENOID, IN SVS4. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV45 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE CLOSE SOLENOID, IN SVS5. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV46 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE CLOSE SOLENOID, IN SVS6. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV47 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE CLOSE SOLENOID, IN SVS7. |  | VABAOP | PL300HPU7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV4S |  | SPARE HPU PRESSURE SAFETY VALVE IN IRP1 SV STATIONS FROM 1 TO 7 USED TO OPERATE @220BARS. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV51 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE OPEN SOLENOID, IN SVS1. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV52 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE OPEN SOLENOID, IN SVS2. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV53 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE OPEN SOLENOID, IN SVS3. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV54 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE OPEN SOLENOID, IN SVS4. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV55 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE OPEN SOLENOID, IN SVS5. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV56 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE OPEN SOLENOID, IN SVS6. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV57 |  | HPU PRESSURE SAFETY VALVE ON 10" N/R VALVE OPEN SOLENOID, IN SVS7. |  | VABAOP | PL300HPU7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV5S |  | SPARE HPU PRESSURE SAFETY VALVE IN IRP1 SV STATIONS FROM 1 TO 7 USED TO OPERATE @220BARS. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV61 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE CLOSE SOLENOID, IN SVS1. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV62 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE CLOSE SOLENOID, IN SVS1. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV63 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE CLOSE SOLENOID, IN SVS3. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV64 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE CLOSE SOLENOID, IN SVS4. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV65 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE CLOSE SOLENOID, IN SVS5. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV66 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE CLOSE SOLENOID, IN SVS6. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV67 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE CLOSE SOLENOID, IN SVS7. |  | VABAOP | PL300HPU7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV6S |  | SPAIR HPU PRESSURE SAFETY VALVE IN IRP1 SV STATIONS FROM 1 TO 7 USED TO OPERATE @220BARS. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV71 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE OPEN SOLENOID, IN SVS1. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV72 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE OPEN SOLENOID, IN SVS2. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV73 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE OPEN SOLENOID, IN SVS3. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV74 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE OPEN SOLENOID, IN SVS4. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV75 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE OPEN SOLENOID, IN SVS5. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV76 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE OPEN SOLENOID, IN SVS6. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV77 |  | HPU PRESSURE SAFETY VALVE ON 12" SRR VALVE OPEN SOLENOID, IN SVS7. |  | VABAOP | PL300HPU7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV81 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE CLOSE SOLENOID, IN SVS1. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV82 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE CLOSE SOLENOID, IN SVS2. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV83 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE CLOSE SOLENOID, IN SVS3. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV84 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE CLOSE SOLENOID, IN SVS4. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV85 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE CLOSE SOLENOID, IN SVS5. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV86 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE CLOSE SOLENOID, IN SVS6. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV91 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE OPEN SOLENOID, IN SVS1. |  | VABAOP | PL300HPU1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV92 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE OPEN SOLENOID, IN SVS2. |  | VABAOP | PL300HPU2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV93 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE OPEN SOLENOID, IN SVS3. |  | VABAOP | PL300HPU3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV94 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE OPEN SOLENOID, IN SVS4. |  | VABAOP | PL300HPU4 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV95 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE OPEN SOLENOID, IN SVS5. |  | VABAOP | PL300HPU5 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300PSV96 |  | HPU PRESSURE SAFETY VALVE ON 16" MP VALVE OPEN SOLENOID, IN SVS6. |  | VABAOP | PL300HPU6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300SVS |  | PIPELINE SECTIONALIZING VALVE STATIONS. |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300SVS1 |  | PIPELINE SECTIONALIZING VALVE STATION #1 35/170KM. |  | 0 | PL300SVS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SVS1-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/11/18 | MC-PM-013-M1
| PL300SVS2 |  | PIPELINE SECTIONALIZING VALVE STATION #2 67/138KM. |  | 0 | PL300SVS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SVS2-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 06/04/19 | MC-PM-013-M1
| PL300SVS3 |  | PIPELINE SECTIONALIZING VALVE STATION #3 96/109KM. |  | 0 | PL300SVS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SVS3-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/11/18 | MC-PM-013-M1
| PL300SVS4 |  | PIPELINE SECTIONALIZING VALVE STATION #4 127/78KM. |  | 0 | PL300SVS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SVS4-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 11/04/19 | MC-PM-013-M1
| PL300SVS5 |  | PIPELINE SECTIONALIZING VALVE STATION #5 155/50KM. |  | 0 | PL300SVS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SVS5-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 15/04/19 | MC-PM-013-M1
| PL300SVS6 |  | PIPELINE SECTIONALIZING VALVE STATION #6 179/26KM. |  | 0 | PL300SVS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SVS6-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 19/04/19 | MC-PM-013-M1
| PL300SVS7 |  | PIPELINE SECTIONALIZING VALVE STATION #7 AT 23.7KM |  | 0 | PL300SVS | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | PL300SVS7-MC1 | ACTIVE | CONT | PM | FIC | 12 | MONTHS | 21/04/19 | MC-PM-013-M1
| PL300SYS |  | Control, DCS, PLC, MISC. |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300TCP001 |  | C.P.RECTIFIER/TRANSFORMER UNIT FOR SVS1. |  | CATHPRO | PL300SVS1 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300TCP002 |  | C.P.RECTIFIER/TRANSFORMER UNIT FOR SVS2. |  | CATHPRO | PL300SVS2 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300TCP003 |  | C.P.RECTIFIER/TRANSFORMER UNIT FOR SVS3. |  | CATHPRO | PL300SVS3 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300TCP004 |  | C.P.RECTIFIER/TRANSFORMER UNIT FOR SVS4. |  | CATHPRO | PL300SVS4 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300TCP005 |  | C.P.RECTIFIER/TRANSFORMER UNIT FOR SVS5. |  | CATHPRO | PL300SVS5 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300TCP006 |  | C.P.RECTIFIER/TRANSFORMER UNIT FOR SVS6. |  | CATHPRO | PL300SVS6 | 3 | CATHPRO | 616101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300TEMP |  | Control, Temperature, PL300 |  | TEMP_TX | PL300 | 3 | TEMP_TX | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL300VALVE |  | Valves, PL300 |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL301 |  | ADR-MUS-RUW NAPHTHA /REFORMATE PIPELINE |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL301MISC |  | Miscellaneous (All Others), PL301 |  | 0 | PL301 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL301SYS |  | Control, DCS, PLC, Others, PL301 |  | 0 | PL301 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL302 |  | ADR-MUS-RUW SRR PIPELINE |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL302MISC |  | Miscellaneous (All Others), PL302 |  | 0 | PL302 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL302SYS |  | Control, DCS, PLC, Others, PL302 |  | 0 | PL302 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL303 |  | RUW-MUS MULTIPRODUCT PIPELINE. |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL303MISC |  | Miscellaneous (All Others), PL303 |  | 0 | PL303 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL303SYS |  | Control, DCS, PLC, Others, PL303 |  | 0 | PL303 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL304 |  | OLD MUSSAFAH ALAIN PIPELINE |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL304SYS |  | Control, DCS, PLC, Others, PL304 |  | 0 | PL304 | 3 | 0 | 617101-310600 | IRPALAIN | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL305 |  | MUS-ADIA JET A1 PIPELINE |  | 0 | PL300 | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL305SYS |  | Control, DCS, PLC, Others, PL305 |  | 0 | PL305 | 3 | 0 | 617101-310600 | IRPADIA | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | N | Medium | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL311 |  | RUW-SHWT DIESEL PIPELINE. (GASOIL) |  | 0 | PL300 | 1 | 0 | 617101-310600 | IRPMTERMINAL | NOT READY | 5 | 1 | 5 | 5 | 5 | 5 | 3.4949 | Non Critical | Low | Medium | Y | High Critical | N | 0 | 60 | I | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL311CCTVJB004 |  | JUNCTION BOX FOR CCTV (SHOWEIHAT) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL311CCTVSW001 |  | 24 Port Switch FOR CCTV (SHOWEIHAT) |  | CCTVSEC | PL311TELM | 3 | CCTVSEC | 617101-310600 | MTERMINAL | NOT READY | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL311TELM |  | Telecom, Telemetry, PA system, PL311 (SHOWEIHAT) |  | CCTV_SYS | PL311 | 3 | CCTV_SYS | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312 |  | RUW- MUS Jet A-1 Pipeline. |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | Non Critical | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312BATT |  | Electrical, Battery Banks, PL312 |  | BATTERY | PL312 | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312FLOW |  | Control, Flow, PL312 |  | FL_MTR | PL312 | 3 | FL_MTR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312GD |  | Gas detectors, PL312 |  | FG_DET | PL312 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | Non Critical | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312MISC |  | Miscellaneous (All Others), PL312 |  | PIPING | PL312 | 4 | PIPING | 0 | MTERMINAL | OPERATING | 1 | 1 | 1 | 1 | 5 | 5 | 1.3979 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312MOV |  | Electric actuators, MOVs, PL312 |  | MOV | PL312 | 3 | MOV | 617101-310600 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PKG |  | Packages unit, PL312 |  | PACKAGE | PL312 | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Non Critical | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PRESS |  | Control, Pressure, PL312 |  | PRES_TX | PL312 | 3 | PRES_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV11 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS1 |  | VABAOP | PL312HPU021 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV12 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS1 |  | VABAOP | PL312HPU021 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV21 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS2 |  | VABAOP | PL312HPU022 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV22 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS2 |  | VABAOP | PL312HPU022 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV31 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS3 |  | VABAOP | PL312HPU023 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV32 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS3 |  | VABAOP | PL312HPU023 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV41 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS4 |  | VABAOP | PL312HPU024 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV42 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS4 |  | VABAOP | PL312HPU024 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV43 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS4 |  | VABAOP | PL312HPU028 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV44 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS4 |  | VABAOP | PL312HPU028 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV45 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS4 |  | VABAOP | PL312HPU029 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV46 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS4 |  | VABAOP | PL312HPU029 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV51 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS5 |  | VABAOP | PL312HPU025 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV52 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS5 |  | VABAOP | PL312HPU025 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV61 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS6 |  | VABAOP | PL312HPU026 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312PSV62 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS6 |  | VABAOP | PL312HPU026 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312SCB |  | Electrical, Feeder,Transformer, Substn, Switch gear, Accessories, PL312 |  | TRANSFMR | PL312 | 3 | TRANSFMR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312SYS |  | Control, DCS, PLC, Others, PL312 |  | POWER_TX | PL312 | 3 | POWER_TX | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312TELM |  | Telecom, Telemetry, PA system, PL312 |  | CCTVSEC | PL312 | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | c | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312TEMP |  | Control, Temperature, PL312 |  | TEMP_ELE | PL312 | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312VALVE |  | All Valves, PL312 |  | CONTHNDV | PL312 | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL312VESSEL |  | Vessel, Tank, Column, Tower, Reactor, Dryer, Mixer, Sphere, PL312 |  | VESSEL | PL312 | 3 | VESSEL | 0 | MTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL313 |  | RUW-MUS DIESEL Pipeline. (Gas Oil) |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315 |  | RUW-TARF-M Zayed Mo-Gas Pipeline. (GASOLINE) |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315BATT |  | Electrical, Battery Banks, PL315 |  | BATTERY | PL315 | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315GD |  | Gas detectors, PL315 |  | FG_DET | PL315 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315MISC |  | Miscellaneous (All Others), PL315 |  | BLDGS | PL315 | 4 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315PRESS |  | Control, Pressure, PL315 |  | INDICATR | PL315 | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315PSV131 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS13 |  | VABAOP | PL315HPU1301 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315PSV132 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS13 |  | VABAOP | PL315HPU1301 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315SCB |  | Electrical, Feeder,Transformer, Substn, Switch gear, Accessories, PL315 |  | BLDGS | PL315 | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315SYS |  | Control, DCS, PLC, Others, PL315 |  | CLDCFG | PL315 | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315TELM |  | Telecom, Telemetry, PA system, PL315 |  | CCTVSEC | PL315 | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315TEMP |  | Control, Temperature, PL315 |  | TEMP_ELE | PL315 | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL315VALVE |  | All Valves, PL315 |  | CONTHNDV | PL315 | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL316 |  | Tariff - Madinat Zayed DIESEL Pipeline. (Gas oil) |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318 |  | Mussafah - Al Ain Mo-Gas Pipeline. (GASOLINE) |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318BATT |  | Electrical, Battery Banks, PL318 |  | BATTERY | PL318 | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318GD |  | Gas detectors, PL318 |  | FG_DET | PL318 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318MISC |  | Miscellaneous (All Others), PL318 |  | BLDGS | PL318 | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PKG |  | Packages unit, PL318 |  | PACKAGE | PL318 | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PRESS |  | Control, Pressure, PL318 |  | INDICATR | PL318 | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV101 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS10 |  | VABAOP | PL318HPU1001 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV102 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS10 |  | VABAOP | PL318HPU1001 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV111 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS11 |  | VABAOP | PL318HPU1101 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV112 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS11 |  | VABAOP | PL318HPU1101 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV121 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS12 |  | VABAOP | PL318HPU1201 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV122 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS12 |  | VABAOP | PL318HPU1201 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV81 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS8 |  | VABAOP | PL318HPU801 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV82 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS8 |  | VABAOP | PL318HPU801 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV91 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS9 |  | VABAOP | PL318HPU901 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318PSV92 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS9 |  | VABAOP | PL318HPU901 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318SCB |  | Electrical, Feeder,Transformer, Substn, Switch gear, Accessories, PL318 |  | TRANSFMR | PL318 | 3 | TRANSFMR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318SYS |  | Control, DCS, PLC, Others, PL318 |  | CLDCFG | PL318 | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318TELM |  | Telecom, Telemetry, PA system, PL318 |  | TELECOM | PL318 | 3 | TELECOM | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318TEMP |  | Control, Temperature, PL318 |  | TEMP_ELE | PL318 | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL318VALVE |  | All Valves, PL318 |  | CONTHNDV | PL318 | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL319 |  | Mussafah - Al Ain DIESEL Pipeline. (GASOIL) |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL321 |  | Mussafah - ADIA JET A-1 Northern Pipeline. |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL321TELM |  | Telecom, Telemetry, PA system, PL321 |  | CCTVSEC | PL321 | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL324 |  | Mussafah - Al Dhafra JP-8 Pipeline. |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL324TELM |  | Telecom, Telemetry, PA system, PL324 |  | CCTVSEC | PL324 | 3 | CCTVSEC | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | t | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325 |  | ADR - ADIA JET A-1 Southern Pipeline. |  | PIPING | PL300 | 1 | PIPING | 617101-310600 | IRPMTERMINAL | NOT READY | 50 | 100 | 5 | 100 | 100 | 5 | 9.0969 | High | High | High | Y | High Critical | N | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325BATT |  | Electrical, Battery Banks, PL325 |  | BATTERY | PL325 | 3 | BATTERY | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | p | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325GD |  | Gas detectors, PL325 |  | FG_DET | PL325 | 1 | FG_DET | 617101-310600 | MFPS | OPERATING | 50 | 50 | 50 | 1 | 100 | 5 | 7.7959 | High | Medium | Medium | Y | High Critical | Y | 0 | 6 | g | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325MISC |  | Miscellaneous (All Others), PL325 |  | BLDGS | PL325 | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325PKG |  | Packages unit, PL325 |  | PACKAGE | PL325 | 3 | PACKAGE | 0 | MTERMINAL | OPERATING | 5 | 10 | 5 | 5 | 5 | 10 | 4.7959 | Low | Low | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325PRESS |  | Control, Pressure, PL325 |  | INDICATR | PL325 | 3 | INDICATR | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325PSV71 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS7 |  | VABAOP | PL325HPU027 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325PSV72 |  | PSV INSTALLED ON HPU TO ACTIVATE SOLENOID USED TO OPERATE EOV IN SVS7 |  | VABAOP | PL325HPU027 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Medium | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325SCB |  | Electrical, Feeder,Transformer, Substn, Switch gear, Accessories, PL325 |  | BLDGS | PL325 | 3 | BLDGS | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | p | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325SYS |  | Control, DCS, PLC, Others, PL325 |  | CLDCFG | PL325 | 3 | CLDCFG | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325TELM |  | Telecom, Telemetry, PA system, PL325 |  | TELECOM | PL325 | 3 | TELECOM | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325TEMP |  | Control, Temperature, PL325 |  | TEMP_ELE | PL325 | 3 | TEMP_ELE | 0 | MTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | N | Low | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PL325VALVE |  | All Valves, PL325 |  | CONTHNDV | PL325 | 3 | CONTHNDV | 0 | MTERMINAL | OPERATING | 5 | 5 | 1 | 1 | 5 | 5 | 2.7959 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | m | 0 | N | N |  | 0 | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLSVS1HPU |  | TO BE DELETED |  | VABAOP | PL300SVS1 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLSVS2HPU |  | TO BE DELETED |  | VABAOP | PL300SVS2 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLSVS3HPU |  | TO BE DELETED |  | VABAOP | PL300SVS3 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLSVS4HPU |  | TO BE DELETED |  | VABAOP | PL300 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLSVS6HPU |  | TO BE DELETED |  | VABAOP | PL300SVS6 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PLSVS7HPU |  | TO BE DELETED |  | VABAOP | PL300SVS7 | 3 | VABAOP | 617101-310600 | IRPMTERMINAL | MOTHBALLED | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| R1141D001 |  | ULG SUMP VESSEL |  | VESSEL | R1141VESSEL | 3 | VESSEL | 0 | IRPMTERMINAL | OPERATING | 10 | 10 | 5 | 10 | 100 | 1 | 5.699 | Low | Low | Low | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| R1141PLR001 |  | Scraper Launcher Jet A1 Pipeline(From RRD to Mussafah) |  | PIPING | R1141MISC | 3 | PIPING | 0 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| R1141PLR002 |  | Scraper Launcher Gas Oil Pipeline(From RRD to Mussafah) |  | PIPING | R1141MISC | 3 | PIPING | 0 | IRPMTERMINAL | OPERATING | 50 | 1 | 1 | 1 | 50 | 1 | 3.3979 | Low | Low | Non Critical | N | Low | N | 0 | 60 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SADIATP |  | CATHODIC PROTECTION TEST POINTS |  | 0 | SADIAPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SADIAVS1 |  | VALVE STATION # 1 AT KM 1.75 |  | 0 | SADIAPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SADIAVS2 |  | VALVE STATION # 2 AT KM 2.5 |  | 0 | SADIAPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | SADIAVS2-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 12/10/18 | MM-PM-012-M3
| SALAINCPS1 |  | CATHODIC PROTECTION STATION # 1 AT KM 3.8 |  | 0 | SALAINPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINCPS2 |  | CATHODIC PROTECTION STATION # 2 AT KM 18.5 |  | 0 | SALAINPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINCPS3 |  | CATHODIC PROTECTION STATION # 3 AT KM 84.5 |  | 0 | SALAINPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINCPS4 |  | CP STATION # 4 AL AIN PIPE LINE AT KM 149. |  | 0 | SALAINPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINDMS1 |  | DENSITY MEASURING STATION AT KM 147 |  | 0 | SALAINPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINSLS |  | SPARE LINE STATION AT KM 0.75 |  | 0 | SALAINPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINSLSV1 |  | VALVE 10" AT KM0.75 |  | 0 | SALAINSLS | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINVS1 |  | MQTAA_ALAIN VALVE STATION # 1 AT 2 KM. |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SALAINVS1-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 12/10/18 | MM-PM-012-M1
| SALAINVS2 |  | MQTAA_ALAIN VALVE STATION # 2 AT KM 27.5 |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SALAINVS2-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 08/08/18 | MM-PM-012-M3
| SALAINVS3 |  | MQTAA_ALAIN VALVE STATION # 3 AT KM 48.5 |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SALAINVS3-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 09/08/18 | MM-PM-012-M3
| SALAINVS4 |  | VALVE STATION # 4 AT KM 75 |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SALAINVS4-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 10/08/18 | MM-PM-012-M3
| SALAINVS5 |  | VALVE STATION # 5 AT KM 85.9 |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SALAINVS5-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 11/08/18 | MM-PM-012-M3
| SALAINVS6 |  | VALVE STATION # 6 AT KM 125.2 |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | SALAINVS6-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 12/08/18 | MM-PM-012-M3
| SALAINVS7 |  | VALVE STATION # 7 AT KM 85.9 |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALAINVS8 |  | VALVE STATION # 8 AT KM 125.2 |  | 0 | SALAINPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCDAVSCAN |  | New Admin Building. |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | s | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SD |  | Supply Division |  | 0 | 0 | 3 | 0 | 617101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SDHDSJKSDK |  | HDHDD |  | 0 | 0 | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SDHELCHOUM |  | Hussain El Choum |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SDITASSETS |  | SD IT Assets |  | 0 | SD | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SD-MSFH-P13 |  | Planing |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SDSHAMSI |  | MOHAMMED JARWAN MOHAMMED AL SHAMSI |  | 0 | P&T_NEW_ADMIN | 3 | 0 | 0 | 0 | NOT READY | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SEC FOR MR. OBEID |  | New Admin Buliding |  | 0 | 0 | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMLPGTP |  | CATHODIC PROTECTION TEST POINTS |  | 0 | SMLPGPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 12 | i | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMLPGVS1 |  | VALVE STATION # 1 AT KM 0.8 (LPG) |  | 0 | SMLPGPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMLPGVS2 |  | VALVE STATION # 2 AT KM 1.8 (LPG) |  | 0 | SMLPGPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMLPGVS3 |  | VALVE STATION # 3 AT KM 12 (LPG) |  | 0 | SMLPGPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | SMLPGVS3-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 12/10/18 | MM-PM-012-M3
| SMTP |  | CATHODIC PROTECTION TEST POINTS |  | 0 | SMPIPE | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | Y | 0 | 6 | e | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMTP31 |  | TEST POINT# 31 ( MUSSAFAH PRODUCT TRANS. P.L.) |  | 0 | SMTP | 3 | 0 | 616101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 6 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMVS1 |  | SANT-MT VALVE STATION 1 @ 0.8KM (MULTI PRODUCT) |  | 0 | SMPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | SMVS1-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 12/10/18 | MM-PM-012-M3
| SMVS2 |  | SANT-MT VALVE STATION 2 @ 1.8KM (MULTI PRODUCT). |  | 0 | SMPIPE | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | SMVS2-MM1 | ACTIVE | MECH | PM | EDS | 3 | MONTHS | 12/10/18 | MM-PM-012-M3
| SMVS3 |  | SANT-MT VALVE STATION 3 @ 12KM (MULTI PRODUCT). |  | 0 | MREDUNDANT | 3 | 0 | 617101-310600 | MTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 6 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-PIG-LAUNCHERS |  | PIG LAUNCHERS AT ADRD. |  | 0 | MTERMINAL | 3 | 0 | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Low | N | Low | N | 0 | 60 | m | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| T-TAS-A3 |  | P&T SECURITY |  | 0 | 0 | 3 | 0 | 0 | 0 | OPERATING | 5 | 1 | 1 | 1 | 1 | 1 | 0.69897 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | d | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| U51PG110 |  | PRESS. GAUGE IN THE LPG PIG LAUNCHER. |  | OPENLOOP | U5101R01 | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| U51PG111 |  | PRESS. GAUGE AFTER MOV-106 (LPG PIG LAUNCHER) |  | OPENLOOP | U5101R01 | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| U51PG160 |  | PRESS. GAUGE IN THE LPG PIG LAUNCHER. |  | OPENLOOP | U5101R01 | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Non Critical | N | Non Critical | N | 0 |  | c | 0 | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| U51RV103 |  | RELIEF VALVE IN THE LPG PIG LAUNCHER. |  | OPENLOOP | U5101R01 | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| U51RV104 |  | RELIEF VALVE IN THE LPG PIPELINE. |  | OPENLOOP | U5101R01 | 3 | OPENLOOP | 623101-310600 | IRPMTERMINAL | OPERATING | 5 | 10 | 1 | 1 | 1 | 1 | 1.699 | Non Critical | Non Critical | Low | Y | High Critical | Y | 0 | 60 | i | 0 | Y | Y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0